## Slide 1: A Resource Adequacy Standard for the Pacific Northwest
Resource Adequacy Steering Committee
October 4, 2011

## Slide 2: outline
Current Adequacy Standard
Proposed Revisions
State of the System Report
Sample Report
Next Steps

## Slide 3: Current Adequacy standard
Current standard in use for 3 years
Led to some confusion – L/R balance
Peer reviewed in 2010
  Eliminate translation to static measures
  Eliminate seasonal assessments
  Add measure for size of problem
  Measure use of standby resources

## Slide 4: Proposed Revisions to be approved by the forum
Keep the current methodology, which includes non-firm resources
Keep the LOLP metric and the 5% threshold
Annual assessment (all months)
Quantify demand response (DR) and standby resources (SR) that are contractually available
Count events that exceed the energy and capacity limits of DR and SR

## Slide 5: State of the system report
Adequacy assessment
Other commonly used adequacy measures
Reliance on non-firm and standby resources
Monthly assessment of potential shortfalls
Frequency, duration and magnitude of events
Conditions under which events occur

## Slide 6: Sample Report – for illustration only
Not an official assessment
LOLP is 6.7% = inadequate supply
Dec, Jan and Aug only months with shortfalls
LOLP driven by peak shortfalls in August (LOLP = 1.4% not counting peak events)
Adding 400 MW of capacity in August will bring LOLP below 5%

## Slide 7: Comparison to old standard
Old standard
  Winter capacity LOLP = 2.4%
  Winter energy LOLP = 1.0%
  Summer capacity LOLP = 4.3%
  Summer energy LOLP = 1.9%
  Interpretation – Adequate
New standard
  LOLP = 6.7%
  Interpretation – Inadequate
Winter and summer capacity problems occur in different games thus, seasonal assessment will underestimate overall adequacy.

## Slide 8: Adequacy summary - IPP
Availability:
  3,500 MW winter (approximate)
  1,000 MW summer
Percent of time used:
  To some degree every winter
  To some degree every summer
Dispatch:
  Winter months (avg): 750 to 1,500 MW-months
  Summer months (avg): 250 to 600 MW-months

## Slide 9: Adequacy summary – sw market
Availability:
  On peak (3,000 MW winter , 0 MW summer)
  Proposed Off peak (1,000 MW year round)
Percent of time used:
  On peak used up to 11% of the time in winter
  Off peak used up to 27% of the time in summer
Dispatch:
  Highest on-peak: 1000 MW-months in one Dec
  Highest off-peak: 400 MW-months in one Aug

## Slide 10: Adequacy summary – Borrowed hydro
Availability:
  1,000 MW-months all months
Percent of time used:
  Mostly in summer, about 90% of the time in Aug
  Less in winter, about 14% in Dec
Dispatch:
  About 700 MW-months in one August
  About 400 MW-months in one December

## Slide 11: Adequacy summary – dr, sr and lolp
Availability:
  DR capacity only, 60 MW winter, 120 MW summer
  SR 602 MW capacity, 83,000 MW-hrs all year
Percent of time used:
  DR is used to some degree in 8.6% of the years
  SR is used somewhat less (no approx yet)
Dispatch:
  DR is generally used up to its availability
  SR energy may be used up before summer

## Slide 12: Adequacy metrics and values
Adequacy Metrics | 
Metric | Description
LOLP | Loss of load probability = number of games with a problem divided by the total number of games
DR and SR | Demand response and standby resources that are contractually available = measure of
CVaR (energy) | Conditional value at risk = average annual curtailment for 5% worst games
CVaR (peak) | Conditional value at risk = average single-hour curtailment for worst 5% of games
EUE | Expected unserved energy = total curtailment divided by the total number of games
LOLE | Loss of load expectation = total number of hours of curtailment divided by total number of games

## Slide 13: Adequacy metrics and values
Adequacy Metrics |  | 
Metric | Value | Units
LOLP | 6.7 | Percent
Use of DR and SR | 8.6 | Percent
CVaR (energy) | 67,618 | MW-hours
CVaR (peak) | 2,277 | MW
EUE | 3,399 | MW-hours
LOLE | 3.3 | Hours/year

## Slide 14: Annual curtailment energy

## Slide 15: Annual highest hour peak curtailment

## Slide 16: Non-firm resources: % of time used

## Slide 17: Non-firm resources: dispatch

## Slide 18: Independent power producers

## Slide 19: SW market purchases

## Slide 20: SW off-peak purchases

## Slide 21: Borrowed hydro

## Slide 22: Energy – Dr, sr and LOLP

## Slide 23: Peak – dr, sr and lolp

## Slide 24: Curtailment statistics
Expected Number of Events* | 0.23 | per year
Average Event Duration | 14 | Hours
Average Event Magnitude | 14569 | MW-hrs
Average Event Peak Shortfall | 1098 | MW
Expected Number of Shortfall Hours | 3.3 | per year
Percent of Games With an Event | 8.6 | percent
*An event is defined as a contiguous set of hours of shortfall.

## Slide 25: Next steps
Forum approves revised standard (namely the elements on slide number 4)
Forward proposed revisions to Council
Work continues on better defining non-firm resource assumptions, use of borrowed hydro, demand response and standby resources
Debate using off-peak summer purchases
2012: Forum approves revised assumptions