## Slide 1: Big Wind Study
Technical Committee Meeting January 27, 2012
Notes: 1
The GENESYS model is being developed, in the short-term, to assess potential reliability problems in the Northwest. In the long-term, it is hoped that this model will become a useful economic tool to help guide the use of the multi-dam hydroelectric power system.

## Slide 2: Outline
Impacts of INC and DEC wind reserves on hydro generating capability
Impacts of increasing wind capacity on hydro and thermal dispatch
Impacts of increasing wind capacity on the existing over generation problem
Assessing the load carrying capability for wind

## Slide 3: Effects of INC and DEC Reserves on Hydroelectric Capability INC Reserve – Covers peak load when wind doesn’t blow DEC Reserve – Backs off generation during light load hours when wind does blow

## Slide 4: Effects of INC and DEC Reserves on Hydroelectric Capability
Chart: Hour of Day
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Orig | 10000 | 10000 | 12000 | 15000 | 30000 | 30000 | 15000 | 12000 | 10000 | 10000 | 10000 | 10000
w/DEC | 11500 | 11500 | 11500 | 15000 | 26000 | 26000 | 15000 | 11500 | 11500 | 11500 | 11500 | 11500
w/INC + DEC | 13000 | 13000 | 13000 | 15000 | 22000 | 22000 | 15000 | 13000 | 13000 | 13000 | 13000 | 13000

## Slide 5: DEC Reduces Hydro Peaking Capability (for 6K of installed wind)
Period | 2-Hr | 4-Hr | 6-Hr | 8-Hr | 10-Hr | 12-Hr
Sep | -33 | -444 | -699 | -778 | -742 | -612
Oct | -364 | -976 | -1115 | -1065 | -865 | -636
Nov | -2 | -108 | -354 | -351 | -356 | -322
Dec | -19 | -149 | -404 | -387 | -365 | -325
Jan | -64 | -186 | -406 | -407 | -393 | -341
Feb | -192 | -274 | -512 | -509 | -472 | -416
Mar | -54 | -142 | -479 | -501 | -465 | -424
Apr 1 | -855 | -1083 | -1057 | -928 | -778 | -597
Apr 2 | -319 | -349 | -380 | -357 | -319 | -304
May | 0 | 0 | -8 | -57 | -84 | -92
Jun | -114 | -233 | -373 | -432 | -434 | -377
Jul | 0 | -41 | -169 | -255 | -321 | -318
Aug 1 | 0 | 0 | -36 | -149 | -295 | -316
Aug 2 | -227 | -652 | -951 | -942 | -820 | -669
For Illustration Only

## Slide 6: DEC Increases Minimum Hydro Generation
Chart: Simulated dispatch for a very wet year
For Illustration Only
Hit minimum hydro generation often

## Slide 7: Effects on Resource Dispatch

## Slide 8
Chart: Simulated Dispatch – No Wind
For Illustration Only

## Slide 9
Chart: Simulated Dispatch – 3K Wind
For Illustration Only

## Slide 10
Chart: Simulated Dispatch – 6K Wind
For Illustration Only

## Slide 11
Chart: Simulated Dispatch – Hydro Only
For Illustration Only

## Slide 12: Future work
Identify resources whose dispatch is most affected by increasing wind capacity
Quantify how natural gas use decreases with increasing amounts of wind
Investigate how thermal ramp-ups and ramp-downs change with increasing wind
Should we investigate carrying some INC and DEC requirements with thermal resources?
Anything else?

## Slide 13: Oversupply Problem*
Oversupply conditions occur when the minimum system generation exceeds firm load and secondary sales markets.
*Still working with BPA staff to review results.

## Slide 14
Chart: Oversupply in Average Megawatts (averaged over all hours of the month)
| 0 | 3 | 4 | 5 | 6 | 7 | 8
Oct | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nov | 0 | 0 | 0 | 0.013056 | 0.12028 | 0.22931 | 0.32764
Dec | 0 | 0 | 0 | 0 | 0 | 0 | 0
Jan | 0 | 0.031317 | 0.32809 | 1.318 | 3.7591 | 7.8878 | 12.8323
Feb | 17.1945 | 56.1677 | 78.4711 | 108.4394 | 146.0205 | 192.246 | 242.5246
Mar | 51.0882 | 96.937 | 121.2508 | 151.0983 | 186.7844 | 227.3099 | 267.1938
Apr | 54.9319 | 174.0746 | 242.6681 | 329.8278 | 435.3122 | 548.9826 | 653.7647
May | 807.7692 | 1295.9043 | 1502.5585 | 1730.1974 | 1971.6988 | 2211.3374 | 2428.6042
Jun | 813.2026 | 1235.5715 | 1420.4836 | 1625.3262 | 1843.1219 | 2059.7807 | 2260.0651
Jul | 86.6167 | 190.1437 | 242.0297 | 302.9313 | 373.7137 | 451.2219 | 529.2931
Aug | 0.040188 | 1.2386 | 2.6462 | 5.0458 | 8.971 | 13.8351 | 19.0313
Sep | 0 | 0.00041667 | 0.030139 | 0.20333 | 0.85153 | 1.7718 | 2.6004
For Illustration Only
No sales market assumed in this case

## Slide 15
For Illustration Only
Intertie size

## Slide 16
Assessing the Effective Load Carrying Capability of Wind (ELCC)

## Slide 17: What is ELCC?
“Effective load carrying capability” is defined as the amount of incremental load a resource can serve without degrading adequacy.
It is usually expressed as a percentage of a resource’s capacity.
Example: a standalone CT with 5% FOR and infinite fuel supply has an ELCC of 95%
ELCC is a function of the system the new resource is added to – this is particularly important for wind.

## Slide 18: Study Methodology
Base case
  Remove all wind
  Calculate total annual average curtailment
Study cases
  Add 200 MWa of annual shaped load
  Add increments of wind capacity until the total annual average curtailment equals that in the base
  Repeat above with greater amounts of load

## Slide 19: ELCC Results (+200 MWa load)
Chart: Average Load/Wind Capacity (%)
| 0.4 | 0.2
Study | 1372179.8 | 1207592.5
Base | 1259934 | 1259934
For Illustration Only

## Slide 20: Annual Wind ELCC Results
Chart: Installed Wind Capacity (MW)
| 758.71576296002854 | 1746.2011539831904 | 2761.7874085397257 | 3962.6618356884992 | 5746.0149429212215 | 7939.4772271509182
Average | 0.2636 | 0.22907 | 0.217 | 0.20188 | 0.17403 | 0.15114
Incremental | 0.2636 | 0.19453 | 0.1704 | 0.14017 | 0.084464 | 0.038684
For Illustration Only

## Slide 21: Observations
ELCC declines with increasing amounts of wind because system flexibility is used up
Eventually wind ELCC will flatten out
Average annual wind generation is ~ 30%, yet currently aggregate ELCC is ~ 23% Thus, can’t plan on average wind generation
Adding storage will increase ELCC
Adding more diverse wind generation will also increase aggregate ELCC