## Sheet 1
Update and status of mission critical elements for the F&W Program hatcheries. These are items that have either already failed, or failure could occur in the near future and have a direct negative effect on the ability of the facility to perform its mission. Highlighted green items have been addressed and yellow highlighted items are in the process of being addressed. Shaded sections reflect elements addressed through the cost savings workgroup in FY 2017.
Site | Mission Critical Element | Status - as of June 29, 2017 | Comment
Nez Perce Tribal Hatchery | River water filtration system | Evaluation under the kelt master plan continues as it proceeds through environmental review and engineering designs. It is anticipated that by the end of the calendar year the relation and possible efficiencies between the two projects will be determined. | Additional evaulation needed, TBD - Cost at $100,000 - Relationship of this high prioity item, in association to the Snake River Basin Steelhead Kelt Reconditioning Facility Master Plan (Project #2007-401-00), needs to be determined prior to action. It is hoped that the cost of these units could be addressed through the master planning effort. Current filtration system is 50-micron. Replacing the system with 20-micron could reduce the accumulation of sediment in the heat exchanger. The cost shown here is approximate for changing the existing filter units to 100-micron to operate as roughing filters, and add 20-micron units for polishing.
| Heat exchanger | Evaluation under the kelt master plan continues as it proceeds through environmental review and engineering designs. It is anticipated that by the end of the calendar year the relation and possible efficiencies between the two projects will be determined. | Additional evaulation needed, TBD - Cost at $45,000 - Relationship of this high prioity item, in association to the Snake River Basin Steelhead Kelt Reconditioning Facility Master Plan (Project #2007-401-00), needs to be determined prior to action. It is hoped that the cost of these units could be addressed through the master planning effort. Unit is designed for 600 gpm and DT of 4.5⁰F (112.5 tons). Cost shown is for replacement in kind. Before this is done, there should be discussion about installation of redundant units so that one could be taken out of service for cleaning without interrupting flow to the hatchery. Note that the chiller associated with the heat exchanger is a separate piece of equipment. The chiller is a closed-loop system that cools glycol and circulates it through the heat exchanger. Heat from the hatchery supply water is transferred to the glycol, cooling the water. No issues with the chiller were noted and it should have 10+ years of remaining useful life.
| River water pumps (2) | NPT determining pump replacement costs with manafactures. Once cost is known BPA will add funds to Tribe's FY17 contract for pump purchase. | Cost @ $50,000 - The pumps at the river water intake have been in service since 2002/2003. These pumps are beyond their expected useful life and could fail at any time. There are four pumps that need replacement, but two have already been purchased and will be installed when the old pumps fail. Two additional pumps need to be purchased.
-Yoosa/Camp | Yoosa intake bypass flow | The NPT are evaluating the cost benefit of this need as part of the hatchery evaluation. At this time this critical need is addressed through additional staff time. | Additional evaulation needed, TBD - Cost unknown until a complete evaluation occurrs - The dam structure that impounds water leaks significantly, to the extent that the operators build a sandbag cofferdam upstream and pipe the water to the intake screen. Detailed evalution by a structural engineer is advised.
Grand Ronde Supplementation
-Upper Grande Ronde | Raceway liners | Addressed* | Cost @ $15,000 - Covered by Accord Funds - Liners are from original installation in 1998 and are worn out from constant exposure to weather.
Colville | Generator | Addressed* | Cost @ $75,000 - Covered by Accord Funds - The generator provides standby power for critical water supply wells. Parts to keep the existing unit running reliably are no longer available.
Umatilla | Well system | Bonneville working with ODFW and CTUIR on urgent electrical issues. Efforts to initiate a comprehensive review of well system is ongoing. | Additional evaulation needed, TBD - Cost unknow until a complete evaulation is completed - Well system provides a fraction of the flow the facility was designed for.
-Three Mile Dam | Leaking pipe | Addressed* | Cost estimated @ $20,000 - Covered by Accord funds - This is a buried pipe between the intake pump and the adult holding tank. There is evidence that water is flowing along the exterior of the pipe based on seepage evident at both ends where the pipe is exposed. Gravel surface along the pipe alignment is sinking, indicating soil is being washed out by the leakage. Difficulty is that one of the column bases of the roof structure on the adult handling is directly over the buried pipe.
Walla Walla Spring Chinook | Structure damage | The issue will be evaluated and addressed in the planning effort associated with Project #2000-038-00, Walla Walla Hatchery Final Design/Construction. | Additional evaulation needed, TBD - Cost unknown until complete evaluation occurs - Differential settlement at fish lock is developing large cracks in the concrete and masonry. Detailed evaluation by a structural engineer is advised.
Snake River Sockeye Propagation
-Springfield | Chiller system | Engineering services contracted to develop design and specifications for chilled water delivery system upgrade at Springfield Hatchery.* | Additional evaulation needed - Ongoing, current evaluation being conducted, covered by Accord Funds - Cost estimated at $75,000 in assessment report - This high priority item is critical to the hatchery in meeting its production level goals. System was supposedly rated at 50 tons, designed to provide a ∆T of 10⁰F for 110 gpm (46 tons actual). The operators can only get the system to provide a ∆T of 6⁰F for 80 gpm (20 tons actual). This system is critical for achieving the full production capacity of the facility. The subconsultant that designed the system told IDFG they don't know why it underperforms. An independent engineering evaluation of the system design is needed to determine the cause(s) of performance issues.
Kootenai River Native Fish Conservation Aquaculture
- Twin Rivers | Boiler System | Addressed, repair/corrective action has occurred by sponsor. | This high priority item is critical to the hatchery in meeting its production level goals. The facility relies on the boilers to keep the facility heated and to heat process water for getting sturgeon to the size required. The boilers experience flame failure constantly, requiring operators to manually restart the boiler. The contractor who installed the units has not been able to correct the issue. On-site assistance from manufacturer's representatives with technical training on these boilers is needed to determine why the boilers do not function properly.
Sekokini Springs | Generator | Addressed | Cost @ $5,000 - Currently, Sekokini does not have a backup generator as the facility operates entirely on gravity fed water. However, in January a UV system will be installed to treat effluent from its new isolation building before it reaches the local river. Without a backup generator (assume a small ~7 kw) the hatchery will be at the mercy of the local utility. An interruption in power to the UV system of up to a day (what operators say is the longest they've gone) would be unacceptable.
Lake Roosevelt Resident
-Sherman | Sanitary Lift Station Pumps | Contracting in progress | Cost @ $20,000 - Replace duplex pumps - one has failed and other is old.
| Emergency Generator and Xfr Switch | Contracting in progress | Cost @ $40,000 - The main hatchery does not have a standby generator or automatic transfer switch.
| Lake Water Pumps | Design and permitting are needed for this pre-existing issue (has been existing for several years). In addition, efficiency could be achieve as part of the anticipated sturgeon master plan associated the facility. | Additional evaulation needed, TBD - Cost @ $30,000. Move pumps and extend to deeper water to maintain flow during reservoir drawdown. Design through procurment is advisable (plus permitting and etc). In addition, relation to future proposed use of hatchery is needed.
| Net Pens | Further study is needed. | Additional evaulation needed, TBD. Reservoir drawdown causing early release of fish and the effect on program goals, current location does not function during reservoir drawdown.
-Spokane | Well #2 | Bonneville will work with Spokane Tribe to address this issue within existing contracts and budget agreements.* | Additional evaulation needed, TBD - Cost @ $120,000. The facility has no redundant groundwater supply for 9 months a year. It appears that original well #2 screen was installed at wrong elevation in non-water bearing strata. Redevelop Well #2 to obtain approx 500 gpm of redundant supply.Providing modifications to the existing well to turn it back into a useful groundwater production well for the hatchery should be considered. Modifications designed by an experienced hydro-geologist / well designer could lead to a relatively easy addition of at least 500 gpm of high quality groundwater to the hatchery system. This improvement would help minimize the future need to rely on low quality surface water for hatchery operations.
Kalispel | Alarm system | Activities at the hatchery are dependent on a future review. | Additional evaulation needed, TBD - Cost @ $50,000. Original System is non-functional and no longer supported. This item may be funded as part of the ongoing coldwater conversion program upgrades. This program has phased out of LMB and raising tripolid trout for put-and-take.
Total allocation from cost savings workgroup $115,000
*In addition, approximately $305,000 has been provided by Accord and contract adjustments between Bonneville and the project sponsors.