## Sheet 1
F&W Program Hatcheries - DRAFT version August 10, 2017
Essential Maintenance/Improvements: The following is a list of essential maintenance/improvements elements* for the F&W Program hatcheries. Also listed are the unresolved mission critical elements from FY 2017. The essential elements where received from 9 of the Programs 14 hatcheries. The order of the specific elements are the prioritizations from the managers. Allocations of funds from FY 2018 cost savings is $283,500. Staff aligned the priorities to the Fiscal Years for planning purposes only. Elements in this list need to be confirmed as implementable in 2018. In addition, permitting and environmental compliance also needs to be confirmed.
Site - Manager | Essential Element | Estimated Cost by Fiscal Year |  |  | Description
|  | 2018 | 2019 | 2020
Sekokini - MFWP | Spring #2 Infiltration Gallery | 15000 |  |  | Spring 2 infiltration gallery needs maintenance to capture flow that is currently diverted away from the cistern. Large snowpack and runoff this spring have led to even more of the flow being routed past the cistern, reducing flow to the hatchery building.
| French Drain |  | 5000 |  | French drain is needed in front of the isolation building to redirect seepage behind the retaining wall and prevent ice formation in front of the entry way.
| Roof |  |  | 12000 | Metal roof replacement on the original hatchery building (not the expansion building).
| Settle Pond Drain |  |  | 7000 | The concrete outflow structure that controls the elevation of the hatchery’s effluent settling pond is crumbling and needs to be replaced.
Lake Roosevelt Resident
Spokane - STOI | NA | NA | NA | NA | Utilizing BIA O&M funds.
Umatilla**
Umatilla - ODFW | Mission Critical - Well System | Efforts to initiate a comprehensive review of well system is ongoing. All essential needs (listed below) are linked to this review. Determination of path to address needs will be defined by end of calendar year. If emergencies arise, action will be addressed through BOG. |  |  | Bonneville working with ODFW and CTUIR on urgent electrical issues. $20,000 allocated in FY 2018 to assist in comprehensive review for specialized engineering services. Efforts to initiate a comprehensive review of well system is ongoing. Additional evaluation needed, TBD - Total cost unknown until a complete evaluation is completed - Well system provides a fraction of the flow the facility was designed for.
ODFW | Pump #3 |  |  |  | Estimate at $50,000. Efforts to initiate a comprehensive review of well system is ongoing. Pump #3 (rewire) and Well#1/pump#5 (rewire) have never been pulled (26years). See Mission Critical item above.
ODFW | Pump #5, Well #1 |  |  |  | Estimate at $20,000. Efforts to initiate a comprehensive review of well system is ongoing. Pump #3 (rewire) and Well#1/pump#5 (rewire) have never been pulled (26years). See Mission Critical item above.
ODFW | Chillers (4) 50 ton |  |  |  | Estimate at $194,000. Efforts to initiate a comprehensive review of well system is ongoing. Chillers are 25 years old and walls are thin from sand scour. Chillers need to be replaced. See Mission Critical item above.
ODFW | Submersible Pumps (2), 15 HP |  |  |  | Estimate at $30,000. Efforts to initiate a comprehensive review of well system is ongoing. Rewire pump. See Mission Critical item above.
ODFW | Production Well , 50 HP Submersible |  |  |  | Estimate at $20,000. Pump equipment condition is good, but well does not produce what it should. Has been rehabilitated, but no lasting benefit. See Mission Critical item above.
ODFW | Production Well #3, 25 HP Submersible |  |  |  | Estimate at $25,000. Pump equipment condition is good, but well does not produce what it should. See Mission Critical item above.
ODFW | Production Well #4, 60 HP Submersible |  |  |  | Estimate at $25,000. Pump equipment condition is good, but well does not produce what it should. Has been rehabilitated, but no lasting benefit. Well is degrading further have lost 150gpm since May. See Mission Critical item above.
Acclimation Sites (#8) - CTUIR | NA | NA | NA | NA | In the near future, the CTUIR annual budgets are sufficient to take care of required O&M as identified in the hatchery assessments.
Kootenai - KTOI | NA | NA | NA | NA | Utilizing BIA Hatchery Cyclical Maintenance Grant.
Snake River Sockeye Propagation** - IDFG
Springfield | Mission Critical - Chiller system | 75000 | 75000 |  | Engineering services contracted to develop design and specifications for chilled water delivery system upgrade at Springfield Hatchery. Estimate based on hatchery assessment report and then includes an estimate on installation.
| Concrete Clarifier |  | 109250 |  | Undersized waste removal system necessitates modifications - upsize early rearing trough effluent piping to larger size & increase size of effluent clarifier system.
| Early rearing trough effluent piping |  |  | 195000 | Undersized waste removal system necessitates removal of only 1 cleaning standpipe at a time. Modification by increasing the diameter of tough effluent piping. This in conjunction with increasing the size of effluent clarifier system will allow 500 gpm influent rate. This will also allow inside vat cleaning to be more efficient and will enhance bio-security in the early rearing building and eliminate the multiple removal of sludge from the clarifier on an annual basis. Estimate reflects estimate of modify troughs with large diameter piping and not replacement of troughs.
Eagle | 2 Fiberglass Transportation Tanks (250 gallon) | 16500 |  |  | Fiberglass transport tank for hauling sockeye adults from the RFLC trap to Eagle or in some years from Lower Granite Dam to Eagle are at the end of their life expectancy. These tanks have been rebuilt and refiberglassed a number of times and continue to leak water. Water is also damaging the internal wooden framework as water is trapped within fiberglassed shell. Price quotes to replace this tank have been requested from JetCo at an estimated cost of $8,250 each.
| Well #3: VFD Unit | 11500 |  |  | Due to the age of this critical unit, replacement is necessary.
| Well #1: 50 Hp submersible pump |  | 9000 |  | Pump is 5 years old, due to be replaced and refurbished for backup.
| Well #1 & #2 Degassing Tower Water Level Sensor. |  | 120000 |  | Aeration column needs minor modification to improve flow through dispersion plate. This unit has failed in cold damp winter conditions and is bypassed for this reason. (Discussions with an electrician to move this unit into the Well #2 building have been initiated, but no cost estimate at this time)
| Chiller (100 TON) |  |  | 84500 | Adult holding chiller needs to be replaced, old R-22 refrigerant filled chiller. Conversion needed to Freon or replace with new unit, whichever is deemed appropriate.
Colville - CCT | Chiller (15 TON APPROX) | 42000 |  |  | Leaks Freon, needs to be replaced
| Aluminum Troughs (14), 21' X 2.75' |  | 74200 |  | Inside rearing troughs are corroding and pinhole leaks observed, need to be replaced
| Aluminum Troughs (6), 16' X 1.3' |  |  | 15000 | Inside rearing troughs are corroding and pinhole leaks observed, need to be replaced
Nez Perce Tribal Hatchery** - NPT
NPTH | Mission Critical - river water filtration system |  |  |  | Additional evaluation needed - Relationship of this high priority item, in association to the Snake River Basin Steelhead Kelt Reconditioning Facility Master Plan (Project #2007-401-00). Kelt decision anticipated in 2018.
| Mission Critical - heat exchanger |  |  |  | Additional evaluation needed, TBD - Relationship of this high priority item, in association to the Snake River Basin Steelhead Kelt Reconditioning Facility Master Plan (Project #2007-401-00). Kelt decision anticipated in 2018.
| UV Disinfection System |  | 92000 |  | Treatment effectiveness is affected by fine sediment. Link to mission critical element (surface water filtration element)
Yoosa Creek | Mission Critical - Yoosa Creek Intake Bypass Flow |  |  |  | The dam structure that impounds water for the intake leaks significantly enough to reduce intake flow. NPT are evaluating the cost benefit of this need as part of hatchery evaluation.
Lukes Gulch | Paint 20' diameter Aluminum Circular Tanks (16) |  | 20000 |  | Paint is worn through on interior surfaces and faded.
Grande Ronde Supplementation
Lostine - NPT | Alarm System, Flow Detection | 30000 |  |  | Has been partially damaged by erosion. Needs to be repaired.
Catherine Creek - CTUIR | NA | NA | NA | NA | In the near future the CTUIR annual budgets are sufficient to take care required O&M as identified in the hatchery assessments.
Upper Grande Ronde - CTUIR | NA | NA | NA | NA | In the near future, the CTUIR annual budgets are sufficient to take care of required O&M as identified in the hatchery assessments.
Fall Chinook Acclimation Facilities - NPT***
Pittsburg | Water Supply and Drain Hoses |  | 27750 |  | Hoses are getting brittle.
| Feed Storage Building |  |  | 5625
| Resident 1, Camp Trailer |  |  | 25500 | 21 years old, due for replacement.
Big Canyon | Flexible Hoses for Water Supply/Drains |  | 27250 |  | Hoses are getting brittle.
| Residence 1, Park Model Trailer |  |  | 25500 | 19 years old, due for replacement.
Captain John Rapids | Alarm System, Low Water Level and No Flow Detection |  | 20000
| Electrical System Improvements |  |  | 5000 | Generator currently feeds through main breaker, no power to pumps if breaker fails.
| Supplemental Oxygen System |  |  | 10000
Lake Roosevelt Resident**
Sherman - WDFW | Mission Critical - Lake Water Pumps |  |  | 30000 | Additional evaluation needed, TBD - Cost @ $30,000. Move pumps and extend to deeper water to maintain flow during reservoir drawdown. Design through procurement is advisable (plus permitting and etc.). In addition, relation to future proposed use of hatchery is needed.
WDFW | Mission Critical - Net Pens |  |  | TBD | Additional evaluation needed, TBD. Reservoir drawdown causing early release of fish and the effect on program goals, current location does not function during reservoir drawdown.
Kalispel** - KT | Mission Critical - Alarm system |  |  | 50000 | Additional evaluation needed, TBD - Cost @ $50,000. Original System is non-functional and no longer supported. Activities at the hatchery are dependent on a future review. This item may be funded as part of the ongoing cold-water conversion program upgrades. This program has phased out of LMB and raising triploid trout for put-and-take.
Total |  | 210000 | 579450 | 465125
Variation Expected (+35%) with cost confirmation and installation costs. |  | 283500 | 782258 | 627919
*Essential Maintenance/Improvements --These items are considered essential for the facility to continue to perform the mission that was originally identified as the purpose for the facility relative to the relevant BPA Program, but the need is less immediate than mission critical elements.
** Hatcheries facilities that have unresolved Mission Critical Elements that need to be addressed
***BPA and LSRCP staff are currently working on determining project overlap, items listed under these facilities will be addressed once that exercise is complete.