## Slide 1: Assumptions used for Adequacy Assessments
Steering Committee Meeting
March 9, 2012

## Slide 2: Why talk about assumptions?
Garbage in, garbage out! “Let’s go dumpster diving!”
Results sensitive to key assumptions
Adequacy assumptions ≠ resource planning assumptions

## Slide 3: Adequacy Assumptions
Market supply
Market access
Borrowed hydro
Wind
Thermal resources and conservation
Standby resources
How to deal with uncertainty in load and conservation

## Slide 4: Adequacy Assessment ≠ Resource Planning
Adequacy Assessment = early warning, should resource development fall short
Resource Planning = acquisition strategy that produces an adequate, efficient, economical and reliable power supply
Adequacy assessment is a part of resource planning

## Slide 5: Treatment of Market Supply Adequacy vs. Resource Planning
Adequacy = realistic assumption for available market and non-firm supply during periods of stress
Resource Planning = policy decision, based on economic considerations, about how much market supply to plan for

## Slide 6: In-region Market
Made up of independent power producers
October-April
  Full capability (about 3,500 MW)
May-September
  1,000 MW max

## Slide 7: Out-of-region Market
Assumed to be from SW coming in over the NW-SW interties
Oct-Apr (on peak)
  Min of tie capacity and once-through-cooling adjusted surplus
  About 3,200 MW 2015, lower for 2017
May-Sep (on peak)
  None
May-Sep (off peak, purchase ahead)
  1000 MW

## Slide 8: Market Access – Not Modeled Due to difficulties in defining or coding
Market “friction” – inefficiencies in market transactions
Sell-ahead market – pre-committed resources could limit supply
Transmission bottlenecks – some utilities don’t have full access to all markets
Will use uncertainty in load/conservation as a surrogate for this

## Slide 9: Borrowed Hydro
Energy derived from drafting below “drafting right” elevations for short periods, then replaced as soon as possible
Available all months
Maximum allowable per month
  1,000 megawatt-months
Maximum used per hour
  Ranges from 2,500 to 3,000 MW

## Slide 10: Wind Resources
40 synthetic wind-year profiles, each profile contains 8,760 capacity factors that represent how wind would operate
Currently using historic 2008-10 data from BPA wind fleet
Future work to adjust for extreme temperatures
Need to develop wind profiles for other sites

## Slide 11: Thermal Resources and Conservation
Thermal resources
  Existing
  Expected to be operational by the study date
Conservation
  6th plan expected level by study date
  Built into the hourly load profiles

## Slide 12: Standby Resources
Resources or demand side actions
Contractually available to utilities
Not designed to be used often
Very small amounts
  Energy capability is 83,000 MW-hours per year
  Capacity 662 MW (Oct-Apr) and 722 MW (May-Sep)

## Slide 13: Uncertainty in Loads and Conservation
Economic load growth and conservation assumptions are essentially point forecasts
How can we address the uncertainty in these values?
Solution = use the range of uncertainty to delineate between the red, yellow and green status for the power supply
Calculate LOLPU, which is the LOLP assessed with higher loads and lower conservation

## Slide 14: Alert Status
Red = warning, resources are too low LOLP > 5%
Yellow = caution, resources getting low LOLP < 5% and LOLPU > 5%
Green = adequate LOLPU < 5%