## Slide 1: State of the System Report for 2015 Test Case for Illustration Only
Steering Committee Meeting
March 9, 2012

## Slide 2: Report Contents
Adequacy Level
Annual
Monthly
Hourly
Green, Yellow or Red
LOLP and other adequacy metrics
Probability curves for:
1) Total curtailed energy and
2) Highest single-hour curtailment
LOLP & Standby Resource use
Probability curves for:
1) Market purchases and
2) Borrowed hydro generation
Probability curves for:
1) Market purchases and
2) Borrowed hydro generation
Statistics
Size, frequency, duration of curtailment
Conditions during curtailments

## Slide 3: Preliminary Adequacy Assessment for 2015
Supply is adequate
Most critical months are Dec, Jan and Aug
Borrowed hydro used most often during summer
Adequacy depends on fair amount of market purchases
  December average = 23% of total market (1,500 MW-mo)
  August average = 30% of total market (600 MW-mo)
Full amount of market purchases made under 1% of time
System becomes inadequate when combined increase in load and decrease in efficiency is about 2000 MW

## Slide 4: Preliminary Adequacy Assessment for 2015 - GREEN
Metric | Value | Units | Threshold
LOLP | 0.93 | Percent | 5 %
Use of Standby | 1.1 | Percent | N/A
CVaR (energy) | 6968 | MW-hours | N/A
CVaR (peak) | 516 | MW | N/A
EUE | 348 | MW-hours | N/A
LOLH | 0.3 | Hours/year | 0.8 to 2.4 Hours/yr

## Slide 5: Adequacy metrics and values
Adequacy Metrics | 
Metric | Description
LOLP | Loss of load probability = number of games with a problem divided by the total number of games
Use of Standby | Number of games that dispatch standby resources at least once divided by total games
CVaR (energy) | Conditional value at risk = average annual curtailment for 5% worst games
CVaR (peak) | Conditional value at risk = average single-hour curtailment for worst 5% of games
EUE | Expected unserved energy = total curtailment divided by the total number of games
LOLH | Loss of load hours= total number of hours of curtailment divided by total number of games

## Slide 6: Total Annual Energy Curtailment Probability Curve*
*Prior to dispatching standby resources
Standby resource energy = 83,000 MW-hours per year
Resulting Energy LOLP (after dispatching standby resources) = 0.07%
Chart: Probability of Exceeding

## Slide 7: Highest Single-Hour Curtailment Probability Curve*
*Prior to dispatching standby resources
Standby resource capacity = 662 MW in winter and 722 MW in summer
Resulting Capacity LOLP (after dispatching standby resources) = about 1%
Chart: Probability of Exceeding

## Slide 8: Monthly LOLP (Months are treated independently)
Chart: Percent
| Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Ann
 | 0.071429 | 0 | 0.42857 | 0.35714 | 0 | 0.071429 | 0 | 0 | 0 | 0 | 0.14286 | 0 | 0.93

## Slide 9: Standby Resource Use Probability (Months are treated independently)
Chart: Percent
| Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Ann
SRUP | 0.14286 | 0 | 0.57143 | 0.35714 | 0 | 0.14286 | 0 | 0 | 0 | 0 | 0.42857 | 0 | 1.1

## Slide 10: Market Purchases by Month
Chart: MW-Months
| Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep
Avg | 518.2714 | 1365.6333 | 1469.9857 | 780.9 | 730.1905 | 531.6905 | 247.9667 | 44.7333 | 108.2667 | 277.0952 | 590.2905 | 425.8619
90th Percentile | 193.7286 | 649.3667 | 929.0143 | 1166.1 | 1160.8095 | 1074.3095 | 501.0333 | 117.2667 | 71.7333 | 259.9048 | 343.7095 | 144.1381

## Slide 11: Average Monthly Market Purchase Probability
Chart: Probability of Exceeding

## Slide 12: Likelihood of Borrowed Hydro Use
Chart: Percent
| Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep
Avg | 58.1 | 5.7 | 13.8 | 1.9 | 2.4 | 1 | 1.9 | 0 | 8.1 | 40.5 | 87.1 | 79

## Slide 13: Borrowed Hydro by Month*
Chart: MW-hours
| Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep
Avg | 6163.0762 | 237.1762 | 1370.9619 | 1544.1571 | 329.1714 | 437.2857 | 167.1238 | 0 | 12187.6762 | 35357.7286 | 48835.081 | 3528.4905
*Average of most used per month

## Slide 14: Borrowed Hydro by Event
Chart: Probability of Exceeding

## Slide 15: Market Purchases by Hour
Chart: Probability
| 6.40040962621608E-4 | 7.1684587813620096E-2 | 0.32130056323604744 | 0.64132104454685124 | 0.96134152585765464 | 1.2813620071684584 | 1.9214029697900672 | 2.5614439324116738 | 3.201484895033281 | 3.8415258576548901 | 6.4016897081413244 | 12.802099334357404 | 19.202508960573471 | 25.602918586789553 | 32.003328213005631 | 38.403737839221712 | 44.804147465437758 | 51.204557091653854 | 57.604966717869942 | 64.005376344085974 | 76.80619559651818 | 89.607014848950328
Oct | 2054 | 2030 | 2030 | 1030 | 1030 | 1030 | 1030 | 1030 | 1030 | 1023 | 1015 | 923 | 843 | 742 | 736 | 736 | 659 | 555 | 555 | 524 | 416 | 224
Nov | 6585 | 5585 | 3585 | 3535 | 3461 | 3213 | 3068 | 2801 | 2583 | 2563 | 2563 | 2079 | 1933 | 1776 | 1449 | 1449 | 1449 | 1307 | 1036 | 766 | 223 | 0
Dec | 6585 | 6585 | 6585 | 4094.8 | 3585 | 3561 | 3535 | 3461 | 3352 | 3227 | 2955 | 2563 | 2513 | 2069 | 1933 | 1812 | 1449 | 1449 | 1340 | 954 | 0 | 0
Jan | 6585 | 6585 | 6585 | 6585 | 5585 | 3905.3 | 3561 | 3514 | 3461 | 3426 | 2915 | 2563 | 1933 | 1741 | 1449 | 1263 | 648 | 0 | 0 | 0 | 0 | 0
Feb | 6585 | 6585 | 4117.6 | 3585 | 3561 | 3531 | 3456 | 3213 | 3013 | 2868 | 2563 | 2079 | 1893 | 1449 | 1263 | 482 | 0 | 0 | 0 | 0 | 0 | 0
Mar | 6585 | 6585 | 3616.6 | 3561 | 3461 | 3452 | 3213 | 3203 | 2955 | 2839 | 2563 | 2315 | 1933 | 1517 | 1449 | 997 | 408 | 0 | 0 | 0 | 0 | 0
Apr | 6585 | 3476 | 3300 | 2848 | 2583 | 2543 | 2086 | 1933 | 1933 | 1933 | 1449 | 985 | 427 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1933 | 1449 | 1421 | 879 | 704 | 665 | 654 | 598 | 555 | 519 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Jun | 2030 | 1030 | 1030 | 994 | 903 | 813 | 675 | 555 | 555 | 524 | 385 | 385 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Jul | 1030 | 1030 | 994 | 994 | 994 | 923 | 793 | 742 | 742 | 723 | 558 | 555 | 416 | 406 | 385 | 385 | 363 | 192 | 0 | 0 | 0 | 0
Aug | 2030 | 2030 | 1030 | 1030 | 1030 | 1030 | 1030 | 1015 | 994 | 994 | 994 | 742 | 630 | 555 | 555 | 549 | 416 | 416 | 408 | 385 | 0 | 0
Sep | 1030 | 1030 | 1030 | 1015 | 994 | 994 | 994 | 994 | 958 | 859 | 742 | 663 | 555 | 555 | 555 | 524 | 416 | 416 | 416 | 385 | 122 | 0

## Slide 16: Curtailment Events
 |  | Duration | Magnitude | Peak | Hydro | Forced Out | Temp | Wind
Game | Mon | hours | mw-hrs | mw-hrs | (%) | (%) | (%) | (%)
3 | Aug | 5 | 473 | 117 | 94 | 10 | 83 | 18
12 | Aug | 15 | 17647 | 1459 | 88 | 16 | 83 | 17
12 | Aug | 19 | 4911 | 479 | 88 | 17 | 48 | 2
16 | Jan | 8 | 6681 | 2970 | 89 | 8 | NA | 3
72 | Mar | 6 | 355 | 73 | 91 | 21 | 16 | 18
72 | Mar | 29 | 30340 | 2133 | 91 | 20 | 1 | 12
285 | Oct | 11 | 11006 | 1414 | 77 | 19 | 68 | 4
430 | Jan | 19 | 27248 | 1592 | 89 | 8 | NA | 67
781 | Dec | 39 | 44293 | 2125 | NA | 13 | 91 | 31
781 | Dec | 2 | 511 | 336 | NA | 9 | 100 | 61
855 | Aug | 17 | 11594 | 1064 | 94 | 17 | 58 | 3
913 | Jan | 35 | 37111 | 1928 | 84 | 9 | 1 | 22
918 | Dec | 5 | 2616 | 719 | 93 | 11 | 54 | 1
918 | Dec | 14 | 5909 | 554 | 93 | 13 | 54 | 3
918 | Dec | 2 | 1615 | 842 | 93 | 10 | 54 | 16
931 | Jan | 72 | 179994 | 5660 | 87 | 9 | NA | 5
940 | Dec | 8 | 51790 | 7800 | 98 | 11 | 88 | 42
995 | Oct | 3 | 1698 | 624 | 77 | 16 | 55 | 1
995 | Dec | 12 | 30110 | 3583 | 96 | 12 | 80 | 19
1068 | Aug | 1 | 166 | 166 | 94 | 17 | 65 | 62
1068 | Aug | 20 | 7017 | 707 | 94 | 18 | 65 | 42
1203 | Dec | 2 | 235 | 230 | 91 | 5 | 69 | 36
1259 | Jan | 11 | 14409 | 2460 | 79 | 3 | 1 | 7

## Slide 17: Curtailment Statistics
Statistic | Value | Unit
Expected Events/year | 0.02 | Events
Average Event Duration | 15 | Hours
Average Event Magnitude | 21206 | MW-hrs
Average Event Peak | 1697 | MW
Expected Curt Hours/year | 0.3 | Hours
% of games With curtailment | 1.1 | %

## Slide 18: Conditions during August Curtailment Event