## Slide 1: Big Wind Study
Resource Adequacy Technical Committee Meeting
April 6, 2011

## Slide 2: Purpose of Study
Estimate the Effective Load Carrying Capability (ELCC) for NW wind turbines
Quantify the relationship between installed wind generation and light-load-hour overgeneration
Examine the effects of wind generation on thermal resource dispatch

## Slide 3: Caveats
Results are not for distribution
BiOp data needs updating (again!)
Still working on hydro shaping logic in GENESYS
Used constant DEC requirements for all studies
Ran limited number of games with sequential hydro, lockstep temperature and random wind

## Slide 4: Wind ELCC Assumptions
2015 operating year
Existing resources
Expected new conservation (short-term model)
Ran Dec-Feb and Jul-Sep only
Base case
  Removed all wind
  Calculated total annual average curtailment per game
Study cases
  Added 200 MWa of shaped load
  Added increments of wind capacity until the total annual average curtailment per game equaled that in the base
  Repeated above with greater amounts of load

## Slide 5: Wind ELCC Results (200 MWa)
Chart: Average Load/Wind Capacity (%)
| 0.4 | 0.2
Study | 1372179.8 | 1207592.5
Base | 1259934 | 1259934

## Slide 6: Wind ELCC Results
 |  | Average | Inc
Load Inc (MWa) | Wind Inc (MW) | ELCC (%) | ELCC (%)
200 | 759 | 26.4 | 26.4
400 | 1746 | 22.9 | 19.5
600 | 2762 | 21.7 | 17.0
800 | 3963 | 20.2 | 14.0
1000 | 5746 | 17.4 | 8.4
1200 | 7939 | 15.1 | 3.9

## Slide 7: Wind ELCC Results
Chart: Installed Wind Capacity (MW)
| 758.71576296002843 | 1746.2011539831865 | 2761.787408539727 | 3962.6618356884987 | 5746.0149429212215 | 7939.4772271509182
Average | 0.2636 | 0.22907 | 0.217 | 0.20188 | 0.17403 | 0.15114
Incremental | 0.2636 | 0.19453 | 0.1704 | 0.14017 | 0.084464 | 0.038684

## Slide 8: Overgeneration Study Assumptions
210 games, sequential hydro, lockstep thermal and random wind (screening studies)
2015 regional loads
Existing resources
2015 Power Plan conservation (1,200 MWa)
No thermal ramping logic (results in lower overgeneration values)
Wind was added with no additional load

## Slide 9
Chart: Average Overgeneration Energy by Month
| 0 | 3 | 4 | 5 | 6 | 7 | 8
Oct | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nov | 0 | 0 | 0 | 0.0094 | 0.0866 | 0.1651 | 0.2359
Dec | 0 | 0 | 0 | 0 | 0 | 0 | 0
Jan | 0 | 0.0233 | 0.2441 | 0.9806 | 2.7968 | 5.8685 | 9.5472
Feb | 11.5547 | 37.7447 | 52.7326 | 72.8713 | 98.1258 | 129.1893 | 162.9765
Mar | 38.0096 | 72.1211 | 90.2106 | 112.4171 | 138.9676 | 169.1186 | 198.7922
Apr | 39.551 | 125.3337 | 174.721 | 237.476 | 313.4248 | 395.2675 | 470.7106
May | 600.9803 | 964.1528 | 1117.9035 | 1287.2669 | 1466.9439 | 1645.235 | 1806.8815
Jun | 585.5059 | 889.6115 | 1022.7482 | 1170.2349 | 1327.0478 | 1483.0421 | 1627.2469
Jul | 64.4428 | 141.4669 | 180.0701 | 225.3809 | 278.043 | 335.7091 | 393.7941
Aug | 0.0299 | 0.9215 | 1.9688 | 3.7541 | 6.6744 | 10.2933 | 14.1593
Sep | 0 | 0.0003 | 0.0217 | 0.1464 | 0.6131 | 1.2757 | 1.8723

## Slide 10
Chart: Overgeneration in Average Megawatts (averaged over all hours of the month)
| 0 | 3 | 4 | 5 | 6 | 7 | 8
Oct | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nov | 0 | 0 | 0 | 0.013056 | 0.12028 | 0.22931 | 0.32764
Dec | 0 | 0 | 0 | 0 | 0 | 0 | 0
Jan | 0 | 0.031317 | 0.32809 | 1.318 | 3.7591 | 7.8878 | 12.8323
Feb | 17.1945 | 56.1677 | 78.4711 | 108.4394 | 146.0205 | 192.246 | 242.5246
Mar | 51.0882 | 96.937 | 121.2508 | 151.0983 | 186.7844 | 227.3099 | 267.1938
Apr | 54.9319 | 174.0746 | 242.6681 | 329.8278 | 435.3122 | 548.9826 | 653.7647
May | 807.7692 | 1295.9043 | 1502.5585 | 1730.1974 | 1971.6988 | 2211.3374 | 2428.6042
Jun | 813.2026 | 1235.5715 | 1420.4836 | 1625.3262 | 1843.1219 | 2059.7807 | 2260.0651
Jul | 86.6167 | 190.1437 | 242.0297 | 302.9313 | 373.7137 | 451.2219 | 529.2931
Aug | 0.040188 | 1.2386 | 2.6462 | 5.0458 | 8.971 | 13.8351 | 19.0313
Sep | 0 | 0.00041667 | 0.030139 | 0.20333 | 0.85153 | 1.7718 | 2.6004

## Slide 11
Chart: Highest Hour Overgeneration by Month
| 0 | 3 | 4 | 5 | 6 | 7 | 8
Oct | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nov | 0 | 0 | 0 | 543.3 | 1094.4 | 1129.1 | 1216.4
Dec | 0 | 0 | 0 | 0 | 0 | 0 | 0
Jan | 0 | 788.7 | 1713.3 | 2637.9 | 3038.2 | 3184.2 | 3388.8
Feb | 3216.5 | 5708.4 | 6618.7 | 7594 | 7976.9 | 7976.9 | 7976.9
Mar | 4513.4 | 6510.7 | 7443.5 | 8376.3 | 8702.9 | 8991.1 | 8991.1
Apr | 3263.9 | 5911.9 | 6907.9 | 7530.7 | 7697.9 | 7697.9 | 7728.7
May | 5749.3 | 8453.4 | 9440.3 | 10277.4 | 10336.4 | 10336.4 | 10336.4
Jun | 7193.6 | 9542 | 10441.2 | 11342.1 | 11843 | 11843 | 11843
Jul | 7184.3 | 9630.9 | 10509.1 | 11387.3 | 11924.5 | 11924.5 | 12039.2
Aug | 508.9 | 2562.7 | 3441.2 | 4368.9 | 5650.4 | 6510 | 6729
Sep | 0 | 62.7 | 1037.1 | 1889.2 | 1889.2 | 1946 | 1955.7

## Slide 12
Chart: Average Monthly Dispatch Boardman
| Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep
0 | 344.48 | 377.73 | 375.77 | 262.66 | 261.45 | 249.33 | 138.57 | 48.151 | 104 | 286.78 | 395.84 | 392.09
3000 | 326.43 | 366.82 | 365.81 | 238.77 | 230.95 | 218.29 | 108.62 | 30.492 | 82.837 | 252.23 | 384.03 | 382.36
6000 | 291.42 | 346.18 | 345.09 | 211.64 | 200.29 | 186.24 | 78.636 | 18.694 | 61.009 | 212.12 | 358.54 | 351.89

## Slide 13
Chart: Aggregate Hourly Dispatch for May No Wind Case

## Slide 14
Chart: Aggregate Hourly Dispatch for May 3000 MW Wind Case

## Slide 15
Chart: Aggregate Hourly Dispatch for May 6000 MW Wind Case

## Slide 16: Next Steps
Update BiOp data
For overgeneration study, run scenarios with no thermal cycling – to assess worst case magnitude
Continue to review hydro shaping logic
Explore adding ramping logic for thermals