## Slide 1: Vetting the GENESYS Model
Resource Adequacy Technical Committee Meeting Portland, Oregon June 23, 2011

## Slide 2: Purpose
To ensure that the GENESYS model accurately represents how regional resources are used.

## Slide 3: Method
Validation involves checking simulated resource dispatch against actual dispatch.
Patterns in the simulated dispatch are checked for consistency with actual dispatch patterns under various load, hydro and wind conditions.

## Slide 4: How do we ensure that GENESYS accurately reflects resource operation?
Compare historical vs. simulated hourly dispatch
  For aggregate resources types (hydro, thermal, wind)
  For thermal fuel types (coal, gas, nuclear)
  For individual resources
Check simulated dispatch for
  Under-supply conditions
  Over-supply conditions
  Various wind and hydro conditions
Adequacy Forum’s technical committee is tasked with reviewing the simulation

## Slide 5: Checking Simulated Dispatch
Check under-supply conditions All resources should be dispatched
Check over-supply conditions All resources that can be turned off should be off
Check individual resource dispatch
  Ensure resources are dispatched in the right order (i.e. thermal displaced first when wind picks up)
  Ensure individual resource dispatch makes sense

## Slide 6: Caveats
The following slides show both simulated and actual resource dispatch
  Actual resource dispatch is provided by BPA for its balancing authority area.
  Simulated resource dispatch is produced by the GENESYS model and covers the NW region.
The scales are quite different and the relationships of loads to resources are different as well (e.g., for BPA hydro is much bigger than load).

## Slide 7: Check Under-Supply Conditions

## Slide 8
Chart: Historic Under-Supply Condition - Dec 2009
Actual Hourly Dispatch

## Slide 9: Simulated Hourly Dispatch*
Chart: Hour of Month (1 = 1 am day 1)
*Not all resources are shown

## Slide 10: Under-Supply Condition
Chart: Days 7 and 8 - Under-Supply Simulated Dispatch
Load | 36191 | 35602 | 34729 | 33927 | 33221 | 32786 | 33107 | 34976 | 37308 | 36552 | 35265 | 33518 | 30940 | 28523 | 27832 | 27241 | 27088 | 27379 | 28402 | 30952 | 34847 | 37326 | 37696 | 37378 | 36749 | 35853 | 35051 | 34348 | 33907 | 34231 | 36130 | 38543 | 38832 | 37816 | 36478 | 34628 | 31912 | 29384
Therm | 15555 | 15461 | 15461 | 15461 | 15461 | 15461 | 15461 | 15461 | 15488 | 15364 | 15131 | 15131 | 15131 | 15131 | 15131 | 15131 | 15131 | 15416 | 15422 | 15422 | 15422 | 15422 | 15422 | 15422 | 15422 | 15422 | 15422 | 15422 | 15422 | 15422 | 15422 | 15422 | 15422 | 15422 | 15422 | 15422 | 15422 | 15422
Purc | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
Hydro | 17478 | 16910 | 15618 | 14014 | 13315 | 12878 | 14026 | 16421 | 18750 | 17995 | 16709 | 14423 | 11467 | 9049 | 6826 | 6473 | 6347 | 6768 | 7611 | 9877 | 14475 | 16831 | 17820 | 17598 | 17093 | 15650 | 14063 | 13406 | 12984 | 14125 | 16554 | 18968 | 19258 | 18146 | 16852 | 14507 | 11301 | 8747
Wind | 139 | 118 | -2 | -10 | -18 | -16 | -17 | -18 | -16 | -17 | -17 | -18 | -17 | -17 | 517 | 280 | 252 | 123 | 303 | 587 | 800 | 923 | 304 | 208 | 85 | 92 | 67 | 20 | 1 | 10 | 5 | 3 | 2 | 99 | 55 | 10 | 123 | 148

## Slide 11: Check Over-Supply Conditions

## Slide 12
Chart: Historic Over-Supply Condition - May 2011
Actual Hourly Dispatch
Thermal mostly off
Hydro shows max flexibility including providing additional spill

## Slide 13: Simulated Hourly Dispatch
Chart: Simulated Hourly Generation - May '98 Water
DEC minimum for within hour balancing (does not show the within hour variation)

## Slide 14: Over-Supply Condition
Chart: First 2 Days - Over-Supply Simulated Dispatch
Load | 15817 | 15473 | 15385 | 15611 | 16433 | 18280 | 20716 | 21912 | 21896 | 21588 | 21244 | 20835 | 20497 | 20162 | 19869 | 19719 | 19771 | 19969 | 20394 | 20757 | 20926 | 20199 | 18412 | 16761 | 15013 | 14690 | 14599 | 14804 | 15574 | 17315 | 19631 | 20773 | 20765 | 20478 | 20155 | 19768 | 19443 | 19124 | 18846 | 18698 | 18731 | 18891 | 19257 | 19573 | 19738 | 19091 | 17436 | 15891
Thermal | 882 | 882 | 882 | 882 | 882 | 882 | 896 | 896 | 896 | 896 | 896 | 896 | 896 | 896 | 896 | 896 | 896 | 896 | 896 | 896 | 896 | 896 | 882 | 882 | 882 | 882 | 882 | 882 | 882 | 882 | 882 | 882 | 882 | 882 | 882 | 882 | 882 | 882 | 882 | 882 | 882 | 882 | 882 | 882 | 882 | 882 | 882 | 882
Hydro | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 20569 | 21764 | 21750 | 21439 | 21070 | 20132 | 18968 | 18551 | 18337 | 18905 | 18966 | 18752 | 19932 | 20218 | 20406 | 19238 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596 | 17596
Wind | -11 | -14 | -29 | -29 | -29 | -32 | -28 | -27 | -29 | -26 | -1 | -13 | 4 | 86 | 7 | 113 | 630 | 1042 | 287 | 364 | 345 | 246 | 272 | 675 | 4027 | 4114 | 5005 | 5193 | 5927 | 5789 | 2972 | 2960 | 5977 | 5732 | 5212 | 5971 | 5964 | 5971 | 5964 | 5951 | 5964 | 5971 | 5237 | 2734 | 2885 | 3054 | 3593 | 3500

## Slide 15: Check Individual Resource Dispatch

## Slide 16: Simulated Winter* Dispatch for Bennett Mountain (gas)
Chart: Hour of Month (1 = 1 am day 1)
Dispatched when needed
*Summer capacity is 165 MW. On 1/31/11 it was dispatched at 182 MW.

## Slide 17: Historical Daily Dispatch Bennett – August* 2010
Chart: Bennett Mountain
 | 0 | 0 | 117.1449 | 153.6585 | 144.5385 | 143.0186 | 131.8 | 0 | 0 | 140.1246 | 0 | 142.351 | 148.7813 | 0 | 0 | 155.4949 | 151.5886 | 154.773 | 155.5799 | 153.6404 | 0 | 0 | 160.7544 | 162.5607 | 152.9828 | 151.575 | 0 | 0 | 0 | 0 | 0
*Summer capacity is 165 MW. On 1/31/11 it was dispatched at 182 MW.

## Slide 18: Simulated Dispatch for Boardman (coal)
Chart: Hour of Month (1 = 1 am day 1)
Base loaded plant

## Slide 19: Next Steps
Add seasonal capacity values to the simulation
  GENESYS currently uses winter capacity values only because until recently the region focused on winter problems
  Seasonal capacity values are easily added via data tables
Add ramping rate logic
  First issue is to get good data
  Logic to implement ramping is not yet in the model
  Coal “day-must” run logic is in the model