## Slide 1: Hydro Peaking Capacity Analysis & Northwest Regional Forecast Comparison
Resource Adequacy Technical Committee
July 28, 2010

## Slide 2: What’s Being Compared
Northwest Regional Forecast
April 2010
PNUCC
Regional Sustained Hydro Peaking Analysis
DRAFT Phase II Report
May 12, 2010
Don Long Services
2009 Pacific Northwest Loads & Resources Study
(a.k.a. White Book)
July 2009
BPA

## Slide 3: D. Long Results Look Good
Spot checked individual projects
  Project capacity values reasonable
  Consistent with other analyses
Provides insights
Highlights key issues

## Slide 4: Observation One
Big difference between instantaneous peak and sustained peak estimates
  14 Federal Projects (Jan. 1937)
  Instantaneous Peak (NRF) 20,508 MW
  1-hr Sustained Peak (D. Long) 12,204 MW

## Slide 5: Observation Two
D. Long’s one-hour &18-hour sustained peak capacity nearly identical
  14 Federal Projects (Jan. 1937)
  1-hr Sustained Peak 12,204 MW
  18-hr Sustained Peak 12,437 MW

## Slide 6: Observation Three
Amount of energy GREATLY effects sustained peak capability
  14 Federal Projects (Jan. 1937)
  (Monthly Energy -- 1-hr Sustained Peak)
  7,200 MWa -- 16,568 MW Whitebook
  5,600 MWa -- 13,693 MW NRF
  ???MWa -- 12,204 MW D. Long

## Slide 7: Observation Four
Treatment of Hydro Maintenance and Reserves is important

## Slide 8: Use of D. Long’s Work
Need for Power Assessments (2011 NRF)
Resource Adequacy Assessment – How?