## Slide 1: Northwest Resource Adequacy Forum "Non-hydro" Resources for the 2010 Resource Adequacy Assessment
July 27, 2010
1
Jeff King
Northwest Power & Conservation Council
July 28, 2010
Notes: AURORAxmp® Electric Market Model
7/27/2010

## Slide 2: Net capacity to GenRes: 2010 vs. 2008 assessments

## Slide 3: I. Screening
Included in GenRes file
  Projects in ID, MT, OR & WA, plus Bridger 1 - 4, IPC shares of Valmy 1 and 2 and PNW share of Foote Creek Wind
  Operating, standby or under construction as of June 2010
Exceptions:
  Regulated and Independent hydropower projects
  Eastern MT projects interconnected to the MRO grid
  Eastern MT Projects interconnected to WECC serving WAPA load
  Planned, idle and suspended projects
  Wastewater treatment energy recovery units unless known to hold a PPA
  100% self-generation projects

## Slide 4: II. Capacity to GenRes
Base capacity priorities (except wind and solar)
  White book January 1-hour capacity
  WECC winter capacity
  Installed capacity
Wind and solar - Installed capacity (John adjusts later)
Adjustments (except wind and solar)
  NorthWestern owned or contracted - 67% derate
  PPL Montana capacity to system sales (13 projects, 962 MW) - 100% derate
  Non-firm power purchase agreements - 100% derate
  Projects owned by, or with long-term PPA to out-of-region utilities* - 100% derate
  Load-side emergency generators w/o announced DR contracts - 100% derate
  Small IPPs w/unknown loads (13 projects totaling 48 MW) - 100% derate

## Slide 5: Additions 2008 > 2010 (Installed MW)

## Slide 6: Wind contractual loads

## Slide 7: Removals 2008-10 (Installed capacity)
Plant | Type | Status | Capacity (MW)
18th St (Springfield ICs) | IC | Retired | 9.5

## Slide 8: Uncommitted IPP capacity (MW)
Plant | Type | 2008 GenRes | 2010 GenRes | Notes
Big Hanaford | CC | 248 | 248 | 
Centralia | Coal | 1240 | 1240 | PGE contract exp. 2016
Colstrip 4 | Coal | 111 | 0 | NWE ratebase
Grays Harbor | CC | 650 | 650 | 
Hardin | Coal | Excluded | 109 | Include? (PowerEx mkts)
Hermiston Power | CC | 530 | 630 | White Book vs. WECC
Klamath Cogen | CC | 480 | 484 | 
Klamath Peakers | GT | 100 | 100 | 
Mint Farm | CC | 319 | 0 | PSE acquisition
Morrow Power | GT | 25 | 25 | 
Total |  | 3702 | 3486 | 

## Slide 9: IPP detail

## Slide 10: Equivalent Forced Outage Rates
Type | 2008* | 2010**
Nuclear | 9.0% | 4.2%
Coal-steam | 7.0% | 6.7%
Combined-cycle | 5.0% | 5.9%
Gas Turbine (aero) | 10% | 5.1%
Gas Turbine (frame) | 7.0% | 5.1%
Reciprocating Engine | 8.0% | 4.7%
* 5th Power Plan values, derived from 2004 - 08 NERC GADS data.
** 6th Power Plan values, derived from earlier NERC GADS data.

## Slide 11: Issues
IPP projects dedicated to system sales?
  PPL Montana coal & hydro
  Hardin coal (to PowerEx)
"Planned" projects?
  Construction not commenced
  Announced service date on or before 2015
  Utility project approved by commission or board (e.g., Langley Gulch)
  IPP project w/permits, PSA, equipment order (e.g., Shepherd's Flat)