## Slide 1: Preliminary Resource Adequacy Assessment for the 2017 Pacific Northwest Power Supply
NW Resource Adequacy Forum Technical Committee Meeting August 16th

## Slide 2: Outline
Range of LOLP
Sensitivities
Review of Forum assumptions
Data that may need more review
Today’s committee decisions
Action items

## Slide 3: Range of LOLP (Illustrative)
7 |  |  |  |  |  | 13
5 |  |  |  |  |  | 
 | 5 |  | 7 |  |  | 
 |  | 5 |  |  |  | 
 |  |  | 5 |  |  | 
1 |  |  |  | 5 |  | 7
High Market, High Load
Low Market, High Load
High Market, Low Load
Low Market, Low Load

## Slide 4: Sensitivities
SW Market
Loads
Resources
Wind Data

## Slide 5: Sensitivity Studies (SW Market)
On-peak winter | LOLP (%) | LOLH (hrs/yr) | EUE (mw-hr)
0.0 GW | 11.9 | 6.2 | 8586
1.7 GW | 6.6 | 2.9 | 3142
3.0 GW | 5.9 | 2.2 | 1952

## Slide 6: Sensitivity Studies (Load)
Operating year loads | LOLP (%) | LOLH (hrs/yr) | EUE (mw-hr)
2017 | 6.6 | 2.9 | 3142
2015 | 3.9 | 1.3 | 1843

## Slide 7: Sensitivity Studies (Resources)
Resources | LOLP (%) | LOLH (hrs/yr) | EUE (mw-hr)
Existing | 6.6 | 2.9 | 3142
+ 170 MW CCCT | 6.4 | 2.4 | 2665

## Slide 8: Sensitivity Studies (Wind Data)
Wind Data (210 games) | LOLP (%) | LOLH (hrs/yr) | EUE (mw-hr)
Temp-Correlated | 5.2 | 1.8 | 1875
Non Temp-Correlated | 3.8 | 1.7 | 1216
Historic 2008-10 | 4.8 | 2.4 | 2514

## Slide 9: Other Sensitivities
Random variable correlations (e.g. should we lockstep temp and hydro?)
Starting seed and order of seeds for random draws
Number of games (may need > 1400)
Compiler?

## Slide 10: Review of Forum Assumptions
SW on-peak – 1.7GW winter, 0 summer
SW off-peak – 3GW winter, 1GW summer
Conservation – 6th plan expected
Resources – existing, licensed and sited
Loads – medium forecast

## Slide 11: Load Forecast

## Slide 12: Data that May Need More Review
SW Market availability
Wind data
Load Forecasts
Other?

## Slide 13: Today’s Committee Decisions
Sensitivity studies OK? If not, redo list.
Comfortable with the results? If not, identify areas that need more work.
Pass results to the steering committee? If not, postpone Aug 30th meeting.

## Slide 14: Action Items
Reassess SW market availability with more current and complete information
Review wind data more carefully, especially temp-correlated data
Review resource maintenance schedules
Review load forecasts