## Slide 1: Announced Coal Unit Retirements: Effect on Regional Resource Adequacy
Council Meeting January 16, 2013
Portland, Oregon
Boardman
Centralia

## Slide 2: Assignment
At the October Council meeting, Member Rockefeller asked:
‘How will the announced closure of coal units at Boardman and Centralia in 2020 affect regional resource adequacy?’

## Slide 3: Analysis Performed
Assessed regional resource adequacy in 2021 after Boardman and Centralia 1 are closed
Estimated how much additional dispatchable resource capacity is needed to make the regional power system adequate1 1The Council’s adequacy standard sets a maximum limit of 5 percent for the power supply’s loss of load probability.

## Slide 4: Summary of Projected Changes From now to 2021
Changes that Increase Need | Notes
Net Load Growth | 1,210 MWa or 0.6% growth rate, with 2,900 MWa of EE savings removed1
Boardman Retires | 510 MWa2 (601 MW nameplate)
Centralia 1 Retires | 620 MWa2 (730 MW nameplate)
1Percent of load growth met with EE is 71%.
2Assuming an 85% availability factor for coal-fired plants.

## Slide 5: Sixth Plan Target Efficiency Levels
Year | Incremental Savings (MWa) | Cumulative Savings from 2010 (MWa) | Cumulative Savings from 2013 (MWa)
2010 | 200 | 200 | 
2011 | 220 | 420 | 
2012 | 240 | 660 | 
2013 | 260 | 920 | 260
2014 | 280 | 1,2001 | 540
2015 | 300 |  | 840
2016 | 320 |  | 1,160
2017 | 340 |  | 1,500
2018 | 3502 |  | 1,850
2019 | 350 |  | 2,200
2020 | 350 |  | 2,550
2021 | 350 |  | 2,900
1Council’s target for 2014 is 1,200 MWa. 2EE savings past 2017 are limited by assumed ramp rates.

## Slide 6: Summary of Projected Changes From now to 2021
Changes that Reduce Need | Notes
Hydro Upgrades | 350 MWa
Thermal Resources | 115 MWa1 (124 MW nameplate)
RPS Resources | 1,200 MWa (4,000 MW nameplate)
1Assuming a 92% availability factor for gas-fired turbines.

## Slide 7: Generating Resource Additions In the Analysis (Cumulative)
Chart: Average Megawatts
| 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
Hydro | 30 | 83 | 100 | 350 | 350 | 350 | 350 | 350 | 350 | 350
Gas | 10 | 10 | 10 | 10 | 115 | 115 | 115 | 115 | 115 | 115
Wind | 0 | 150 | 300 | 450 | 600 | 750 | 900 | 1050 | 1200

## Slide 8: Loss of Load Probability
Chart: LOLP (%)
| 2013 | 2021 | B & C Retire | B & C Retire + 2,000 MW
LOLP | 8.3 | 15.3 | 5
-1,130 MWa Coal (1,330 MW)
+ 1,840 MWa New (2,000 MW)
+1,210 MWa Load +115 MWa Gas +350 MWa Hydro +1,200 MWa Wind

## Slide 9: Conclusions
2021 adequacy without Boardman, Centralia 15.3% LOLP
Additional dispatchable resource capacity needed to bring LOLP back to 5%: 2,000 megawatts

## Slide 10: Planned Resources Not in the Analysis (Cumulative)
Source: PNUCC
Chart: Nameplate Capacity MW
| 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
Gas | 200 | 1265 | 2060 | 2060 | 2060 | 2060 | 2060 | 2273 | 2273
Geo | 0 | 0 | 0 | 200 | 200 | 218 | 218 | 218
Bio | 6 | 6 | 6 | 20 | 20 | 20 | 20 | 51 | 51
Cogen | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Diesel | 0 | 52 | 52 | 52 | 52 | 52 | 52 | 52
Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31

## Slide 11: Additional Slides

## Slide 12: Adequacy Milestones
Year LOLP
2013 < 5%
2015 5%
2017 6.6%
2021 with coal units 8.3%
2021 without coal units 15.3%
2021 without coal, with 2,000 MW 5%

## Slide 13: Results
Step | Description | LOLP
1 | 2021 LOLP with Boardman and Centralia | 8.3%
2 | 2021 Without Boardman and Centralia | 15.3%
3 | 2021 Without Boardman and Centralia With 2,000 MW new dispatchable capacity | 5.0%
0 | 2017 LOLP | 6.6%