## forRPM
Ramp Rate | Resource Type | Measure Category | Sector | End Use | kW per unit | kWh per unit | TRC Net Levelized Cost (Net of All Benefits) | segment | measure | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | MAX | Savings Allocation by Category and Month for Segments 1 | [12 empty] | Savings Allocation by Category and Month for Segments 2
[5 empty] | Wholesale KW | Busbar Savings | lvlcost |  |  | aMW_2016 | aMW_2017 | aMW_2018 | aMW_2019 | aMW_2020 | aMW_2021 | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | MAX | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
LO5Med | NR | Data Centers | Commercial | Electronics | 0.060302 | 480.1237 | 10.2802 |  | Best Practice | 1.0714 | 2.5315 | 4.4144 | 6.4505 | 8.8788 | 11.8957 | 15.4657 | 18.9281 | 22.4328 | 25.7651 | 28.7516 | 30.9043 | 32.6363 | 34.0869 | 35.4167 | 36.5325 | 37.7337 | 39.0599 | 40.5281 | 42.0287 | 166.3435 | 23.1878 | 21.7873 | 24.7119 | 22.5162 | 23.0941 | 23.0205 | 22.0421 | 25.1444 | 21.6572 | 24.6048 | 21.2634 | 21.6498 | 0 | 18.6679 | 16.7918 | 16.7013 | 16.7824 | 16.9992 | 15.7588 | 17.7179 | 16.8851 | 17.6592 | 16.5661 | 17.423 | 17.4915
LO5Med | NR | Data Centers | Commercial | Electronics | 0.027848 | 221.7239 | 27.1572 |  | Commercial Technology | 0.4948 | 1.1691 | 2.0386 | 2.9789 | 4.1003 | 5.4935 | 7.1422 | 8.7411 | 10.3596 | 11.8985 | 13.2777 | 14.2718 | 15.0716 | 15.7415 | 16.3556 | 16.8709 | 17.4256 | 18.0381 | 18.7161 | 19.4091 | 76.8184 | 10.7083 | 10.0615 | 11.4121 | 10.3981 | 10.665 | 10.631 | 10.1791 | 11.6118 | 10.0014 | 11.3626 | 9.8196 | 9.998 | 0 | 8.6209 | 7.7546 | 7.7128 | 7.7502 | 7.8503 | 7.2775 | 8.1822 | 7.7976 | 8.1551 | 7.6503 | 8.0461 | 8.0777
LO5Med | NR | Data Centers | Commercial | Electronics | 0.006582 | 52.4058 | 20.9801 |  | Cutting Edge | 0.11695 | 0.27631 | 0.48183 | 0.70407 | 0.96913 | 1.2984 | 1.6881 | 2.066 | 2.4486 | 2.8123 | 3.1383 | 3.3732 | 3.5623 | 3.7206 | 3.8658 | 3.9875 | 4.1187 | 4.2634 | 4.4237 | 4.5875 | 18.1565 | 2.531 | 2.3781 | 2.6973 | 2.4577 | 2.5207 | 2.5127 | 2.4059 | 2.7445 | 2.3639 | 2.6856 | 2.3209 | 2.3631 | 0 | 2.0376 | 1.8328 | 1.823 | 1.8318 | 1.8555 | 1.7201 | 1.9339 | 1.843 | 1.9275 | 1.8082 | 1.9017 | 1.9092
Note on A1: Charlie Grist: Lookup in ComMaster
Note on B1: Charlie Grist: New, NR, Retro
Note on C1: Charlie Grist: Measure Index Name
Note on E1: Charlie Grist: Use Massoud's Names
Note on F1: Charlie Grist: From Shaped Savings column 14
Note on G1: Charlie Grist: From SC or from Shaped Savings column 3.
Note on H1: Charlie Grist: From SC or from Shaped Savings column K (column 11)
Note on I1: Charlie Grist: From SC
Note on J1: Charlie Grist: From SC
Note on K1: Charlie Grist: From SC. For shaping. RPM also uses this divided by savings per unit to calculate units, and then uses kW per unit * units to calculate kW.
Note on AF1: Charlie Grist: From Shaped Savings. Copy whole row down since column increment is hardwired into formula.

## 7PSourceSummary
Measure: | Data Centers
Item | Methods & Sources | Note | 7P Updates
Measures Described | Total of 22 efficiency measures divided into three tiers; Best Practice, Commercial Technology and Cutting Edge. Measures are described below. |  | New analysis from Cadmus.
Energy Savings Calculation Basis | Model developed by Cadmus and Masanet. Based on equipment upgrades and equipment turnover model. Also incorporates interaction with cooling and infrastructure requirements which impact PUE. Model uses seven categories of data center workload function (described below) | Masanet, E., Brown, R.E., Shehabi, A., Koomey, J.G., and B. Nordman (2011). “Estimating the Energy Use and Efficiency Potential of U.S. Data Centers. Proceedings of the IEEE, Volume 99, Number 8 | New for 7P. Based primarily on Masanet et al.
Baseline Energy Use | Based on CBSA 2014 data on data centers embedded in commercial buildings. Cadmus used power supply data, data center floor area, number of racks, HVAC system characteristics and other factors to estimate baseline energy use. |  | Baseline developed in workbook 'Embedded DC Analysis Tool'
Applicable Stock | All embedded data centers. Potential estimate is based on total load estimate from the Cadmus model. |  | New from Cadmus model
Baseline Saturation | Saturation for key measures (virtualization and ENERGY STAR servers) are based on CBSA survey results. Other key equipment saturations based on national estimates per sources noted in the model.
Baseline Penetration | Assume 20% due to significant market uptake of virtualization
Permutations | There 198 permutations of measure and function.
Costs | Costs for measures are from a variety of sources dated 2008-2014.
Measure Life | Five to fifteen years depending on hardware
Savings Shape | Flat - Use Total Industrial | Have not found measured shape data
Achievability Ramp Rate | Medium early. Most potential in virtualization and other fast uptake measures. | Retro5Med
| Tier 1: Best Practice |  | Function
| Decommissioning of unused servers |  | Servers
| Server virtualization/consolidation |  | Storage
| Server power management |  | Network
| Energy efficient data storage management |  | Transformer
UPS
Lighting
| Tier 2: Commercial Technology |  | Cooling
Energy efficient servers
Massive array of idle disks (MAID)
Efficient network topology
Energy efficient transformers
Energy efficient power supplies (UPS)
Energy efficient lighting
Hot or cold aisle configuration
Hot or cold aisle configuration plus containment (e.g., strip curtains or rigid enclosures)
Variable speed drives on pumps/fans
Premium efficiency motors
Air-side economizer
In-row cooling
Water-side economizer
Install misters, foggers, or ultrasonic humidifiers
Tier 3: Cutting Edge
Solid state storage
Efficient network topology
Direct current (as opposed to AC) to the racks
Direct liquid cooling of chips

## SC-NR
Units Methodology | Units are MWh of Embedded Data Center (EDC) load. Savings are kWh per MWh EDC load. Treated here as Retrofit for purposes of supply curve. Units analysis, including stock turnover components, are in the EDC model. EDC load is taken as the Business as Usual case (BAU) from the model. This model incorporates growth in demand for computation, turnover of equipment, increasing performance of new equipment entering the stock, existing saturations of efficient equipment, like virtualization, and other factors. Measure applicability is based on a baseline penetration estimated at 20%. Twenty two measures are bundled into three tiers.
| Vintage | NR | Stock
End-Use: | Measure Bundle | Data Centers-NR | Region
Electronics | Report Year | 2035 | Base
| Total Potential (aMW) | 261.3184 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
|  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | TOTAL MAX | TOTAL
|  |  |  | FLOOR_2016 | FLOOR_2017 | FLOOR_2018 | FLOOR_2019 | FLOOR_2020 | FLOOR_2021 | FLOOR_2022 | FLOOR_2023 | FLOOR_2024 | FLOOR_2025 | FLOOR_2026 | FLOOR_2027 | FLOOR_2028 | FLOOR_2029 | FLOOR_2030 | FLOOR_2031 | FLOOR_2032 | FLOOR_2033 | FLOOR_2034 | FLOOR_2035 | 85% | TOTAL
|  |  | DataCenter | 381.6014 | 404.6989 | 421.4604 | 419.6464 | 423.6656 | 432.7609 | 446.3153 | 450.9822 | 459.0513 | 470.196 | 484.1621 | 494.2107 | 506.6419 | 521.3539 | 538.2852 | 554.0194 | 571.8818 | 591.9021 | 614.1363 | 636.8744
|  |  | MWh Embedded Data Center Load | 3342828.5504 | 3545162.0054 | 3691993.0948 | 3676102.6518 | 3711310.907 | 3790985.6934 | 3909722.1322 | 3950604.3016 | 4021289.0441 | 4118917.1147 | 4241259.8428 | 4329285.6678 | 4438182.9982 | 4567060.3816 | 4715378.671 | 4853209.5294 | 5009684.7706 | 5185062.5855 | 5379834.3765 | 5579019.5935 |  | 5579019.5935
aMW Embedded Data Center Load
APPLY MEASURE APPLICABILITY, SATURATION TURNOVER RATE FOR MAX ANNUAL # UNITS |  |  | Total EDC Load
Applicability | Saturation | Turnover Rate | Data Centers-NR | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | TOTAL MAX | TOTAL
80% | 100% | 20% | MWh Embedded Data Center Load | 534852.5681 | 567225.9209 | 590718.8952 | 588176.4243 | 593809.7451 | 606557.711 | 625555.5412 | 632096.6882 | 643406.2471 | 659026.7383 | 678601.5749 | 692685.7068 | 710109.2797 | 730729.6611 | 754460.5874 | 776513.5247 | 801549.5633 | 829610.0137 | 860773.5002 | 892643.135 | 3793733.3236 | 13769103.026
APPLY MEASURE APPLICABILITY, SATURATION TURNOVER RATE FOR MAX ANNUAL # UNITS |  |  | Carryover from Untreated New
Applicability | Saturation |  | Data Centers-NR | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | TOTAL MAX
80% | 100% | 20% | MWh Embedded Data Center Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Achievability => | 2016: LO5Med
INCREMENTAL ACHIEVABILITY |  |  | Data Centers-NR | 4.3% | 9.58% | 16.04% | 23.54% | 32.1% | 42.1% | 53.07% | 64.28% | 74.84% | 83.92% | 90.95% | 95.77% | 98.65% | 100.1% | 100.8% | 101% | 101% | 101.1% | 101.1% | 101.1% | TOTAL MAX
Acheivable and 85% Max Per Year |  |  | MWh Embedded Data Center Load | 19548.8614 | 46187.8289 | 80541.3224 | 117690.9173 | 161996.959 | 217039.7218 | 282176.9046 | 345348.4422 | 409293.8716 | 470091.2669 | 524581.3697 | 563859.0114 | 595458.3336 | 621925.8522 | 646188.1515 | 666546.0851 | 688462.2231 | 712659.7542 | 739446.494 | 766826.1057 | 3793733.3236 | 8675869.4765
CUMULATIVE ADOPTION |  |  | Data Centers-NR | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | TOTAL MAX
Acheivable and 85% Max Per Year |  |  | MWh Embedded Data Center Load | 19548.8614 | 65736.6903 | 146278.0127 | 263968.93 | 425965.889 | 643005.6108 | 925182.5154 | 1270530.9576 | 1679824.8292 | 2149916.0961 | 2674497.4658 | 3238356.4772 | 3833814.8109 | 4455740.6631 | 5101928.8145 | 5768474.8996 | 6456937.1227 | 7169596.8769 | 7909043.3709 | 8675869.4765 | 3793733.3236
SUPPLY CURVE SAVINGS BY BUNDLE |  |  | NR | 1: aMW
kWh per Luminaire | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh |  | 1 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
Busbar Savings | lvlcost | segment | measure | FLOOR_2016 | FLOOR_2017 | FLOOR_2018 | FLOOR_2019 | FLOOR_2020 | FLOOR_2021 | FLOOR_2022 | FLOOR_2023 | FLOOR_2024 | FLOOR_2025 | FLOOR_2026 | FLOOR_2027 | FLOOR_2028 | FLOOR_2029 | FLOOR_2030 | FLOOR_2031 | FLOOR_2032 | FLOOR_2033 | FLOOR_2034 | FLOOR_2035 | TOTAL MAX
480.1237 | 10.2802 |  | Best Practice | 1.0714 | 2.5315 | 4.4144 | 6.4505 | 8.8788 | 11.8957 | 15.4657 | 18.9281 | 22.4328 | 25.7651 | 28.7516 | 30.9043 | 32.6363 | 34.0869 | 35.4167 | 36.5325 | 37.7337 | 39.0599 | 40.5281 | 42.0287 | 166.3435
221.7239 | 27.1572 |  | Commercial Technology | 0.4948 | 1.1691 | 2.0386 | 2.9789 | 4.1003 | 5.4935 | 7.1422 | 8.7411 | 10.3596 | 11.8985 | 13.2777 | 14.2718 | 15.0716 | 15.7415 | 16.3556 | 16.8709 | 17.4256 | 18.0381 | 18.7161 | 19.4091 | 76.8184
52.4058 | 20.9801 |  | Cutting Edge | 0.11695 | 0.27631 | 0.48183 | 0.70407 | 0.96913 | 1.2984 | 1.6881 | 2.066 | 2.4486 | 2.8123 | 3.1383 | 3.3732 | 3.5623 | 3.7206 | 3.8658 | 3.9875 | 4.1187 | 4.2634 | 4.4237 | 4.5875 | 18.1565
|  |  | Max Annual Available | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
RECOMBINE MEASURE BUNDLES INTO SUPPLY CURVE CUMULATIVE
|  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
|  | lvlcost | lvlcost | FLOOR_2016 | FLOOR_2017 | FLOOR_2018 | FLOOR_2019 | FLOOR_2020 | FLOOR_2021 | FLOOR_2022 | FLOOR_2023 | FLOOR_2024 | FLOOR_2025 | FLOOR_2026 | FLOOR_2027 | FLOOR_2028 | FLOOR_2029 | FLOOR_2030 | FLOOR_2031 | FLOOR_2032 | FLOOR_2033 | FLOOR_2034 | FLOOR_2035 | TOTAL MAX
| Block 1: <= 0 mills/kWh | >=-9999 | <=0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 2: <= 10 mills/kWh | >0 | <=10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 3: 10-20 mills/kWh | >10 | <=20 | 1.0714 | 2.5315 | 4.4144 | 6.4505 | 8.8788 | 11.8957 | 15.4657 | 18.9281 | 22.4328 | 25.7651 | 28.7516 | 30.9043 | 32.6363 | 34.0869 | 35.4167 | 36.5325 | 37.7337 | 39.0599 | 40.5281 | 42.0287 | 166.3435
| Block 4: 20-30 mills/kWh | >20 | <=30 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 5: 30-40 mills/kWh | >30 | <=40 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 6: 40-50 mills/kWh | >40 | <=50 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 7: 50-60 mills/kWh | >50 | <=60 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 8: 60-70 mills/kWh | >60 | <=70 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 9: 70-80 mills/kWh | >70 | <=80 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 10: 80-90 mills/kWh | >80 | <=90 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 11: 90-100 mills/kWh | >90 | <=100 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 12: 100-110 mills/kWh | >100 | <=110 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 13: 110-120 mills/kWh | >110 | <=120 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 14: 120-130 mills/kWh | >120 | <=130 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 15: 130-140 mills/kWh | >130 | <=140 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 16: 140-150 mills/kWh | >140 | <=150 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 17: 150-160 mills/kWh | >150 | <=160 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 18: 160-170 mills/kWh | >160 | <=170 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 19: 170-180 mills/kWh | >170 | <=180 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 20: 180-190 mills/kWh | >180 | <=190 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 21: 190-200 mills/kWh | >190 | <=200 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 22: 200-210 mills/kWh | >200 | <=210 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 23: 210-220 mills/kWh | >210 | <=220 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 24: 220-230 mills/kWh | >220 | <=230 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 25: 230-240 mills/kWh | >230 | <=240 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 26: 240-250 mills/kWh | >240 | <=250 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 27: 250-260 mills/kWh | >250 | <=260 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 28: 260-270 mills/kWh | >260 | <=270 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 29: 270-280 mills/kWh | >270 | <=280 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 30: 280-290 mills/kWh | >280 | <=290 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 31: 290-300 mills/kWh | >290 | <=300 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
| Block 32: >300 mills/kWh | >300 | <=999 | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | 261.3184
RECOMBINE MEASURE BUNDLES INTO SUPPLY CURVE INREMENETAL
|  | SC-NR | Data Centers-NR | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
|  | 0 |  | FLOOR_2016 | FLOOR_2017 | FLOOR_2018 | FLOOR_2019 | FLOOR_2020 | FLOOR_2021 | FLOOR_2022 | FLOOR_2023 | FLOOR_2024 | FLOOR_2025 | FLOOR_2026 | FLOOR_2027 | FLOOR_2028 | FLOOR_2029 | FLOOR_2030 | FLOOR_2031 | FLOOR_2032 | FLOOR_2033 | FLOOR_2034 | FLOOR_2035 | TOTAL MAX
|  | Block 1: <= 0 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 2: <= 10 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 3: 10-20 mills/kWh |  | 1.0714 | 2.5315 | 4.4144 | 6.4505 | 8.8788 | 11.8957 | 15.4657 | 18.9281 | 22.4328 | 25.7651 | 28.7516 | 30.9043 | 32.6363 | 34.0869 | 35.4167 | 36.5325 | 37.7337 | 39.0599 | 40.5281 | 42.0287 | 166.3435
|  | Block 4: 20-30 mills/kWh |  | 0.61175 | 1.4454 | 2.5204 | 3.6829 | 5.0694 | 6.7919 | 8.8303 | 10.8071 | 12.8082 | 14.7107 | 16.4159 | 17.645 | 18.6339 | 19.4621 | 20.2214 | 20.8585 | 21.5443 | 22.3015 | 23.1398 | 23.9966 | 94.9749
|  | Block 5: 30-40 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 6: 40-50 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 7: 50-60 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 8: 60-70 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 9: 70-80 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 10: 80-90 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 11: 90-100 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 12: 100-110 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 13: 110-120 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 14: 120-130 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 15: 130-140 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 16: 140-150 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 17: 150-160 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 18: 160-170 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 19: 170-180 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 20: 180-190 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 21: 190-200 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 22: 200-210 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 23: 210-220 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 24: 220-230 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 25: 230-240 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 26: 240-250 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 27: 250-260 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 28: 260-270 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 29: 270-280 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 30: 280-290 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 31: 290-300 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 32: >300 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total per Year |  | 1.6832 | 3.9769 | 6.9348 | 10.1334 | 13.9483 | 18.6876 | 24.296 | 29.7352 | 35.241 | 40.4758 | 45.1675 | 48.5494 | 51.2701 | 53.549 | 55.6381 | 57.3909 | 59.278 | 61.3614 | 63.6678 | 66.0252 | TOTAL MAX
|  | Cumulative at Earliest Deployment |  | 1.6832 | 5.6601 | 12.5948 | 22.7282 | 36.6765 | 55.3641 | 79.66 | 109.3952 | 144.6362 | 185.112 | 230.2795 | 261.3184 | 261.3184 | 261.3184 | 261.3184 | 261.3184 | 261.3184 | 261.3184 | 261.3184 | 261.3184 | 261.3184

## M_Input_Out
Shaped Savings Results; By Category and sorted by TRC BC ratio
[14 empty] | Savings Allocation by Category and Month for Segments 1 | [11 empty] | Savings Allocation by Category and Month for Segments 2
Category | Measure | Busbar Savings | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Wholesale KW | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Best Practice |  | 480.1237 | 30.9615 | 6.1923 | 37.1538 | 113.608 | 288.2415 | 677.8822 | -3.0491 | 10.2802 | 2.5372 | 4.5612 | 0.060302 | 23.1878 | 21.7873 | 24.7119 | 22.5162 | 23.0941 | 23.0205 | 22.0421 | 25.1444 | 21.6572 | 24.6048 | 21.2634 | 21.6498 | 18.6679 | 16.7918 | 16.7013 | 16.7824 | 16.9992 | 15.7588 | 17.7179 | 16.8851 | 17.6592 | 16.5661 | 17.423 | 17.4915
Cutting Edge |  | 52.4058 | 6.2712 | 1.2542 | 7.5254 | 20.021 | 31.4617 | 1257.9305 | 0.44363 | 20.9801 | 1.5714 | 0.49786 | 0.006582 | 2.531 | 2.3781 | 2.6973 | 2.4577 | 2.5207 | 2.5127 | 2.4059 | 2.7445 | 2.3639 | 2.6856 | 2.3209 | 2.3631 | 2.0376 | 1.8328 | 1.823 | 1.8318 | 1.8555 | 1.7201 | 1.9339 | 1.843 | 1.9275 | 1.8082 | 1.9017 | 1.9092
Commercial Technology |  | 221.7239 | 43.3659 | 8.6732 | 52.0391 | 103.3204 | 133.1116 | 2055.9902 | 5.2491 | 27.1572 | 1.2883 | 2.1064 | 0.027848 | 10.7083 | 10.0615 | 11.4121 | 10.3981 | 10.665 | 10.631 | 10.1791 | 11.6118 | 10.0014 | 11.3626 | 9.8196 | 9.998 | 8.6209 | 7.7546 | 7.7128 | 7.7502 | 7.8503 | 7.2775 | 8.1822 | 7.7976 | 8.1551 | 7.6503 | 8.0461 | 8.0777

## M_Input
Data Set Name | [13 empty] | #REF!
Measure Index Name | Data Centers
Costs must be denominated in the same year as 'Input Cost Reference Year' = |  | 2012
| Savings Units are: | kWh/MWh DC Load |  | Units Scalar | 1000
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105
Input Data | [7 empty] | Periodic Replacement Costs and Savings and Replacement Period | [5 empty] | Gas Inputs |  | Retro or LO | Early Retrofit Parameters
Category Name | Measure Name | Savings (kwh/yr) | Life (yrs) | Capital Cost | Annual O&M | Shape Pointer | Non-E Val ($/yr) | Cost 1 ($) | Period 1 | Cost 2 ($) | Period 2 | Cost 3 ($) | Period 3 | Savings (therms/yr) | Shape Pointer | R or L | Savings 2 (kWh) | Remaining Life (yrs) | Salvage Value ($)
Best Practice | Decommissioning of unused servers | 67.1075 | 5 | 2.0776 |  | Total Industrial-Total Industrial | [9 empty] | R
Best Practice | Server virtualization/consolidation | 301.071 | 5 | 24.8564 |  | Total Industrial-Total Industrial | [9 empty] | R
Best Practice | Server power management | 23.377 | 5 | 0 |  | Total Industrial-Total Industrial | [9 empty] | R
Best Practice | Energy efficient data storage management | 55.7506 | 5 | 4.0274 |  | Total Industrial-Total Industrial | [9 empty] | R
Commercial Technology | Energy efficient servers | 77.5809 | 5 | 10.0079 |  | Total Industrial-Total Industrial | [9 empty] | R
Commercial Technology | Massive array of idle disks (MAID) | 23.2869 | 5 | 3.004 |  | Total Industrial-Total Industrial | [9 empty] | R
Commercial Technology | Efficient network topology | 26.1807 | 5 | 0 |  | Total Industrial-Total Industrial | [9 empty] | R
Commercial Technology | Energy efficient transformers | 4.8055 | 5 | 1.4878 |  | Total Industrial-Total Industrial | [9 empty] | R
Commercial Technology | Energy efficient power supplies (UPS) | 44.2971 | 15 | 17.6001 |  | Total Industrial-Total Industrial | [9 empty] | R
Commercial Technology | Energy efficient lighting | 10.5469 | 10 | 5.4422 |  | Total Industrial-Total Industrial | [9 empty] | R
Commercial Technology | Hot or cold aisle configuration | 1.3247 | 10 | 0.21873 |  | Total Industrial-Total Industrial | [9 empty] | R
Commercial Technology | Hot or cold aisle configuration plus containment (e.g., strip curtains or rigid enclosures) | 2.6494 | 10 | 0.54684 |  | Total Industrial-Total Industrial | [9 empty] | R
Commercial Technology | Variable speed drives on pumps/fans | 2.6494 | 10 | 0.39646 |  | Total Industrial-Total Industrial | [9 empty] | R
Commercial Technology | Premium efficiency motors | 2.6494 | 10 | 0.71089 |  | Total Industrial-Total Industrial | [9 empty] | R
Commercial Technology | Air-side economizer | 2.6494 | 10 | 1.0527 |  | Total Industrial-Total Industrial | [9 empty] | R
Commercial Technology | In-row cooling | 2.6494 | 10 | 0.68355 |  | Total Industrial-Total Industrial | [9 empty] | R
Commercial Technology | Water-side economizer | 2.6494 | 10 | 1.2577 |  | Total Industrial-Total Industrial | [9 empty] | R
Commercial Technology | Install misters, foggers, or ultrasonic humidifiers | 2.6494 | 10 | 0.95696 |  | Total Industrial-Total Industrial | [9 empty] | R
Cutting Edge | Solid state storage | 12.86 | 5 | 3.3179 |  | Total Industrial-Total Industrial | [9 empty] | R
Cutting Edge | Efficient network topology | 21.9628 | 5 | 0 |  | Total Industrial-Total Industrial | [9 empty] | R
Cutting Edge | Direct current (as opposed to AC) to the racks | 2.0042 | 5 | 1.0962 |  | Total Industrial-Total Industrial | [9 empty] | R
Cutting Edge | Direct liquid cooling of chips | 11.9968 | 10 | 1.8571 |  | Total Industrial-Total Industrial | [9 empty] | R
ProCost Results
Version: | ProCost 3.0 - Beta04
Run Time: | Wednesday, 18 March , 2015 at 12:02 AM
Regurgitation of ProData input parameters which were used for this run
| Run Parameters |  | Run Parameters |  |  | Marginal Cost & Conservation Load Shape Parameters | [9 empty] | Sponsor Parameters | [5 empty] | Program Parameters |  |  | Utility System Parameters
| Run Type | Electric | Run Type | Electric |  | Marginal Costs and Savings Shape File | Q:\SeventhPlan\Conservation Analysis\Global EE Inputs\MC Files\MC_AND_LOADSHAPE_v3.0_24segment-7P-D9 - NewSegValues.xlsx |  |  | 6P MidC Final (with carbon) | [6 empty] | Customer | Wholesale Elec | Retail Elec | Nat Gas |  | Program Life (yrs) | 20 |  |  | Electric | Gas
| Negative B/C Ratios | Off | Negative B/C Ratios | Off |  | Marginal Elec Avoided Cost Input Worksheet | 7P Mid |  |  | Conservation Load Shapes | [5 empty] | Real After-Tax Cost of Capital | 0.068013 | 0.043878 | 0.053289 | 0.054479 |  | Program Start Date | 2016 |  | Bulk System T&D Loss Factor | 0.0040389 | 0.01
| Admin Cost @ Category Level | On | Admin Cost @ Category Level | On |  | Elec Savings Shape Input Worksheet | GLSShapes |  |  | 6P_Gas_Final | [5 empty] | Financial Life (years) | 12 | 12 | 1 | 1 |  | Present Value Time Zero | 2016 |  | Bulk System T&D Credit ($/kw-yr)($/dailytherm-yr) | 26 | 0
| Repeat Periodic Replacement | On | Repeat Periodic Replacement | On |  | Marginal Gas Avoided Cost Input Worksheet | 7P Gas |  |  | Conservation Load Shapes | [6 empty] | Customer | Wholesale Elec | Retail Elec | Nat Gas |  | Input Cost Reference Year | 2012 |  | Bulk System T&D I2R Loss Component (%) | 0.9 | N/A
[6 empty] | Gas Savings Shape Input Worksheet | GLSShapes | [8 empty] | Sponsor Share of Initial Capital Cost | 0.35 | 0.195 | 0.455 | 0 |  | Real Discount Rate | 0.04 |  | Local System Dist Loss Factor | 0.047399 | 0
| Run Type: | Electric |  |  |  | Marginal Elec CO2 per kWh Input Worksheet | CO2 lbs per kWh .95 |  |  | CO2 lbs per therm | [5 empty] | Sponsor Share of Annual O&M | 1 | 0 | 0 | 0 |  | Capital Real Escalation Rate | 0 |  | Local System Dist Credit ($/kw-yr)($/dailytherm-yr) | 31 | 0
| Negative B/C Ratios: | False: (Converts Negative B/C Ratios) |  |  |  | Marginal Gas CO2 per therm Input Worksheet | CO2 lbs per therm |  |  | Zero Dollars per ton CO2 | [5 empty] | Sponsor Share of Periodic Replacement Cost | 1 | 0 | 0 | 0 |  | Admin Cost (as % of Initial Capital Cost) | 0.2 |  | Local System Dist I2R Loss Component (%) | 0.7 | N/A
| Admin Cost / Category Level: | True: Admin Costs added at Category Results |  |  |  | Marginal Avoided Cost CO2 Input Worksheet | Zero Dollars per ton CO2 |  |  | LineLossShapes | [5 empty] | Sponsor Share of Admin Cost |  | 0.3 | 0.7 | 0 |  | Regional Act Conservation Credit (%) | 0 |  | Risk-Mitigation Credit (mills/kWh)(mills/therm) - Retro. | 0 | 0
| Periodic O&M Treatment: | True: (Periodic O&M Repeats over measure life) |  |  |  | Line Loss Shape Input Worksheet | LineLossShapes | [8 empty] | Last Year of Non-Customer O&M & Period Replacement |  | 20 |  |  |  | Report Annual Carbon Saved for Year | 2018 |  | Risk-Mitigation Credit (mills/kWh)(mills/therm) - Lost Op. | 0 | 0
Measure Results; Sorted in same order as input
Total Results |  | Measure Input Data | [8 empty] | Savings | [5 empty] | PV Capital |  |  |  | PV Admin |  |  |  | PV O&M |  |  |  | PV Periodic Repl. |  |  |  | Total PV Capital, O&M and Periodic Repl Costs |  |  |  |  | PV Wholesale Electric Utility Costs & Benefits | [6 empty] | PV Retail Electric Utility Costs & Benefits | [6 empty] | PV Electric Utility System Costs & Benefits | [5 empty] | Electric Utility System Economics |  | Sponsor Levelized Cost (mills/kwh) |  |  |  |  | PV Regional Costs & Benefits | [15 empty] | TRC Economics |  | Physical CO2 | [6 empty] | Gas Inputs |  |  |  | PV Gas Utility System Costs & Benefits |  |  |  |  | Gas Utility System Economics
Category | Measure | Measure Life | Site Savings (kWh) | Site Savings (therms) | Capital Cost ($/unit) | Annual O&M Cost ($/unit) | PV Per. Repl. Cost ($/unit) | Load Shape (electric) | Diversified Load Factor (electric) | Wholesale Power Coincidence Factor (electric) | Wholesale Electric Energy (kWh) | Wholesale Electric Demand (kw) | Retail Electric Demand (kW) | Wholesale Gas Energy (therms/yr) | Wholesale Gas Demand (therms/day) | Retail Gas Demand (therms/day) | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Total | Wholesale Utility System Energy | Wholesale Utility System T&D Def. Cap. | Wholesale Utility System Act C-E Credit | Wholesale Utility System Risk Mitigation Benefit | Wholesale Utility System Total System Benefit | Wholesale Utility System Total Non-Consumer Cost | Wholesale Utility System B/C Ratio | Retail Utility System Energy | Retail Utility System T&D Def. Cap. | Retail Utility System Act C-E Credit | Retail Utility System Risk Mitigation Benefit | Retail Utility System Total System Benefit | Retail Utility System Total Non-Consumer Cost | Retail Utility System System B/C Ratio | Utility System Energy | Utility System T&D Def. Cap. | Utility System Act C-E Credit | Utility System Total Risk Mitigation Benefit | Utility System Total System Benefit | Utility System Total Non-Consumer Cost | Utility System Net Levelized Cost (Net of Elec T&D Capacity Benefits, Act Credit & Risk-Mitigation Benefit) in mills/kwh | Utility System System B/C Ratio | Wholesale Electric Levelized Cost | Retail Electric Levelized Cost | Natural Gas Levelized Cost | Customer Levelized Cost | Total Levelized Cost | PV Regional Electric Energy | PV Regional Gas Energy | PV Regional Electric T&D Def. Cap. | PV Regional Gas T&D Def. Cap. | PV Regional Electric System CO2 | PV Regional Gas System CO2 | PV Regional Electric System Risk-Mitigation Benefit | PV Regional Gas System Risk-Mitigation Benefit | PV Regional Non-E Value | PV Regional Act Credit | PV Regional Capital Cost | PV Regional Admin Cost | PV Regional Annual O&M Cost | PV Regional Periodic Replacement Cost | PV Total Regional Benefit | PV Total Regional Cost | TRC B/C Ratio | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | Electric System CO2 Avoided (Lifetime Tons) | Gas System CO2 Avoided (Lifetime Tons) | Total System CO2 Avoided (Lifetime Tons) | Electric System CO2 Avoided (Annual Tons in 2018) | Gas System CO2 Avoided (Annual Tons in 2018) | Total System CO2 Avoided (Annual Tons in 2018) |  | Gas Site Savings (therms) | Load Shape (gas) | Diversitfied Load Factor (gas) | Wholesale Coincidence Factor (gas) | Total Gas Utility System Energy | Gas Utility System T&D Def. Cap. | Gas Utility System Risk Mitigation Benefit | Gas Utility System Total System Benefit | Gas Utility System Total Non-Consumer Cost | Gas Utility System Net Levelized Cost (Net of Gas T&D Capacity Benefits & Risk-Mitigation Benefits) in cents/therm | Gas Utility System System B/C Ratio
Best Practice | Decommissioning of unused servers | 5 | 67.1075 | 0 | 2.0776 | 0 | 0 | Total Industrial-Total Industrial |  |  | 72.031 | 0.0090468 | 0.0089815 | 0 | 0 | 0 | 0.41431 | 0.95741 | 0 | 5.8363 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41431 | 0.95741 | 0 | 5.8363 | 7.2081 | 36.2631 | 3.1967 | 0 | 0 | 39.4598 | 0.41431 | 95.2419 | 36.2631 | 3.7839 | 0 | 0 | 40.047 | 0.95741 | 41.8285 | 36.2631 | 6.9806 | 0 | 0 | 43.2437 | 1.3717 | -5.7296 | 31.5251 | 0.42323 | 0.97802 | 0 | 5.962 | 7.3632 | 36.2631 | 0 | 6.9806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2081 |  | 0 | 0 | 43.2437 | 7.2081 | 5.9994 | 0.23235 | 0.6843 | 0 | 0.6843 | 0.034215 | 0 | 0.034215 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Best Practice | Server virtualization/consolidation | 5 | 301.071 | 0 | 24.8564 | 0 | 0 | Total Industrial-Total Industrial |  |  | 323.1596 | 0.040588 | 0.040295 | 0 | 0 | 0 | 4.9567 | 11.4542 | 0 | 69.8243 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9567 | 11.4542 | 0 | 69.8243 | 86.2352 | 162.6907 | 14.3416 | 0 | 0 | 177.0322 | 4.9567 | 35.7157 | 162.6907 | 16.9762 | 0 | 0 | 179.6668 | 11.4542 | 15.6857 | 162.6907 | 31.3177 | 0 | 0 | 194.0084 | 16.4109 | -3.3942 | 11.8219 | 1.1286 | 2.6081 | 0 | 15.8986 | 19.6353 | 162.6907 | 0 | 31.3177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2352 |  | 0 | 0 | 194.0084 | 86.2352 | 2.2498 | 12.5044 | 3.07 | 0 | 3.07 | 0.1535 | 0 | 0.1535 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Best Practice | Server power management | 5 | 23.377 | 0 | 0 | 0 | 0 | Total Industrial-Total Industrial |  |  | 25.0921 | 0.0031515 | 0.0031287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.6323 | 1.1136 | 0 | 0 | 13.7459 | 0 | 9999 | 12.6323 | 1.3181 | 0 | 0 | 13.9505 | 0 | 9999 | 12.6323 | 2.4317 | 0 | 0 | 15.064 | 0 | -7.1309 | 9999 | 0 | 0 | 0 | 0 | 0 | 12.6323 | 0 | 2.4317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 15.064 | 0 | 9999 | -7.1309 | 0.23838 | 0 | 0.23838 | 0.011919 | 0 | 0.011919 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Best Practice | Energy efficient data storage management | 5 | 55.7506 | 0 | 4.0274 | 0 | 0 | Total Industrial-Total Industrial |  |  | 59.8409 | 0.0075158 | 0.0074615 | 0 | 0 | 0 | 0.80312 | 1.8559 | 0 | 11.3135 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80312 | 1.8559 | 0 | 11.3135 | 13.9725 | 30.1261 | 2.6557 | 0 | 0 | 32.7818 | 0.80312 | 40.818 | 30.1261 | 3.1435 | 0 | 0 | 33.2697 | 1.8559 | 17.9265 | 30.1261 | 5.7992 | 0 | 0 | 35.9254 | 2.659 | -3.8613 | 13.5108 | 0.98754 | 2.2821 | 0 | 13.9113 | 17.1809 | 30.1261 | 0 | 5.7992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.9725 |  | 0 | 0 | 35.9254 | 13.9725 | 2.5712 | 10.05 | 0.56849 | 0 | 0.56849 | 0.028424 | 0 | 0.028424 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial Technology | Energy efficient servers | 5 | 77.5809 | 0 | 10.0079 | 0 | 0 | Total Industrial-Total Industrial |  |  | 83.2728 | 0.010459 | 0.010383 | 0 | 0 | 0 | 1.9957 | 4.6118 | 0 | 28.1133 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9957 | 4.6118 | 0 | 28.1133 | 34.7208 | 41.9226 | 3.6956 | 0 | 0 | 45.6182 | 1.9957 | 22.8581 | 41.9226 | 4.3745 | 0 | 0 | 46.2971 | 4.6118 | 10.0388 | 41.9226 | 8.07 | 0 | 0 | 49.9927 | 6.6075 | -1.2923 | 7.566 | 1.7635 | 4.0751 | 0 | 24.8416 | 30.6801 | 41.9226 | 0 | 8.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.7208 |  | 0 | 0 | 49.9927 | 34.7208 | 1.4398 | 23.5493 | 0.7911 | 0 | 0.7911 | 0.039555 | 0 | 0.039555 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial Technology | Massive array of idle disks (MAID) | 5 | 23.2869 | 0 | 3.004 | 0 | 0 | Total Industrial-Total Industrial |  |  | 24.9954 | 0.0031393 | 0.0031167 | 0 | 0 | 0 | 0.59904 | 1.3843 | 0 | 8.4386 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59904 | 1.3843 | 0 | 8.4386 | 10.4219 | 12.5836 | 1.1093 | 0 | 0 | 13.6929 | 0.59904 | 22.8581 | 12.5836 | 1.3131 | 0 | 0 | 13.8967 | 1.3843 | 10.0388 | 12.5836 | 2.4223 | 0 | 0 | 15.006 | 1.9833 | -1.2923 | 7.566 | 1.7635 | 4.0751 | 0 | 24.8416 | 30.6801 | 12.5836 | 0 | 2.4223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4219 |  | 0 | 0 | 15.006 | 10.4219 | 1.4398 | 23.5493 | 0.23746 | 0 | 0.23746 | 0.011873 | 0 | 0.011873 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial Technology | Efficient network topology | 5 | 26.1807 | 0 | 0 | 0 | 0 | Total Industrial-Total Industrial |  |  | 28.1015 | 0.0035294 | 0.003504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.1474 | 1.2471 | 0 | 0 | 15.3945 | 0 | 9999 | 14.1474 | 1.4762 | 0 | 0 | 15.6236 | 0 | 9999 | 14.1474 | 2.7233 | 0 | 0 | 16.8707 | 0 | -7.1309 | 9999 | 0 | 0 | 0 | 0 | 0 | 14.1474 | 0 | 2.7233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 16.8707 | 0 | 9999 | -7.1309 | 0.26697 | 0 | 0.26697 | 0.013348 | 0 | 0.013348 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial Technology | Energy efficient transformers | 5 | 4.8055 | 0 | 1.4878 | 0 | 0 | Total Industrial-Total Industrial |  |  | 5.1581 | 0.00064783 | 0.00064316 | 0 | 0 | 0 | 0.29668 | 0.68559 | 0 | 4.1793 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29668 | 0.68559 | 0 | 4.1793 | 5.1616 | 2.5968 | 0.22891 | 0 | 0 | 2.8257 | 0.29668 | 9.5242 | 2.5968 | 0.27096 | 0 | 0 | 2.8677 | 0.68559 | 4.1829 | 2.5968 | 0.49987 | 0 | 0 | 3.0966 | 0.98228 | 6.8816 | 3.1525 | 4.2323 | 9.7802 | 0 | 59.6198 | 73.6323 | 2.5968 | 0 | 0.49987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1616 |  | 0 | 0 | 3.0966 | 5.1616 | 0.59994 | 66.5015 | 0.049002 | 0 | 0.049002 | 0.0024501 | 0 | 0.0024501 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial Technology | Energy efficient power supplies (UPS) | 15 | 44.2971 | 0 | 17.6001 | 0 | 0 | Total Industrial-Total Industrial |  |  | 47.547 | 0.0059717 | 0.0059286 | 0 | 0 | 0 | 3.5097 | 8.1104 | 0 | 11.7766 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5097 | 8.1104 | 0 | 11.7766 | 23.3967 | 23.937 | 2.1101 | 0 | 0 | 26.0471 | 3.5097 | 7.4214 | 23.937 | 2.4977 | 0 | 0 | 26.4347 | 8.1104 | 3.2594 | 23.937 | 4.6078 | 0 | 0 | 28.5448 | 11.6201 | 10.8519 | 2.4565 | 5.4315 | 12.5513 | 0 | 18.2249 | 36.2077 | 23.937 | 0 | 4.6078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.3967 |  | 0 | 0 | 28.5448 | 23.3967 | 1.22 | 29.0768 | 0.4517 | 0 | 0.4517 | 0.022585 | 0 | 0.022585 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial Technology | Energy efficient lighting | 10 | 10.5469 | 0 | 5.4422 | 0 | 0 | Total Industrial-Total Industrial |  |  | 11.3207 | 0.0014218 | 0.0014116 | 0 | 0 | 0 | 1.0853 | 2.5078 | 0 | 6.5252 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0853 | 2.5078 | 0 | 6.5252 | 10.1183 | 5.6993 | 0.5024 | 0 | 0 | 6.2017 | 1.0853 | 5.7145 | 5.6993 | 0.5947 | 0 | 0 | 6.294 | 2.5078 | 2.5097 | 5.6993 | 1.0971 | 0 | 0 | 6.7964 | 3.5931 | 16.2233 | 1.8915 | 7.0538 | 16.3004 | 0 | 42.4124 | 65.7666 | 5.6993 | 0 | 1.0971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1183 |  | 0 | 0 | 6.7964 | 10.1183 | 0.67169 | 58.6357 | 0.10755 | 0 | 0.10755 | 0.0053773 | 0 | 0.0053773 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial Technology | Hot or cold aisle configuration | 10 | 1.3247 | 0 | 0.21873 | 0 | 0 | Total Industrial-Total Industrial |  |  | 1.4219 | 0.00017858 | 0.0001773 | 0 | 0 | 0 | 0.043619 | 0.1008 | 0 | 0.26226 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043619 | 0.1008 | 0 | 0.26226 | 0.40668 | 0.71583 | 0.063102 | 0 | 0 | 0.77894 | 0.043619 | 17.8579 | 0.71583 | 0.074694 | 0 | 0 | 0.79053 | 0.1008 | 7.8428 | 0.71583 | 0.1378 | 0 | 0 | 0.85363 | 0.14441 | 0.34246 | 5.911 | 2.2572 | 5.2161 | 0 | 13.572 | 21.0453 | 0.71583 | 0 | 0.1378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40668 |  | 0 | 0 | 0.85363 | 0.40668 | 2.099 | 13.9144 | 0.013508 | 0 | 0.013508 | 0.0006754 | 0 | 0.0006754 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial Technology | Hot or cold aisle configuration plus containment (e.g., strip curtains or rigid enclosures) | 10 | 2.6494 | 0 | 0.54684 | 0 | 0 | Total Industrial-Total Industrial |  |  | 2.8438 | 0.00035717 | 0.00035459 | 0 | 0 | 0 | 0.10905 | 0.25199 | 0 | 0.65566 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10905 | 0.25199 | 0 | 0.65566 | 1.0167 | 1.4317 | 0.1262 | 0 | 0 | 1.5579 | 0.10905 | 14.2863 | 1.4317 | 0.14939 | 0 | 0 | 1.5811 | 0.25199 | 6.2743 | 1.4317 | 0.27559 | 0 | 0 | 1.7073 | 0.36104 | 2.2108 | 4.7288 | 2.8215 | 6.5201 | 0 | 16.9649 | 26.3066 | 1.4317 | 0 | 0.27559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0167 |  | 0 | 0 | 1.7073 | 1.0167 | 1.6792 | 19.1757 | 0.027016 | 0 | 0.027016 | 0.0013508 | 0 | 0.0013508 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial Technology | Variable speed drives on pumps/fans | 10 | 2.6494 | 0 | 0.39646 | 0 | 0 | Total Industrial-Total Industrial |  |  | 2.8438 | 0.00035717 | 0.00035459 | 0 | 0 | 0 | 0.079059 | 0.18269 | 0 | 0.47535 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079059 | 0.18269 | 0 | 0.47535 | 0.73711 | 1.4317 | 0.1262 | 0 | 0 | 1.5579 | 0.079059 | 19.7052 | 1.4317 | 0.14939 | 0 | 0 | 1.5811 | 0.18269 | 8.6542 | 1.4317 | 0.27559 | 0 | 0 | 1.7073 | 0.26175 | -0.35816 | 6.5224 | 2.0456 | 4.7271 | 0 | 12.2996 | 19.0723 | 1.4317 | 0 | 0.27559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73711 |  | 0 | 0 | 1.7073 | 0.73711 | 2.3162 | 11.9414 | 0.027016 | 0 | 0.027016 | 0.0013508 | 0 | 0.0013508 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial Technology | Premium efficiency motors | 10 | 2.6494 | 0 | 0.71089 | 0 | 0 | Total Industrial-Total Industrial |  |  | 2.8438 | 0.00035717 | 0.00035459 | 0 | 0 | 0 | 0.14176 | 0.32759 | 0 | 0.85236 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14176 | 0.32759 | 0 | 0.85236 | 1.3217 | 1.4317 | 0.1262 | 0 | 0 | 1.5579 | 0.14176 | 10.9895 | 1.4317 | 0.14939 | 0 | 0 | 1.5811 | 0.32759 | 4.8264 | 1.4317 | 0.27559 | 0 | 0 | 1.7073 | 0.46935 | 5.0133 | 3.6375 | 3.668 | 8.4762 | 0 | 22.0544 | 34.1986 | 1.4317 | 0 | 0.27559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3217 |  | 0 | 0 | 1.7073 | 1.3217 | 1.2917 | 27.0677 | 0.027016 | 0 | 0.027016 | 0.0013508 | 0 | 0.0013508 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial Technology | Air-side economizer | 10 | 2.6494 | 0 | 1.0527 | 0 | 0 | Total Industrial-Total Industrial |  |  | 2.8438 | 0.00035717 | 0.00035459 | 0 | 0 | 0 | 0.20991 | 0.48508 | 0 | 1.2621 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20991 | 0.48508 | 0 | 1.2621 | 1.9571 | 1.4317 | 0.1262 | 0 | 0 | 1.5579 | 0.20991 | 7.4214 | 1.4317 | 0.14939 | 0 | 0 | 1.5811 | 0.48508 | 3.2594 | 1.4317 | 0.27559 | 0 | 0 | 1.7073 | 0.695 | 10.8519 | 2.4565 | 5.4315 | 12.5513 | 0 | 32.6575 | 50.6403 | 1.4317 | 0 | 0.27559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9571 |  | 0 | 0 | 1.7073 | 1.9571 | 0.87232 | 43.5094 | 0.027016 | 0 | 0.027016 | 0.0013508 | 0 | 0.0013508 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial Technology | In-row cooling | 10 | 2.6494 | 0 | 0.68355 | 0 | 0 | Total Industrial-Total Industrial |  |  | 2.8438 | 0.00035717 | 0.00035459 | 0 | 0 | 0 | 0.13631 | 0.31499 | 0 | 0.81958 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13631 | 0.31499 | 0 | 0.81958 | 1.2709 | 1.4317 | 0.1262 | 0 | 0 | 1.5579 | 0.13631 | 11.429 | 1.4317 | 0.14939 | 0 | 0 | 1.5811 | 0.31499 | 5.0194 | 1.4317 | 0.27559 | 0 | 0 | 1.7073 | 0.4513 | 4.5462 | 3.783 | 3.5269 | 8.1502 | 0 | 21.2062 | 32.8833 | 1.4317 | 0 | 0.27559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2709 |  | 0 | 0 | 1.7073 | 1.2709 | 1.3434 | 25.7524 | 0.027016 | 0 | 0.027016 | 0.0013508 | 0 | 0.0013508 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial Technology | Water-side economizer | 10 | 2.6494 | 0 | 1.2577 | 0 | 0 | Total Industrial-Total Industrial |  |  | 2.8438 | 0.00035717 | 0.00035459 | 0 | 0 | 0 | 0.25081 | 0.57958 | 0 | 1.508 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25081 | 0.57958 | 0 | 1.508 | 2.3384 | 1.4317 | 0.1262 | 0 | 0 | 1.5579 | 0.25081 | 6.2114 | 1.4317 | 0.14939 | 0 | 0 | 1.5811 | 0.57958 | 2.7279 | 1.4317 | 0.27559 | 0 | 0 | 1.7073 | 0.83038 | 14.355 | 2.056 | 6.4895 | 14.9963 | 0 | 39.0194 | 60.5053 | 1.4317 | 0 | 0.27559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3384 |  | 0 | 0 | 1.7073 | 2.3384 | 0.7301 | 53.3744 | 0.027016 | 0 | 0.027016 | 0.0013508 | 0 | 0.0013508 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial Technology | Install misters, foggers, or ultrasonic humidifiers | 10 | 2.6494 | 0 | 0.95696 | 0 | 0 | Total Industrial-Total Industrial |  |  | 2.8438 | 0.00035717 | 0.00035459 | 0 | 0 | 0 | 0.19083 | 0.44098 | 0 | 1.1474 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19083 | 0.44098 | 0 | 1.1474 | 1.7792 | 1.4317 | 0.1262 | 0 | 0 | 1.5579 | 0.19083 | 8.1636 | 1.4317 | 0.14939 | 0 | 0 | 1.5811 | 0.44098 | 3.5853 | 1.4317 | 0.27559 | 0 | 0 | 1.7073 | 0.63181 | 9.2171 | 2.7022 | 4.9377 | 11.4103 | 0 | 29.6887 | 46.0366 | 1.4317 | 0 | 0.27559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7792 |  | 0 | 0 | 1.7073 | 1.7792 | 0.95956 | 38.9057 | 0.027016 | 0 | 0.027016 | 0.0013508 | 0 | 0.0013508 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Cutting Edge | Solid state storage | 5 | 12.86 | 0 | 3.3179 | 0 | 0 | Total Industrial-Total Industrial |  |  | 13.8035 | 0.0017337 | 0.0017211 | 0 | 0 | 0 | 0.66163 | 1.5289 | 0 | 9.3202 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66163 | 1.5289 | 0 | 9.3202 | 11.5108 | 6.9492 | 0.61259 | 0 | 0 | 7.5618 | 0.66163 | 11.429 | 6.9492 | 0.72512 | 0 | 0 | 7.6743 | 1.5289 | 5.0194 | 6.9492 | 1.3377 | 0 | 0 | 8.2869 | 2.1905 | 4.5462 | 3.783 | 3.5269 | 8.1502 | 0 | 49.6832 | 61.3603 | 6.9492 | 0 | 1.3377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.5108 |  | 0 | 0 | 8.2869 | 11.5108 | 0.71992 | 54.2294 | 0.13113 | 0 | 0.13113 | 0.0065566 | 0 | 0.0065566 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Cutting Edge | Efficient network topology | 5 | 21.9628 | 0 | 0 | 0 | 0 | Total Industrial-Total Industrial |  |  | 23.5741 | 0.0029608 | 0.0029394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.8681 | 1.0462 | 0 | 0 | 12.9143 | 0 | 9999 | 11.8681 | 1.2384 | 0 | 0 | 13.1065 | 0 | 9999 | 11.8681 | 2.2846 | 0 | 0 | 14.1527 | 0 | -7.1309 | 9999 | 0 | 0 | 0 | 0 | 0 | 11.8681 | 0 | 2.2846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 14.1527 | 0 | 9999 | -7.1309 | 0.22396 | 0 | 0.22396 | 0.011198 | 0 | 0.011198 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Cutting Edge | Direct current (as opposed to AC) to the racks | 5 | 2.0042 | 0 | 1.0962 | 0 | 0 | Total Industrial-Total Industrial |  |  | 2.1512 | 0.00027019 | 0.00026824 | 0 | 0 | 0 | 0.2186 | 0.50515 | 0 | 3.0794 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2186 | 0.50515 | 0 | 3.0794 | 3.8031 | 1.083 | 0.095471 | 0 | 0 | 1.1785 | 0.2186 | 5.3911 | 1.083 | 0.11301 | 0 | 0 | 1.196 | 0.50515 | 2.3677 | 1.083 | 0.20848 | 0 | 0 | 1.2915 | 0.72375 | 17.6246 | 1.7844 | 7.4771 | 17.2784 | 0 | 105.3283 | 130.0838 | 1.083 | 0 | 0.20848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8031 |  | 0 | 0 | 1.2915 | 3.8031 | 0.33959 | 122.9529 | 0.020437 | 0 | 0.020437 | 0.0010218 | 0 | 0.0010218 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Cutting Edge | Direct liquid cooling of chips | 10 | 11.9968 | 0 | 1.8571 | 0 | 0 | Total Industrial-Total Industrial |  |  | 12.877 | 0.0016173 | 0.0016056 | 0 | 0 | 0 | 0.37033 | 0.85578 | 0 | 2.2267 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37033 | 0.85578 | 0 | 2.2267 | 3.4528 | 6.4828 | 0.57147 | 0 | 0 | 7.0542 | 0.37033 | 19.0484 | 6.4828 | 0.67645 | 0 | 0 | 7.1592 | 0.85578 | 8.3657 | 6.4828 | 1.2479 | 0 | 0 | 7.7307 | 1.2261 | -0.12462 | 6.305 | 2.1162 | 4.8901 | 0 | 12.7237 | 19.73 | 6.4828 | 0 | 1.2479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4528 |  | 0 | 0 | 7.7307 | 3.4528 | 2.239 | 12.5991 | 0.12233 | 0 | 0.12233 | 0.0061166 | 0 | 0.0061166 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Category Results; Sorted by TRC Levelized Cost
Total Results |  | Measure Input Data | [8 empty] | Savings | [5 empty] | PV Capital |  |  |  | PV Admin |  |  |  | PV O&M |  |  |  | PV Periodic Repl. |  |  |  | Total PV Capital, O&M and Periodic Repl Costs |  |  |  |  | PV Wholesale Electric Utility Costs & Benefits | [6 empty] | PV Retail Electric Utility Costs & Benefits | [6 empty] | PV Electric Utility System Costs & Benefits | [5 empty] | Electric Utility System Economics |  | Sponsor Levelized Cost (mills/kwh) |  |  |  |  | PV Regional Costs & Benefits | [15 empty] | TRC Economics |  | Physical CO2 | [6 empty] | Gas Inputs |  |  |  | PV Gas Utility System Costs & Benefits |  |  |  |  | Gas Utility System Economics
Category | Measure | Measure Life | Site Savings (kWh) | Site Savings (therms) | Capital Cost ($/unit) | Annual O&M Cost ($/unit) | PV Per. Repl. Cost ($/unit) | Load Shape (electric) | Diversified Load Factor (electric) | Wholesale Power Coincidence Factor (electric) | Wholesale Electric Energy (kWh) | Wholesale Electric Demand (kw) | Retail Electric Demand (kW) | Wholesale Gas Energy (therms/yr) | Wholesale Gas Demand (therms/day) | Retail Gas Demand (therms/day) | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Total | Wholesale Utility System Energy | Wholesale Utility System T&D Def. Cap. | Wholesale Utility System Act C-E Credit | Wholesale Utility System Risk Mitigation Benefit | Wholesale Utility System Total System Benefit | Wholesale Utility System Total Non-Consumer Cost | Wholesale Utility System B/C Ratio | Retail Utility System Energy | Retail Utility System T&D Def. Cap. | Retail Utility System Act C-E Credit | Retail Utility System Risk Mitigation Benefit | Retail Utility System Total System Benefit | Retail Utility System Total Non-Consumer Cost | Retail Utility System System B/C Ratio | Utility System Energy | Utility System T&D Def. Cap. | Utility System Act C-E Credit | Utility System Total Risk Mitigation Benefit | Utility System Total System Benefit | Utility System Total Non-Consumer Cost | Utility System Net Levelized Cost (Net of Elec T&D Capacity Benefits, Act Credit & Risk-Mitigation Benefit) in mills/kwh | Utility System System B/C Ratio | Wholesale Electric Levelized Cost | Retail Electric Levelized Cost | Natural Gas Levelized Cost | Customer Levelized Cost | Total Levelized Cost | PV Regional Electric Energy | PV Regional Gas Energy | PV Regional Electric T&D Def. Cap. | PV Regional Gas T&D Def. Cap. | PV Regional Electric System CO2 | PV Regional Gas System CO2 | PV Regional Electric System Risk-Mitigation Benefit | PV Regional Gas System Risk-Mitigation Benefit | PV Regional Non-E Value | PV Regional Act Credit | PV Regional Capital Cost | PV Regional Admin Cost | PV Regional Annual O&M Cost | PV Regional Periodic Replacement Cost | PV Total Regional Benefit | PV Total Regional Cost | TRC B/C Ratio | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | Electric System CO2 Avoided (Lifetime Tons) | Gas System CO2 Avoided (Lifetime Tons) | Total System CO2 Avoided (Lifetime Tons) | Electric System CO2 Avoided (Annual Tons in 2018) | Gas System CO2 Avoided (Annual Tons in 2018) | Total System CO2 Avoided (Annual Tons in 2018) |  | Gas Site Savings (therms) | Load Shape (gas) | Diversitfied Load Factor (gas) | Wholesale Coincidence Factor (gas) | Total Gas Utility System Energy | Gas Utility System T&D Def. Cap. | Gas Utility System Risk Mitigation Benefit | Gas Utility System Total System Benefit | Gas Utility System Total Non-Consumer Cost | Gas Utility System Net Levelized Cost (Net of Gas T&D Capacity Benefits & Risk-Mitigation Benefits) in cents/therm | Gas Utility System System B/C Ratio
Best Practice |  | 5 | 447.3063 | 0 | 30.9615 | 0 | 0 |  |  |  | 480.1237 | 0.060302 | 0.059866 | 0 | 0 | 0 | 6.1741 | 14.2675 | 0 | 86.9741 | 1.8577 | 4.3346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0318 | 18.6021 | 0 | 86.9741 | 113.608 | 241.7122 | 21.3075 | 0 | 0 | 263.0198 | 8.0318 | 32.7472 | 241.7122 | 25.2218 | 0 | 0 | 266.934 | 18.6021 | 14.3497 | 241.7122 | 46.5293 | 0 | 0 | 288.2415 | 26.6339 | -3.0491 | 10.8223 | 1.2309 | 2.8509 | 0 | 13.3293 | 17.4111 | 241.7122 | 0 | 46.5293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.4157 | 6.1923 | 0 | 0 | 288.2415 | 113.608 | 2.5372 | 10.2802 | 4.5612 | 0 | 4.5612 | 0.22806 | 0 | 0.22806 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Cutting Edge |  | 6.2286 | 48.8237 | 0 | 6.2712 | 0 | 0 |  |  |  | 52.4058 | 0.006582 | 0.0065345 | 0 | 0 | 0 | 1.2506 | 2.8899 | 0 | 14.6263 | 0.37627 | 0.87797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6268 | 3.7678 | 0 | 14.6263 | 20.021 | 26.383 | 2.3257 | 0 | 0 | 28.7088 | 1.6268 | 17.647 | 26.383 | 2.753 | 0 | 0 | 29.136 | 3.7678 | 7.7328 | 26.383 | 5.0787 | 0 | 0 | 31.4617 | 5.3947 | 0.44363 | 5.832 | 2.2842 | 5.2903 | 0 | 20.5365 | 28.111 | 26.383 | 0 | 5.0787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.7667 | 1.2542 | 0 | 0 | 31.4617 | 20.021 | 1.5714 | 20.9801 | 0.49786 | 0 | 0.49786 | 0.024893 | 0 | 0.024893 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial Technology |  | 7.8807 | 206.5686 | 0 | 43.3659 | 0 | 0 |  |  |  | 221.7239 | 0.027848 | 0.027647 | 0 | 0 | 0 | 8.6477 | 19.9836 | 0 | 66.0159 | 2.602 | 6.0712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.2497 | 26.0548 | 0 | 66.0159 | 103.3204 | 111.6241 | 9.8399 | 0 | 0 | 121.464 | 11.2497 | 10.7971 | 111.6241 | 11.6476 | 0 | 0 | 123.2717 | 26.0548 | 4.7312 | 111.6241 | 21.4875 | 0 | 0 | 133.1116 | 37.3045 | 5.2491 | 3.5682 | 3.7333 | 8.6466 | 0 | 21.9082 | 34.2881 | 111.6241 | 0 | 21.4875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.6472 | 8.6732 | 0 | 0 | 133.1116 | 103.3204 | 1.2883 | 27.1572 | 2.1064 | 0 | 2.1064 | 0.10532 | 0 | 0.10532 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Supply Curve Results; Categories sorted by TRC Net Levelized Cost
Totals for Categories with Benefits Exceeding Costs. Levelized cost is TRC Net Levelized Cost (Net of Benefits) | [12 empty] | Savings Allocation by Cost Bin and Month for Segments 1 | [12 empty] | Savings Allocation by Cost Bin and Month for Segments 2
| Totals Basis | Busbar Electric Savings in kWh | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Measures with B/C > 1.00 | 713.2885 | 65.9871 | 0 | 65.9871 | 184.161 | 428.2217 | 810.3977 | -2.6366 | 11.8669 | 1078.3554 | 6.7763 | 34.4486 | 32.368 | 36.7128 | 33.4509 | 34.3094 | 34.2 | 32.7464 | 37.3554 | 32.1747 | 36.5537 | 31.5896 | 32.1638 |  | 27.7336 | 24.9465 | 24.8121 | 24.9325 | 25.2546 | 23.4118 | 26.3223 | 25.0851 | 26.2351 | 24.6112 | 25.8843 | 25.9859
| Categories with B/C > 1.00 | 754.2534 | 80.5986 | 16.1197 | 96.7183 | 236.9493 | 452.8149 | 1123.2993 | -0.36704 | 15.9849 | 2.103 | 7.1655 | 13.2392 | 12.4396 | 14.1094 | 12.8558 | 13.1857 | 13.1437 | 12.5851 | 14.3564 | 12.3653 | 14.0483 | 12.1405 | 12.3611 |  | 10.6585 | 9.5874 | 9.5357 | 9.582 | 9.7058 | 8.9976 | 10.1161 | 9.6407 | 10.0826 | 9.4585 | 9.9478 | 9.9869
Supply Curve Results: By TRC Net Levelized Cost - Net of Benefits
| Block 1: <= 0 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 2: <= 10 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 3: 10-20 mills/kWh | 480.1237 | 30.9615 | 6.1923 | 37.1538 | 113.608 | 288.2415 | 677.8822 | -3.0491 | 10.2802 | 2.5372 | 4.5612 | 23.1878 | 21.7873 | 24.7119 | 22.5162 | 23.0941 | 23.0205 | 22.0421 | 25.1444 | 21.6572 | 24.6048 | 21.2634 | 21.6498 |  | 18.6679 | 16.7918 | 16.7013 | 16.7824 | 16.9992 | 15.7588 | 17.7179 | 16.8851 | 17.6592 | 16.5661 | 17.423 | 17.4915
| Block 4: 20-30 mills/kWh | 274.1297 | 49.6371 | 9.9274 | 59.5645 | 123.3413 | 164.5733 | 1903.4239 | 4.3304 | 25.9763 | 1.3425 | 2.6043 | 13.2392 | 12.4396 | 14.1094 | 12.8558 | 13.1857 | 13.1437 | 12.5851 | 14.3564 | 12.3653 | 14.0483 | 12.1405 | 12.3611 |  | 10.6585 | 9.5874 | 9.5357 | 9.582 | 9.7058 | 8.9976 | 10.1161 | 9.6407 | 10.0826 | 9.4585 | 9.9478 | 9.9869
| Block 5: 30-40 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 6: 40-50 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 7: 50-60 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 8: 60-70 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 9: 70-80 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 10: 80-90 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 11: 90-100 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 12: 100-110 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 13: 110-120 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 14: 120-130 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 15: 130-140 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 16: 140-150 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 17: 150-160 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 18: 160-170 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 19: 170-180 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 20: 180-190 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 21: 190-200 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 22: > 200 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Shaped Savings Results; By Category and sorted by TRC BC ratio
[13 empty] | Savings Allocation by Cost Bin and Month for Segments 1 Feb: Savings Allocation by Category and Month for Segments 1 |  |  | Savings Allocation by Category and Month for Segments 2
Category | Measure | Busbar Savings | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Wholesale KW | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Best Practice |  | 480.1237 | 30.9615 | 6.1923 | 37.1538 | 113.608 | 288.2415 | 677.8822 | -3.0491 | 10.2802 | 2.5372 | 4.5612 | 0.060302 | 23.1878 | 21.7873 | 24.7119 | 22.5162 | 23.0941 | 23.0205 | 22.0421 | 25.1444 | 21.6572 | 24.6048 | 21.2634 | 21.6498 |  | 18.6679 | 16.7918 | 16.7013 | 16.7824 | 16.9992 | 15.7588 | 17.7179 | 16.8851 | 17.6592 | 16.5661 | 17.423 | 17.4915
Cutting Edge |  | 52.4058 | 6.2712 | 1.2542 | 7.5254 | 20.021 | 31.4617 | 1257.9305 | 0.44363 | 20.9801 | 1.5714 | 0.49786 | 0.006582 | 2.531 | 2.3781 | 2.6973 | 2.4577 | 2.5207 | 2.5127 | 2.4059 | 2.7445 | 2.3639 | 2.6856 | 2.3209 | 2.3631 |  | 2.0376 | 1.8328 | 1.823 | 1.8318 | 1.8555 | 1.7201 | 1.9339 | 1.843 | 1.9275 | 1.8082 | 1.9017 | 1.9092
Commercial Technology |  | 221.7239 | 43.3659 | 8.6732 | 52.0391 | 103.3204 | 133.1116 | 2055.9902 | 5.2491 | 27.1572 | 1.2883 | 2.1064 | 0.027848 | 10.7083 | 10.0615 | 11.4121 | 10.3981 | 10.665 | 10.631 | 10.1791 | 11.6118 | 10.0014 | 11.3626 | 9.8196 | 9.998 |  | 8.6209 | 7.7546 | 7.7128 | 7.7502 | 7.8503 | 7.2775 | 8.1822 | 7.7976 | 8.1551 | 7.6503 | 8.0461 | 8.0777
Note on I6: :ProCost Perioodic replacement costs and savinsg of the measure. These are costs and savings that occur periodicially, but at different periods than annually. Can be positive or negative. Periodic replacement costs for both the measure and the baseline measure should be included if applicable. ProCost can analysze these costs in two ways dependent on the 'Repeat Periodic Replacemetn' switch in the ProData page. When set to 'On', ProCost repeats replacement costs for multiple times over the life of a measure depending on the input period and measure life. For example fluorescent lamps may have a 4-year replacement cycle that repeats 3 times in a 15-year measure life. When set to 'Off', ProCost reads the period as the year after installation that the replacement cost occurs and does not subsequently reinstall or repeat the replacement costs. For example a compressor may be replaced only once in the life of a heat-pump system. Example: A new fluorescent lighting systems may have a measure life of 15 years, and a lamp life of five years. Two lamps lamps per fixture must be replaced at years 6 and 11. Lamp and labor costs, expressed as positive costs, are entered as a cost and the period would be enetered as 5. The baseline measure may have a four year lamp life and would have required a three-lamp replacement at years 5, 9 and 13. Lamp and labor replacement costs would be entered as annual savings in dollars with a 4-year period. ProCost determines the net present value of the two cost streams.
Note on O6: :ProCost If the measure has gas savings for incfreases, enter the annual savings and shape of the savings here. Example: Clothes washer saves electric motor and dryer energy and gas water heat.
Note on A7: :Procost Category for the measure. Individual measures can be grouped into categories. Procost output is reported by measure and by category. All measures must belong to at least one category. Category name can be the same as measure name. Example: Measures can be combined into one category if they have components with different load shapes or measure lives. On wash machines there may be one load shape for the electric motor savings component, a second load shape for the electric water heat savings component and a third shape for electric dryer savings component.
Note on B7: :ProCost Name of Measure. User-defined. For PTR measures, defined naming conventions apply.
Note on C7: :ProCost Annual electric savings for the measure in kWh at the site. May be positive, negative or zero. Savings are incremental to the baseline alternative.
Note on D7: :ProCost Physical life of the measure in years. Must be >=1.
Note on E7: :ProCost Initial cost to install the measure in dollars. Costs are incremental to the baseline alternative. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on F7: :ProCost Annaul opperations and maintenace cost for the measure in dollars. Must be incremental cost over the baseline alternative. May be positive, negative or zero. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page. O&M costs are enetered as positive values. Negative values represent O&M savings compared to the baseline alternative. Example: Annualized maintenace cost for a heat pump heating system compared to a baseline electric resistance heating system.
Note on G7: :ProCost Name of the pointer to the shape of the savings. The shapes represent the daily and monthly shape of the savings in four time segments for each month of the year. Shape of the savings is relative to the baseline alternative. These shaps are in the MC_AND_Loadshape file.
Note on H7: :ProCost Annual value of any non-energy benefits of the measure, relative to the baseline alternative. Expressed in dollars per year and denominated in dollars of the 'Cost Reference Year'. Positive value represents dollar savings. Negative value represents dollar cost. Example: Water, detergent and sewer savings from efficient clothes washer.
Note on I7: : Cost in dollars that is incurred for Period 1. Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on J7: :ProCost Duration of Period1. The time at which Period 1 costs, or savings, occur. In years.
Note on K7: : Cost in dollars that is incurred for Period 2 Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on L7: :ProCost Duration of Period 2. The time at which Period 2 costs, or savings, occur. In years.
Note on M7: : Cost in dollars that is incurred for Period 3. Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on N7: :ProCost Duration of Period 3. The time at which Period 3 costs, or savings, occur. In years.
Note on O7: : Annual gas savings, or increases, in therms.
Note on P7: :ProCost Name of the pointer to the shape of the savings. The shapes represent the daily and monthly shape of the savings in four time segments for each month of the year. Shape of the savings is relative to the baseline alternative. These shaps are in the MC_AND_Loadshape file.
Note on BH56: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BM56: Direct and program administrative costs of the measure to sponsor. Separate costs for each sponsor. Depends on share of costs incurred by sponsor, sponsor cost of capital, and financing term which are user-defined inputs. Includes applicable Capital, O&M, Periodic Replacement and Program Administrative costs. Sponsor costs are levelized over program life. Does not include any adjustments for benefit. NOTE: Units are per kWh for 'Electric' runs and per therm for 'Gas' runs for all sponsors.
Note on CE56: All costs minus all benefits regardless of which sponsor incurs the cost or accrues the benefits. TRC Net Levelized Cost includes all applicable costs and all benefits. In addition to energy system costs and benefits, TRC Net Levelized Cost includes non-energy, other-fuel, O&M, periodic-replacement and risk-mitigation benefits and costs. TRC Net Levelized Cost corresponds to TRC B/C ratios with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure. The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the TRC B/C ratio and the TRC Net Levelized Cost. If Risk-Mitigation credit is non-zero, TRC Levelized Cost will be reduced by the risk-mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on CW56: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BH83: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BM83: Direct and program administrative costs of the measure to sponsor. Separate costs for each sponsor. Depends on share of costs incurred by sponsor, sponsor cost of capital, and financing term which are user-defined inputs. Includes applicable Capital, O&M, Periodic Replacement and Program Administrative costs. Sponsor costs are levelized over program life. Does not include any adjustments for benefit. NOTE: Units are per kWh for 'Electric' runs and per therm for 'Gas' runs for all sponsors.
Note on CE83: All costs minus all benefits regardless of which sponsor incurs the cost or accrues the benefits. TRC Net Levelized Cost includes all applicable costs and all benefits. In addition to energy system costs and benefits, TRC Net Levelized Cost includes non-energy, other-fuel, O&M, periodic-replacement and risk-mitigation benefits and costs. TRC Net Levelized Cost corresponds to TRC B/C ratios with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure. The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the TRC B/C ratio and the TRC Net Levelized Cost. If Risk-Mitigation credit is non-zero, TRC Levelized Cost will be reduced by the risk-mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on CW83: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.

## CostData
From Cadmus as Part of Council 7P Analysis Contract: Contact is Bob Huang.
Measure | Category | Modelled in NPCC Model | Payback period (years) | Low Payback | High Payback | Average Payback | Average commercial rate of electricity ($/kWh) | Average Cost ($/kWh) | Lifetime | Real Discount Rate | Real Levelized Cost of Energy Savings ($/kWh) | Share of Tier Savings | kWh Saved per kWh DC Load | First Cost per kWh Saved | Scenario | Levelized Cost $/kWh | First Cost $/kWh Saved | kWh Saved per kWh DC Load | Sources for Payback Periods of EETBPs (Listed in Table 40)
Decommissioning of unused servers | BP | Y | - | 0.1 | 0.5 | 0.3 | 0.1032 | 0.03096 | 5 | 4% | 0.0069545 | 15% | 6.711% | 0.0020776 | Best Practices | 0.015545 | 0.069206 | 0.44738 | Appliances N: NetApp Introduces Unified Scale-Out Storage Systems and Virtualization Software for the Unbound Cloud Era. Edited by; 2014.
Server virtualization/consolidation | BP | Y | 0.1-1.5 | 0.1 | 1.5 | 0.8 | 0.1032 | 0.08256 | 5 | 4% | 0.018545 | 67.3% | 30.11% | 0.024856 | Commercial Technology | 0.02953 | 0.20559 | 0.21094 | Asetek: Internal Loop Liquid Cooling. Edited by; 2014.
Server power management | BP | Y | - | 0 | 0 | 0 | 0.1032 | 0 | 5 | 4% | 0 | 5.225% | 2.338% | 0 | Cutting Edge Technology | 0.024274 | 0.12472 | 0.050281 | Associates JGa: Enterprise Class SSD: A Business Benefit Analysis. Edited by; 2014.
Energy efficient data storage management | BP | Y | 0.5 - 0.9 | 0.5 | 0.9 | 0.7 | 0.1032 | 0.07224 | 5 | 4% | 0.016227 | 12.46% | 5.575% | 0.0040274 |  |  |  |  | Bushell, Michael J: Top 10 Energy Conservation Measures for Data Centers. Willdan Energy Solutions. Presentation to Energy Center of Wisconsin, December 11, 2014.
Energy efficient servers | ComT | Y | 1-1.5 | 1 | 1.5 | 1.25 | 0.1032 | 0.129 | 5 | 4% | 0.028977 | 36.78% | 7.758% | 0.010008 |  |  |  | 0.7086 | Consulting F: The Total Economic Impact of VMware vCenter Configuration Manager. Edited by; 2009.
Massive array of idle disks (MAID) | ComT | Y | 1-1.5 | 1 | 1.5 | 1.25 | 0.1032 | 0.129 | 5 | 4% | 0.028977 | 11.04% | 2.329% | 0.003004 |  |  |  |  | Corporation ID: IT Management and Virtualization Software Reduce Cost and Energy Consumption at BMC Datacenter: An ROI Case Study. Framingham, MA; 2008.
Efficient network topology | ComT | Y |  | 0 | 0 | 0 | 0.1032 | 0 | 5 | 4% | 0 | 12.41% | 2.618% | 0 |  |  |  |  | Corporation ID: Storage Economics: Assessing the Real Cost of Storage. Edited by. London, UK; 2008.
Energy efficient transformers | ComT | Y | 2.0 - 4.0 | 2 | 4 | 3 | 0.1032 | 0.3096 | 5 | 4% | 0.069545 | 2.278% | 0.4806% | 0.0014878 | Turnover Rate | 16.67% |  |  | Corporation ID: The Business Value of Dell EqualLogic and Compellent Primary Storage Solutions. Edited by. London, UK.
Energy efficient power supplies (UPS) | ComT | Y | 1-6.7 | 1 | 6.7 | 3.85 | 0.1032 | 0.39732 | 15 | 4% | 0.035735 | 21% | 4.43% | 0.0176 | Average Measure Life | 5.9322 |  |  | Courtot P: Energy Savings Potential of CSL-3 Transformers and PDU’s in Data Centers. Edited by; 2009.
Energy efficient lighting | ComT | Y | 2.2-3 | 2.2 | 3 | 5 | 0.1032 | 0.516 | 10 | 4% | 0.063618 | 5% | 1.055% | 0.0054422 |  |  |  |  | Ellis DL: DATA CENTER DESIGN CONSIDERATIONS AND TRENDS. Edited by: IEEE Central Tennessee Section; 2009.
Hot or cold aisle configuration | ComT | Y | 1-2.2 | 1 | 2.2 | 1.6 | 0.1032 | 0.16512 | 10 | 4% | 0.020358 | 0.628% | 0.1325% | 0.00021873 |  |  |  |  | Energy USDo: Database Technology Company Saves $262,000 Annually. Edited by. Washington, DC; 2009.
Hot or cold aisle configuration plus containment (e.g., strip curtains or rigid enclosures) | ComT | Y | 0.7-3.3 | 0.7 | 3.3 | 2 | 0.1032 | 0.2064 | 10 | 4% | 0.025447 | 1.256% | 0.2649% | 0.00054684 |  |  |  |  | Geet IMaOV: Data Center Energy Efficiency and Renewable Energy Site Assessment: Anderson Readiness Center. Edited by. Golden, CO: National Renewable Energy Laboratory; 2014.
Variable speed drives on pumps/fans | ComT | Y | 0.5-2.4 | 0.5 | 2.4 | 1.45 | 0.1032 | 0.14964 | 10 | 4% | 0.018449 | 1.256% | 0.2649% | 0.00039646 |  |  |  |  | Google: Google’s Green Data Centers: Network POP Case Study. Mountain View, CA: 2011.
Premium efficiency motors | ComT | Y | 2.6 | 2.6 | 2.6 | 2.6 | 0.1032 | 0.26832 | 10 | 4% | 0.033081 | 1.256% | 0.2649% | 0.00071089 |  |  |  |  | Grid G: CASE STUDY: THE ROI OF COOLING SYSTEM ENERGY EFFICIENCY UPGRADES. Edited by; 2011.
Air-side economizer | ComT | Y | 0.8-6.9 | 0.8 | 6.9 | 3.85 | 0.1032 | 0.39732 | 10 | 4% | 0.048986 | 1.256% | 0.2649% | 0.0010527 |  |  |  |  | Group SVL: Cisco Lab Setpoint Increase: Energy Efficient Data Center Demonstration Project. Edited by. San Jose, CA; 2008.
In-row cooling | ComT | Y | 2.0 - 3.0 | 2 | 3 | 2.5 | 0.1032 | 0.258 | 10 | 4% | 0.031809 | 1.256% | 0.2649% | 0.00068355 |  |  |  |  | Group SVL: Control of Computer Room Air Handlers Using Wireless Sensors: Energy Efficient Data Center Demonstration Project. Edited by. San Jose, CA; 2009.
Water-side economizer | ComT | Y | 2.3-6.9 | 2.3 | 6.9 | 4.6 | 0.1032 | 0.47472 | 10 | 4% | 0.058529 | 1.256% | 0.2649% | 0.0012577 |  |  |  |  | IBM: 2009. Edited by. Somers, NY; Cloud Computing: An Explanation of Where ROI Comes From.
Install misters, foggers, or ultrasonic humidifiers | ComT | Y | 1.9-5.1 | 1.9 | 5.1 | 3.5 | 0.1032 | 0.3612 | 10 | 4% | 0.044533 | 1.256% | 0.2649% | 0.00095696 |  |  |  |  | Kanellos M: The World’s Best Green Technology? Edited by; 2010.
Solid state storage | CET | Y | 2.0 - 3.0 | 2 | 3 | 2.5 | 0.1032 | 0.258 | 5 | 4% | 0.057954 | 25.58% | 1.286% | 0.0033179 |  |  |  |  | Kelly M: 365 Main Energy Efficiency Initiatives. Edited by.
Efficient network topology | CET | Y |  | 0 | 0 | 0 | 0.1032 | 0 | 5 | 4% | 0 | 43.68% | 2.196% | 0 |  |  |  |  | Mahdavi R: Energy Efficiency Opportunities in Federal High Performance Computing Data Centers: Prepared for the U.S. Department of Energy Federal Energy Management Program. Edited by. Berkeley, CA: Lawrence Berkeley National Laboratory; 2013.
Direct current (as opposed to AC) to the racks | CET | Y | 5.3 | 5.3 | 5.3 | 5.3 | 0.1032 | 0.54696 | 5 | 4% | 0.12286 | 3.986% | 0.2004% | 0.0010962 |  |  |  |  | Mahdavi R: Opportunities to Improve Energy Efficiency in Three Federal Data Centers: Prepared for the U.S. Department of Energy’s Federal Energy Management Program. Edited by. Berkeley, CA: Lawrence Berkeley National Laboratory; 2014.
Direct liquid cooling of chips | CET | Y | 1.0 - 2.0 | 1 | 2 | 1.5 | 0.1032 | 0.1548 | 10 | 4% | 0.019085 | 23.86% | 1.2% | 0.0018571 |  |  |  |  | Power EN: Energy Efficiency Solutions for Your Data Center. Edited by; 2014.
Computational fluid dynamics optimization | BP | N | <1 | 0 | 1 | 0.5 | 0.1032 | 0.0516 | 10 | 4% | 0.0063618 | [7 empty] | Research F: The Total Economic Impact of HP 3PAR Storage. Edited by. Cambridge, MA; 2012.
Blanking panels, grommets, or structured cabling | BP | N | 1 | 1 | 14 | 7.5 | 0.1032 | 0.774 | 10 | 4% | 0.095427 | [7 empty] | Resources WDoN: Godfrey & Kahn – Server Virtualization. Edited by; 2012.
Adjusting server inlet temperatures | BP | N | - | 0 | 0 | 0 | 0.1032 | 0 | 10 | 4% | 0 | [7 empty] | Systems HD: Tiered Storage and Virtualization in the Real World: Calculating the ROI and Cost Savings of a Move to Tiered Storage by Fidelity National Information Services. Edited by; 2009. vol October 2009.]
Broaden humidity range | BP | N | - | 0 | 0 | 0 | 0.1032 | 0 | 10 | 4% | 0 | [7 empty] | Target T: Data Center Energy Efficiency Guide. Edited by; 2011.
Turn off humidifiers | BP | N | - | 0 | 0 | 0 | 0.1032 | 0 | 10 | 4% | 0 | [7 empty] | Technologies P: Initial investment payback analysis report: Dell PowerEdge R710 solution with Hyper-V vs. Dell PowerEdge 2850 solution. Edited by. Durham, North Carolina; 2009.
Vellante D: JCPenney tiers away energy costs. Edited by; 2010.
Wire B: Asetek Wins Frost & Sullivan Award for Their Revolutionary Data Center Cooling Solution. Edited by; 2014.
Note on E3: robert.huang: From unpublished NYSERDA work
Note on I3: robert.huang: Assumed average commercial rate across US, based on EPA data
Note on K3: robert.huang: From Massoud's estimates for Localized DCs.
Note on L3: robert.huang: Provided by Charlie Grist, NWPCC
Note on N3: robert.huang: Based on examination of NPCC model.
Note on F4: Charlie Grist: Revised to add some cost.
Note on G4: Charlie Grist: Revised to add some cost.
Note on M4: Charlie Grist: Revised to add some cost.
Note on K12: Charlie Grist: Revised to 15 years based on Green Grid and comment from BPA.
Note on H13: Charlie Grist: Revised upward from 2.6 based on lower assumed hours of lighting operation.

## ETO Server Virt Estim
Server Virtualization
EUI and Costs QC Checked
No O&M
| ETO Model Building Type | CBSA Building Type | CBECS 2003 Mapped Building Type | CBSA Building Square Footage | Number of Servers per 1000 SQFT | Implied Number of Servers per Building | Annual Savings per Server (kWh per 1000 SQFT) | Cost per Server ($/1000 SQFT)
| Total | Average All Buildings | Average All Buildings | 14338 | 0.11 | 1.5772 | 3.463 | 2.963
| C_Retail | Dry Goods Retail | Mercantile | 14395 | 0.08 | 1.1516 | 3.463 | 2.963
| C_Grocery | Grocery | Food Sales | 17096 | 0 | 0 | 3.463 | 2.963
| C_Office | Office | Office | 17635 | 0.18 | 3.1743 | 3.463 | 2.963
| C_Restaurant | Restaurant | Food Service | 4486 | 0 | 0 | 3.463 | 2.963
| C_Warehouse | Warehouse | Warehouse | 21176 | 0.04 | 0.84704 | 3.463 | 2.963
| C_Hospital | Hospital | Inpatient | 37989 | 0 | 0 | 3.463 | 2.963
| C_Lodging | Hotel/Motel | Lodging | 28126 | 0 | 0 | 3.463 | 2.963
| C_Other Health | Other Health | Outpatient | 16637 | 0.1 | 1.6637 | 3.463 | 2.963
| C_Other | Other | Other | 8062 | 0.03 | 0.24186 | 3.463 | 2.963
| C_School | School | Education | 30768 | 0.16 | 4.9229 | 3.463 | 2.963
| C_College | University | Education | 37795 | 0.1 | 3.7795 | 3.463 | 2.963
| C_Data Center | NA | NA | 334000 | 506.1839 | 169065.4206 | 3.463 | 2.963
| Baseline Initial Saturation |  | Enterprise Data Center Baseline Initial Saturation
| 63% | However, virtualization is less common in small data centers. A 2012 NRDC paper entitled Small Server Rooms, Big Energy Savings included an informal survey of 30 small businesses (ranging from 3 to 750 employees) and found that only 37% used virtualization. | 5%
| Source: 2013, Energy Star, Data Center Energy Efficiency Strategies - Server Virtualization (http://www.energystar.gov/index.cfm?c=power_mgt.datacenter_efficiency_virtualization) |  | Source: Discussion with ETO for data center measures 02/26/2014 - very low baseline initial saturation for data centers
Energy and Cost Savings
| Number of servers | 54
| Annual Energy Savings (kWh) | 187000
| Annual Energy Savings per Server (kWh/Server) | 3462.963
| Total Cost | 160000
| Total Cost per Server | 2962.963
| $/kWh Saved | 0.85561
| Measure Lifetime (years) | 4 | Based on Energy Star userful life of a server (https://www.energystar.gov/index.cfm?c=power_mgt.datacenter_efficiency_purchasing)
Source: 2007, Green Building Research Center, Best Practices Case Studies - University of California, Santa Cruz Server Virtualization (http://greenbuildings.berkeley.edu/pdfs/bp2007_ucsc_virtualization.pdf)
Table C-EQ3 ( Miscellaneous Equipment: Number of Servers) of CBSA 2009 Final Report, Base = Have Server(s)
| ETO Model Building Type | Total | C_Retail | C_Grocery | C_Office | C_Restaurant | C_Warehouse | C_Hospital | C_Lodging | C_Other Health | C_Other | C_School | C_College
| Number of Servers | Total | Dry Goods Retail | Grocery | Office | Restaurant | Warehouse | Hospital | Hotel/Motel | Other Health | Other | School | University | Vacant
| Per 1000 SQFT | 0.11 | 0.08 | 0 | 0.18 | 0 | 0.04 | 0 | 0 | 0.1 | 0.03 | 0.16 | 0.1 | 0
| Observations | 165 | 16 | 5 | 74 | 2 | 12 | 3 | 3 | 11 | 17 | 20 | M | 2
|  |  |  | Small |  | Small |  | Small | Small |  |  |  | Medium
Source: Adapted from 2009, NEEA, Commercial Building Stock Assessment; Table C-EQ3 Miscellaneous Equipment: Number of Servers
Table C-EQ3 Servers/1000 SQFT Statistics
| Min | 0
| Max | 0.18
| Mean | 0.1
| Median | 0.1
Note on C41: Navigant: Updated to 0 from 0.03 per discussion with ETO 03/30/2014.

## 6P Server Virt
PUE
| Summary of Savings Estimates, Normalized to kWh per Server Eliminated and per New Virtual Server |  |  |  | 1.6
| Source | kWh per Server Eliminated | kWh per New Virtual Server | Treatment of PUE | kWh per Server Eliminated with PUE
| ETO per ERS work papers | 1916 | 17245 | Cooling only | 2490.8
| VMWare (Vendor Case Studies) | 2857.0468 | 32856.0386 | None | 4571.2749
| BC Hydro (Project Data) | 2541 | 25000 | Included | 2541
| Green IT White Paper (Typical Examples) | 1500 | 13140 | None | 2400
| VMWare rule of thumb for sales presentations | 7000 |  | Included high | 7000
| 6Plan Estimate with low end PUE |  |  |  | 2500
Development of Cost and Savings Numbers
V Ratio | Approach | Annual Savings | Life | Capital | Annual OM | Shape | NEV | Cost per First Year Savings | Quick Levelized Cost
9 | Per 10 Servers Virtualized including Avoided Legacy Servers | 22500 | 4 | 19000 | -18423 | ExCommLight |  | 0.025644 | 0.0070648
9 | Per 10 Servers Virtualized NO Avoided Legacy Servers | 22500 | 4 | 19000 | -7560 | ExCommLight |  | 0.50844 | 0.14007
9 | Per 10 Servers Virtualized NO Avoided Legacy Servers NO O&M Savings | 22500 | 4 | 19000 | 0 | ExCommLight |  | 0.84444 | 0.23264

## ETO Data Centers
Data Centers
| Measure # | Energy Efficiency Measure Name | Measure Group | Measure Lifetime (Maximum 70 yrs) | Annual Electricity Savings (kWh) | Total Incremental Cost of Measure | Total Incremental Cost of Measure per SQFT (Assuming 10000 SQFT) | Total Potential Incentive If Measure is Cost-effective | Combined Utility System BCR | Combined Societal BCR | kWh Levelized Cost | Simple Customer Payback w/ Incentive (years) | Source
| 1 | High Efficiency Power Distribution | Power Distribution | 15 | 5170000 | 700000 | 70 | 245000 | 19 | 6.7 | 0 | 1.2 | Source: 2014, ETO, Data Center Power Distirbution Blessing Memo
(Custom Project Example)
| Source: Adapted from 2013, ETO, Data Center Power Distribution Blessing Memo |  |  | Per 1000 SQFT | 5170 | 700
| Metric | Value | Source
| Data Center PDU Density (PDU's/1000 SQFT) | 0.002994 | Breakouts incorporated into savings calculations; assumed 1 central PDU per data center
| Enterprise Data Center Baseline Initial Saturation | 90% | Discussion with ETO for data center measures 02/26/2014 - very high baseline initial saturation for data centers, requirement for program
| Measure # | Energy Efficiency Measure Name | Measure Group | Measure Lifetime (Maximum 70 yrs) | Annual Electricity Savings (kWh) | Total Incremental Cost of Measure | Total Incremental Cost of Measure per SQFT (Assuming 10000 SQFT) | Total Potential Incentive If Measure is Cost-effective | Combined Utility System BCR | Combined Societal BCR | kWh Levelized Cost | Simple Customer Payback w/ Incentive (years) | Source
| 1 | High Efficiency Custom Server | Server | 3 | 78 | 13 | 0.0013 | 4 | 3.6 | 1.3 | 0.02 | 1.4 | Source: 2014, ETO, Data Center Server Blessing Memo
(Custom Project Example)
| 2 | ENERGYSTAR v1.1 Server | Server | 3 | 565 | 45 | 0.0045 | 98 | 1.2 | 2.5 | 0.06 | -1.3 | Source: 2014, ETO, Data Center Server Blessing Memo
(savings from 80 PLUS)
| Source: Adapted from 2013, ETO, Data Center Server Blessing Memo |  |  | Per 1000 SQFT | 0.565 | 0.045
| Metric | Value | Source
| Server Density (Servers/1000 SQFT) | 506.1839 | Calculated
| Enterprise Data Center Baseline Initial Saturation | 5% | Discussion with ETO for data center measures 02/26/2014 - very low baseline initial saturation for data centers, requirement for program
http://www.pge.com/includes/docs/pdfs/mybusiness/energysavingsrebates/incentivesbyindustry/DataCenters_BestPractices.pdf
| Measure # | Energy Efficiency Measure Name | Measure Group | UPS kW Rating | Wattage Scaling Factor (Based on Facebook Prinville OR Electrical UPS Specifications) | Measure Lifetime (Maximum 70 yrs) | Annual Electricity Savings (kWh/UPS) | Scaled Annual Electricity Savings (kWh/UPS) | Total Incremental Cost of Measure ($/UPS) | Scaled Total Incremental Cost of Measure ($/UPS) | Total Potential Incentive If Measure is Cost-effective | Combined Utility System BCR | Combined Societal BCR | kWh Levelized Cost | Simple Customer Payback w/ Incentive (years) | Source | Notes
| 1 | 5 kW UPS | Voltage and Frequency Independent (VFI) - Double Conversion UPS | 5 | 11.32 | 5 | 247 | 2796.04 | 225 | 2547 | 37 | 2.2 | 0.4 | 0.03 | 10.4 | Source: 2014, ETO, Data Center Uninterruptible Power Supply Blessing Memo | Straight weight from 75kW Design Capacity due to limited data on measure group shares. Known that the Open Compute project moved away from centralized UPS (http://mvdirona.com/jrh/TalksAndPapers/Open_Compute_Project_Battery_Cabinet_v1.0.pdf).
VFI
| 2 | 10 kW UPS | Voltage and Frequency Independent (VFI) - Double Conversion UPS | 10 | 5.66 | 15 | 1189 | 6729.74 | 450 | 2547 | 178 | 6 | 2.4 | 0.01 | 3.1 | Source: 2014, ETO, Data Center Uninterruptible Power Supply Blessing Memo
VFI
| 3 | 1,000 kW UPS | Voltage and Frequency Independent (VFI) - Double Conversion UPS | 1000 | 0.0566 | 15 | 217532 | 12312.3112 | 20000 | 1132 | 32630 | 6 | 9.8 | 0.01 | -0.8 | Source: 2014, ETO, Data Center Uninterruptible Power Supply Blessing Memo
VFI
| 4 | 1.5 kW UPS | Voltage Independent (VI) - Interactive UPS | 1.5 | 37.7333 | 5 | 120 | 4528 | 26 | 981.0667 | 18 | 2.2 | 1.5 | 0.03 | 0.9 | Source: 2014, ETO, Data Center Uninterruptible Power Supply Blessing Memo
VI
| 5 | 5 kW UPS | Voltage Independent (VI) - Interactive UPS | 5 | 11.32 | 5 | 443 | 5014.76 | 150 | 1698 | 66 | 2.2 | 1 | 0.03 | 2.6 | Source: 2014, ETO, Data Center Uninterruptible Power Supply Blessing Memo
VI
| 6 | 1.5 kW UPS | Voltage and Frequency Dependent (VFD) - Standby UPS | 1.5 | 37.7333 | 5 | 120 | 4528 | 7 | 264.1333 | 18 | 2.2 | 5.6 | 0.03 | -1.3 | Source: 2014, ETO, Data Center Uninterruptible Power Supply Blessing Memo
VFD
| Source: Adapted from 2013, ETO, Data Center Uninterruptible Power Supply Blessing Memo |  |  | 170.5 | AVERAGE | 8.3333 |  | 5984.8085 |  | 1528.2
[7 empty] | Per 1000 SQFT | 5.9848 |  | 1.5282
| Metric | Value | Source
| UPS Density (UPS/1000 SQFT) | 0.89065 | Calculated
| Enterprise Data Center Baseline Initial Saturation | 90% | Discussion with ETO for data center measures 02/26/2014 - very high baseline initial saturation for data centers, requirement for program
| Metric | Value | Notes | Source
| Facebook Power Usage Effectiveness (PUE) | 1.07 |  | https://www.facebook.com/PrinevilleDataCenter/app_399244020173259; http://www.facebook.com/note.php?note_id=10150148003778920 (1.07 at full Load)
| IT Load | 54.27 | MW | http://perspectives.mvdirona.com/2012/08/13/FunWithEnergyConsumptionData.aspx
| Average Server Power Draw (kW) | 0.3 | Average Estimate for all Installed Servers at Prineville, OR | http://perspectives.mvdirona.com/2012/08/13/FunWithEnergyConsumptionData.aspx
| Number of Servers | 169065.4206 | Average Estimate for all Installed Servers at Prineville, OR
| UPS Sizing (kW) | 56.6 | Design Backup Capability (scalable units installed - up to 75kW) | http://mvdirona.com/jrh/TalksAndPapers/Open_Compute_Project_Battery_Cabinet_v1.0.pdf
| Total UPS Load Requirement Estimate | 50719.6262 | No Factor of Safety | Calculated
| Total Number of UPS | 896 | No Factor of Safety | Calculated
| Annual Savings | 5362388.4459 |  | Calculated
| Annual Losses | 11564496.8944 |  | Calculated
| Annual Savings | 46.37% |  | Calculated
| Annual Savings Comparison | 30-55% | Energy Star UPS units can reduce UPS losses by 30-55% | https://www.energystar.gov/certified-products/detail/uninterruptible_power_supplies
| Technical Suitability | 0.25 | Engineering Judgement; Review of the Open Compute Project specifications shows a high degree of customization and attention to efficiency in concert with whole data center design. Efficiency ratings from the Open Compute Project specifications show >90% at 20% load, >94% at 50% load, and >91% at full load. Therefore, part load efficiencies are reportedly greater than Voltage and Frequency Independent (VFI) - Double Conversion UPS and under that of Voltage and Frequency Dependent (VFD) - Standby UPS and Voltage Independent (VI) - Interactive UPS units. Annual savings are based on the scaled design average for all units from UPS sizing of 56.6kW. With this knowledge 50% of the UPS load is assumed to be custom smaller, non-centralized UPS. Of the remaining 50%, there is a large degree of uncertainty of the technical suitability and thus a 50% of 50% = 25% assumption is applied. | http://mvdirona.com/jrh/TalksAndPapers/Open_Compute_Project_Battery_Cabinet_v1.0.pdf
| Total Incremental Cost | 1369267.2
Table 1: Ac-output UPS Loading Assumptions for Calculating Average Efficiency
| Rated Output Power, P, in watts (W) | Input Dependency Characteristic* | Proportion of Time Spent at Specified Proportion of Reference Test Load, tn%
|  |  | 25% | 50% | 75% | 100%
| P ≤ 1500 W | VFD | 0.2 | 0.2 | 0.3 | 0.3
|  | VI or VFI | 0 | 0.3 | 0.4 | 0.3
| 1500 W <P ≤ 10,000 W | VFD, VI, or VFI | 0 | 0.3 | 0.4 | 0.3
| P > 10,000 W | VFD, VI, or VFI | 0.25 | 0.5 | 0.25 | 0
| 2014, Energy Star, UPS Key Product Criteria (https://www.energystar.gov/index.cfm?c=uninterruptible_power_supplies.pr_crit_uninterruptible_power_supplies) |  | Load | Energy Star Weight (25% taken to weight 20% measurement) | Energy Star Weight (75% redistributed into 50 and 100% totals) | % Efficiency (Open Compute Specifications)
|  |  | 20% | 0.25 | 0.25 | 90%
|  |  | 50% | 0.5 | 0.625 | 94%
|  |  | 100% | 0 | 0.125 | 91%
|  |  |  | 0.75 | 1 | 93%
Rounded up as efficiencies are reportedly greater than measured
| Table 2: Ac-output UPS Minimum Average Efficiency Requirement |  |  |  |  | http://mvdirona.com/jrh/TalksAndPapers/Open_Compute_Project_Battery_Cabinet_v1.0.pdf
Minimum Average Efficiency Requirement (EffAVG_MIN), where:
P is the Rated Output Power in watts (W), and
ln is the natural logarithm.
| Rated Output Power | Input Dependency Characteristic
|  | VFD | VI | VFI
| P ≤ 1500 W | 0.967 |  | 0.0099 X ln (P) +0.815
| 1500 W <P ≤ 10,000 W | 0.97 | 0.967
| P > 10,000 W | 0.97 | 0.95 | 0.0099 X ln (P) +0.805
| Source: 2014, Energy Star, UPS Key Product Criteria (https://www.energystar.gov/index.cfm?c=uninterruptible_power_supplies.pr_crit_uninterruptible_power_supplies) |  |  | 0.91334
| Category | Annual Consumption Distribution (%) | Annual Consumption (kWh/year) | Modeled Building SQFT* | Implied Annual EUI (kWh/SQFT) | Implied Annual EUI (kWh/1000 SQFT) | Notes
| HVAC - Pumps and Chiller | 28.07% | 50803477.3292 | 334000 | 152.1062 | 152106.2195 | Square Footage Approximation for Facebook Prineville, OR. Consumption distribution from LBNL/ACEE and Emerson Studies.
| Lighting | 0.8873% | 1606180.1242 | 334000 | 4.8089 | 4808.9225
| Computer Loads | 52.17% | 94443391.3043 | 334000 | 282.7646 | 282764.6446
| UPS Losses | 6.389% | 11564496.8944 | 334000 | 34.6242 | 34624.2422
| Building Switchgear/MV transformer/other losses | 2.484% | 4497304.3478 | 334000 | 13.465 | 13464.9831
| HVAC - Air Movement | 10% | 18101650 | 334000 | 54.1966 | 54196.5569
| Total | 100% | 181016500 | 334000 | 541.9656 | 541965.5689
Source: Adapted from 2008, Emerson Network Power, Energy Logic: Reducing Data Center Energy Consumption by Creating Savings that Cascade Across Systems (https://www.cisco.com/web/partners/downloads/765/other/Energy_Logic_Reducing_Data_Center_Energy_Consumption.pdf) & 2003, ACEEE, Data Centers and Energy Use - Let's Look at the Data (http://hightech.lbl.gov/documents/data_centers/aceee162.pdf) * Based on Square Footage Approximation of 334,000 SQFT from 2013, Vault Data Solutions, The Vault Tax Benefits and Data Security Evaporative Cooling Load assumed to Take Full HVAC Load (Pumps + Chiller + HVAC Air Movement)
Source: 2000, Trane, “Chilled Water System Design and Operation”, CTV-SLB005-EN
| Chilled Water System | Consumption (%)
| Chiller | 58%
| Water Pumps | 26%
| Cooling Tower | 16% |  |  |  | http://mvdirona.com/jrh/TalksAndPapers/Open_Compute_Project_Battery_Cabinet_v1.0.pdf
Source: 2012, Energy Star, Understanding and Designing Energy-Efficiency Programs for Data Centers (http://www.energystar.gov/ia/products/power_mgt/ES_Data_Center_Utility_Guide.pdf)
Custom HVAC Data Center Cooling
Source: 2011, Open Compute Project, Facebook Data Center v1.0 Mechanical and Electrical Specifications
Source: 2013, Glumac, Data Center Efficiency Analysis Study Note: Per discussion with ETO, System Type 4 baseline cooling should be chillers with measure going to evaporative cooling
|  |  |  | End-Use | LBNL/ACEE | Emerson | Adjusted Emerson
% End-Use Consumption
|  |  |  | HVAC - Pumps and Chiller | 25% | 38.07% | 28.07%
|  |  |  | Lighting | 1% | 0.8873% | 0.8873%
|  |  |  | Computer Loads | 59% | 52.17% | 52.17%
|  |  |  | UPS Losses | 5% | 6.389% | 6.389%
|  |  |  | Building Switchgear/MV transformer/other losses |  | 2.484% | 2.484%
|  |  |  | HVAC - Air Movement | 10% |  | 10%
|  |  |  | Total | 100% | 100% | 100%
[5 empty] | 2003, ACEEE, Data Centers and Energy Use - Let's Look at the Data (http://hightech.lbl.gov/documents/data_centers/aceee162.pdf) | 2008, Emerson Network Power, Energy Logic: Reducing Data Center Energy Consumption by Creating Savings that Cascade Across Systems (https://www.cisco.com/web/partners/downloads/765/other/Energy_Logic_Reducing_Data_Center_Energy_Consumption.pdf)
Source: 2008, Emerson Network Power, Energy Logic: Reducing Data Center Energy Consumption by Creating Savings that Cascade Across Systems (https://www.cisco.com/web/partners/downloads/765/other/Energy_Logic_Reducing_Data_Center_Energy_Consumption.pdf)
| Category | Power Draw | % Distribution
| Computing | 588 | 52.17%
| Lighting | 10 | 0.8873%
| UPS and Distribution Losses | 72 | 6.389%
| Cooling power draw for computing and UPS losses | 429 | 38.07%
| Building Switchgear/MV transformer/other losses | 28 | 2.484%
| Total | 1127 | 100%
Source: 2003, ACEEE, Data Centers and Energy Use - Let's Look at the Data (http://hightech.lbl.gov/documents/data_centers/aceee162.pdf)
https://www.energystar.gov/index.cfm?c=power_mgt.datacenter_efficiency_purchasing
Data Center Load Forecast
| Year | Month | DC Forecast |  | Year | Base Annual Consumption (MWh) | Base Annual Consumption (kWh)
| 2013 | 1 | 17170 |  | 2013 | 246729 | 246729000
| 2013 | 2 | 17948 |  | 2014 | 362033 | 362033000 | Consumption here for 2 Enterprise data centers. 50% split assumption for consumption.
| 2013 | 3 | 18115 |  | 2015 | 436106 | 436106000
| 2013 | 4 | 18115 |  | 2016 | 466855 | 466855000
| 2013 | 5 | 19577 |  | 2017 | 544720 | 544720000
| 2013 | 6 | 18946 |  | 2018 | 544720 | 544720000
| 2013 | 7 | 20436 |  | 2019 | 544720 | 544720000
| 2013 | 8 | 21597 |  | 2020 | 544720 | 544720000
| 2013 | 9 | 22087 |  | 2021 | 544720 | 544720000
| 2013 | 10 | 23493 |  | 2022 | 544720 | 544720000
| 2013 | 11 | 23890 |  | 2023 | 544720 | 544720000
| 2013 | 12 | 25355 |  | 2024 | 544720 | 544720000
| 2014 | 1 | 26025 |  | 2025 | 544720 | 544720000
| 2014 | 2 | 24111 |  | 2026 | 544720 | 544720000
| 2014 | 3 | 26482 |  | 2027 | 544720 | 544720000
| 2014 | 4 | 27130 |  | 2028 | 544720 | 544720000
| 2014 | 5 | 28703 |  | 2029 | 544720 | 544720000
| 2014 | 6 | 28932 |  | 2030 | 544720 | 544720000
| 2014 | 7 | 31090 |  | 2031 | 544720 | 544720000
| 2014 | 8 | 32284 |  | 2032 | 544720 | 544720000
| 2014 | 9 | 32397 |  | 2033 | 544720 | 544720000
| 2014 | 10 | 34670
| 2014 | 11 | 34200
| 2014 | 12 | 36009
| 2015 | 1 | 36009
| 2015 | 2 | 32525
| 2015 | 3 | 34848
| 2015 | 4 | 34848
| 2015 | 5 | 36009
| 2015 | 6 | 35355
| 2015 | 7 | 37237
| 2015 | 8 | 37761
| 2015 | 9 | 36876
| 2015 | 10 | 38628
| 2015 | 11 | 37382
| 2015 | 12 | 38628
| 2016 | 1 | 38628
| 2016 | 2 | 34890
| 2016 | 3 | 37382
| 2016 | 4 | 37382
| 2016 | 5 | 38628
| 2016 | 6 | 37889
| 2016 | 7 | 39856
| 2016 | 8 | 40379
| 2016 | 9 | 39410
| 2016 | 10 | 41247
| 2016 | 11 | 39917
| 2016 | 12 | 41247
| 2017 | 1 | 41917
| 2017 | 2 | 39458
| 2017 | 3 | 41861
| 2017 | 4 | 42509
| 2017 | 5 | 44595
| 2017 | 6 | 44312
| 2017 | 7 | 46983
| 2017 | 8 | 47913
| 2017 | 9 | 47016
| 2017 | 10 | 49252
| 2017 | 11 | 48312
| 2017 | 12 | 50592
| 2018 | 1 | 41917
| 2018 | 2 | 39458
| 2018 | 3 | 41861
| 2018 | 4 | 42509
| 2018 | 5 | 44595
| 2018 | 6 | 44312
| 2018 | 7 | 46983
| 2018 | 8 | 47913
| 2018 | 9 | 47016
| 2018 | 10 | 49252
| 2018 | 11 | 48312
| 2018 | 12 | 50592
| 2019 | 1 | 41917
| 2019 | 2 | 39458
| 2019 | 3 | 41861
| 2019 | 4 | 42509
| 2019 | 5 | 44595
| 2019 | 6 | 44312
| 2019 | 7 | 46983
| 2019 | 8 | 47913
| 2019 | 9 | 47016
| 2019 | 10 | 49252
| 2019 | 11 | 48312
| 2019 | 12 | 50592
| 2020 | 1 | 41917
| 2020 | 2 | 39458
| 2020 | 3 | 41861
| 2020 | 4 | 42509
| 2020 | 5 | 44595
| 2020 | 6 | 44312
| 2020 | 7 | 46983
| 2020 | 8 | 47913
| 2020 | 9 | 47016
| 2020 | 10 | 49252
| 2020 | 11 | 48312
| 2020 | 12 | 50592
| 2021 | 1 | 41917
| 2021 | 2 | 39458
| 2021 | 3 | 41861
| 2021 | 4 | 42509
| 2021 | 5 | 44595
| 2021 | 6 | 44312
| 2021 | 7 | 46983
| 2021 | 8 | 47913
| 2021 | 9 | 47016
| 2021 | 10 | 49252
| 2021 | 11 | 48312
| 2021 | 12 | 50592
| 2022 | 1 | 41917
| 2022 | 2 | 39458
| 2022 | 3 | 41861
| 2022 | 4 | 42509
| 2022 | 5 | 44595
| 2022 | 6 | 44312
| 2022 | 7 | 46983
| 2022 | 8 | 47913
| 2022 | 9 | 47016
| 2022 | 10 | 49252
| 2022 | 11 | 48312
| 2022 | 12 | 50592
| 2023 | 1 | 41917
| 2023 | 2 | 39458
| 2023 | 3 | 41861
| 2023 | 4 | 42509
| 2023 | 5 | 44595
| 2023 | 6 | 44312
| 2023 | 7 | 46983
| 2023 | 8 | 47913
| 2023 | 9 | 47016
| 2023 | 10 | 49252
| 2023 | 11 | 48312
| 2023 | 12 | 50592
| 2024 | 1 | 41917
| 2024 | 2 | 39458
| 2024 | 3 | 41861
| 2024 | 4 | 42509
| 2024 | 5 | 44595
| 2024 | 6 | 44312
| 2024 | 7 | 46983
| 2024 | 8 | 47913
| 2024 | 9 | 47016
| 2024 | 10 | 49252
| 2024 | 11 | 48312
| 2024 | 12 | 50592
| 2025 | 1 | 41917
| 2025 | 2 | 39458
| 2025 | 3 | 41861
| 2025 | 4 | 42509
| 2025 | 5 | 44595
| 2025 | 6 | 44312
| 2025 | 7 | 46983
| 2025 | 8 | 47913
| 2025 | 9 | 47016
| 2025 | 10 | 49252
| 2025 | 11 | 48312
| 2025 | 12 | 50592
| 2026 | 1 | 41917
| 2026 | 2 | 39458
| 2026 | 3 | 41861
| 2026 | 4 | 42509
| 2026 | 5 | 44595
| 2026 | 6 | 44312
| 2026 | 7 | 46983
| 2026 | 8 | 47913
| 2026 | 9 | 47016
| 2026 | 10 | 49252
| 2026 | 11 | 48312
| 2026 | 12 | 50592
| 2027 | 1 | 41917
| 2027 | 2 | 39458
| 2027 | 3 | 41861
| 2027 | 4 | 42509
| 2027 | 5 | 44595
| 2027 | 6 | 44312
| 2027 | 7 | 46983
| 2027 | 8 | 47913
| 2027 | 9 | 47016
| 2027 | 10 | 49252
| 2027 | 11 | 48312
| 2027 | 12 | 50592
| 2028 | 1 | 41917
| 2028 | 2 | 39458
| 2028 | 3 | 41861
| 2028 | 4 | 42509
| 2028 | 5 | 44595
| 2028 | 6 | 44312
| 2028 | 7 | 46983
| 2028 | 8 | 47913
| 2028 | 9 | 47016
| 2028 | 10 | 49252
| 2028 | 11 | 48312
| 2028 | 12 | 50592
| 2029 | 1 | 41917
| 2029 | 2 | 39458
| 2029 | 3 | 41861
| 2029 | 4 | 42509
| 2029 | 5 | 44595
| 2029 | 6 | 44312
| 2029 | 7 | 46983
| 2029 | 8 | 47913
| 2029 | 9 | 47016
| 2029 | 10 | 49252
| 2029 | 11 | 48312
| 2029 | 12 | 50592
| 2030 | 1 | 41917
| 2030 | 2 | 39458
| 2030 | 3 | 41861
| 2030 | 4 | 42509
| 2030 | 5 | 44595
| 2030 | 6 | 44312
| 2030 | 7 | 46983
| 2030 | 8 | 47913
| 2030 | 9 | 47016
| 2030 | 10 | 49252
| 2030 | 11 | 48312
| 2030 | 12 | 50592
| 2031 | 1 | 41917
| 2031 | 2 | 39458
| 2031 | 3 | 41861
| 2031 | 4 | 42509
| 2031 | 5 | 44595
| 2031 | 6 | 44312
| 2031 | 7 | 46983
| 2031 | 8 | 47913
| 2031 | 9 | 47016
| 2031 | 10 | 49252
| 2031 | 11 | 48312
| 2031 | 12 | 50592
| 2032 | 1 | 41917
| 2032 | 2 | 39458
| 2032 | 3 | 41861
| 2032 | 4 | 42509
| 2032 | 5 | 44595
| 2032 | 6 | 44312
| 2032 | 7 | 46983
| 2032 | 8 | 47913
| 2032 | 9 | 47016
| 2032 | 10 | 49252
| 2032 | 11 | 48312
| 2032 | 12 | 50592
| 2033 | 1 | 41917
| 2033 | 2 | 39458
| 2033 | 3 | 41861
| 2033 | 4 | 42509
| 2033 | 5 | 44595
| 2033 | 6 | 44312
| 2033 | 7 | 46983
| 2033 | 8 | 47913
| 2033 | 9 | 47016
| 2033 | 10 | 49252
| 2033 | 11 | 48312
| 2033 | 12 | 50592
Source: 2014, ETO, Data Center Load Forecast for PAC

## ESTAR SERVERS
http://energy.gov/eere/femp/covered-product-category-enterprise-servers
| Measure # | Energy Efficiency Measure Name | Measure Group | Measure Lifetime (Maximum 70 yrs) | Annual Electricity Savings (kWh) | Total Incremental Cost of Measure | Total Incremental Cost of Measure per SQFT (Assuming 10000 SQFT) | Total Potential Incentive If Measure is Cost-effective | Combined Utility System BCR | Combined Societal BCR | kWh Levelized Cost | Simple Customer Payback w/ Incentive (years) | Source
| 1 | High Efficiency Custom Server | Server | 3 | 78 | 13 | 0.0013 | 4 | 3.6 | 1.3 | 0.02 | 1.4 | Source: 2014, ETO, Data Center Server Blessing Memo | Simple lvl Cost
|  | (Custom Project Example) | [11 empty] | 0.060058
| 2 | ENERGYSTAR v1.1 Server | Server | 3 | 565 | 45 | 0.0045 | 98 | 1.2 | 2.5 | 0.06 | -1.3 | Source: 2014, ETO, Data Center Server Blessing Memo | Simple lvl cost
|  | (savings from 80 PLUS) | [11 empty] | 0.0287
| Source: Adapted from 2013, ETO, Data Center Server Blessing Memo |  |  | Per 1000 SQFT | 0.565 | 0.045
| Metric | Value | Source
| Server Density (Servers/1000 SQFT) | 506.1839 | Calculated
| Enterprise Data Center Baseline Initial Saturation | 5% | Discussion with ETO for data center measures 02/26/2014 - very low baseline initial saturation for data centers, requirement for program
http://www.pge.com/includes/docs/pdfs/mybusiness/energysavingsrebates/incentivesbyindustry/DataCenters_BestPractices.pdf

## LOG
Item | Description | Who | When | Note
1 | Changed from Reto to NR approach | CG | 2015-02-22 | Better reflects nature of opportuntity and the potential over long run where growth is in the stock.
2 | Respond to comments make changes | CG | 2015-03-17 | Added costs for decomissionig, increased costs for lighting, check ES server market pen
3 | Updated High Low Forecast | CG | 2015-03-17
4
5
6
7
8
9
10
11
12