## 7PSourceSummary
Measure: | DCV Parking Garage
Item | Methods & Sources | 7P Updates
Measures Described | CO2-based demand control ventilation in parking garages.
Energy Savings Calculation Basis | Savings data from California Building efficiency standards. Savings are 0.925 kWh/sf, or 1.23 per design CFM
Applicable Stock | Share of Parking garage SF. Existing only (retrofit measure). Assume new SF covered by code
Baseline Saturation | TBD (currently 20%) - professional judgement
Baseline | Parking garage SF, constant fan ventilation
Permutations | None
Costs | From California data
Measure Life | 15 years
Savings Shape | C-All-HVAC-Vent-All-All-E
Achievability Ramp Rate | retro12med
File Version
V1 | Original version posted for review
v2 | Added forRPM tab and updated savings Shape
v3 | Added the High/Low forecast option

## forRPM
Ramp Rate | Resource Type | Measure Category | Sector | End Use | kW per unit | kWh per unit | TRC Net Levelized Cost (Net of All Benefits) | segment | measure | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | MAX | Savings Allocation by Category and Month for Segments 1 | [12 empty] | Savings Allocation by Category and Month for Segments 2
[5 empty] | Wholesale KW | Busbar Savings | lvlcost |  |  | aMW_2016 | aMW_2017 | aMW_2018 | aMW_2019 | aMW_2020 | aMW_2021 | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | MAX | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Retro12Med | Retro | DCV Parking Garage | Commercial | HVAC | 0.00018689 | 0.99419 | 40.1042 |  | DCV Parking Garage-Retro | 0.79198 | 0.7896 | 0.78723 | 0.78487 | 0.78252 | 0.70215 | 0.56004 | 0.44669 | 0.35628 | 0.28417 | 0.22665 | 0.18078 | 0.14419 | 0.115 | 0.091727 | 0.073162 | 0.00049752 | 0.00017715 | 6.0212e-05 | 1.9575e-05 | 7.1178 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 | 0 | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
Retro12Med | Retro | DCV Parking Garage | Commercial | HVAC | 0.00018689 | 0.99419 | 40.1042 |  | DCV Parking Garage-Retro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 | 0 | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
Retro12Med | Retro | DCV Parking Garage | Commercial | HVAC | 0.00018689 | 0.99419 | 40.1042 |  | DCV Parking Garage-Retro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 | 0 | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
Retro12Med | Retro | DCV Parking Garage | Commercial | HVAC | 0.00018689 | 0.99419 | 40.1042 |  | DCV Parking Garage-Retro | 0.050317 | 0.050085 | 0.049855 | 0.049625 | 0.049397 | 0.044253 | 0.035239 | 0.028062 | 0.022346 | 0.017795 | 0.01417 | 0.011284 | 0.0089858 | 0.0071555 | 0.0056981 | 0.0045375 | 3.0807e-05 | 1.0952e-05 | 3.7164e-06 | 1.2063e-06 | 0.44885 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 | 0 | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
Retro12Med | Retro | DCV Parking Garage | Commercial | HVAC | 0.00018689 | 0.99419 | 40.1042 |  | DCV Parking Garage-Retro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 | 0 | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
Retro12Med | Retro | DCV Parking Garage | Commercial | HVAC | 0.00018689 | 0.99419 | 40.1042 |  | DCV Parking Garage-Retro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 | 0 | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
Retro12Med | Retro | DCV Parking Garage | Commercial | HVAC | 0.00018689 | 0.99419 | 40.1042 |  | DCV Parking Garage-Retro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 | 0 | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
Retro12Med | Retro | DCV Parking Garage | Commercial | HVAC | 0.00018689 | 0.99419 | 40.1042 |  | DCV Parking Garage-Retro | 0.025775 | 0.025669 | 0.025564 | 0.025459 | 0.025355 | 0.022726 | 0.018106 | 0.014425 | 0.011493 | 0.0091567 | 0.0072954 | 0.0058124 | 0.0046308 | 0.0036895 | 0.0029395 | 0.0023419 | 1.5908e-05 | 5.6582e-06 | 1.921e-06 | 6.2386e-07 | 0.23046 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 | 0 | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
Retro12Med | Retro | DCV Parking Garage | Commercial | HVAC | 0.00018689 | 0.99419 | 40.1042 |  | DCV Parking Garage-Retro | 0.071894 | 0.0716 | 0.071306 | 0.071014 | 0.070722 | 0.063389 | 0.050503 | 0.040237 | 0.032058 | 0.025541 | 0.020349 | 0.016212 | 0.012917 | 0.010291 | 0.0081991 | 0.0065324 | 4.4373e-05 | 1.5783e-05 | 5.3584e-06 | 1.7401e-06 | 0.64283 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 | 0 | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
Retro12Med | Retro | DCV Parking Garage | Commercial | HVAC | 0.00018689 | 0.99419 | 40.1042 |  | DCV Parking Garage-Retro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 | 0 | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
Retro12Med | Retro | DCV Parking Garage | Commercial | HVAC | 0.00018689 | 0.99419 | 40.1042 |  | DCV Parking Garage-Retro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 | 0 | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
Retro12Med | Retro | DCV Parking Garage | Commercial | HVAC | 0.00018689 | 0.99419 | 40.1042 |  | DCV Parking Garage-Retro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 | 0 | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
Retro12Med | Retro | DCV Parking Garage | Commercial | HVAC | 0.00018689 | 0.99419 | 40.1042 |  | DCV Parking Garage-Retro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 | 0 | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
Retro12Med | Retro | DCV Parking Garage | Commercial | HVAC | 0.00018689 | 0.99419 | 40.1042 |  | DCV Parking Garage-Retro | 0.070966 | 0.070796 | 0.070626 | 0.070456 | 0.070287 | 0.063107 | 0.050364 | 0.040195 | 0.032079 | 0.025601 | 0.020432 | 0.016306 | 0.013014 | 0.010386 | 0.0082888 | 0.0066152 | 4.5012e-05 | 1.6037e-05 | 5.4541e-06 | 1.7742e-06 | 0.63959 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 | 0 | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
Retro12Med | Retro | DCV Parking Garage | Commercial | HVAC | 0.00018689 | 0.99419 | 40.1042 |  | DCV Parking Garage-Retro | 0.061816 | 0.061686 | 0.061557 | 0.061427 | 0.061298 | 0.055053 | 0.04395 | 0.035086 | 0.02801 | 0.022361 | 0.017851 | 0.014251 | 0.011377 | 0.0090823 | 0.0072505 | 0.0057883 | 3.9397e-05 | 1.4041e-05 | 4.7766e-06 | 1.5543e-06 | 0.5579 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 | 0 | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
Retro12Med | Retro | DCV Parking Garage | Commercial | HVAC | 0.00018689 | 0.99419 | 40.1042 |  | DCV Parking Garage-Retro | 0.020625 | 0.020576 | 0.020526 | 0.020477 | 0.020428 | 0.018341 | 0.014638 | 0.011682 | 0.0093231 | 0.0074406 | 0.0059382 | 0.0047392 | 0.0037822 | 0.0030185 | 0.002409 | 0.0019226 | 1.3082e-05 | 4.661e-06 | 1.5852e-06 | 5.1566e-07 | 0.18589 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 | 0 | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
Retro12Med | Retro | DCV Parking Garage | Commercial | HVAC | 0.00018689 | 0.99419 | 40.1042 |  | DCV Parking Garage-Retro | 0.10942 | 0.10893 | 0.10844 | 0.10795 | 0.10747 | 0.096287 | 0.076684 | 0.061072 | 0.048639 | 0.038736 | 0.03085 | 0.024569 | 0.019567 | 0.015584 | 0.012411 | 0.0098842 | 6.7115e-05 | 2.3862e-05 | 8.0983e-06 | 2.6289e-06 | 0.97659 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 | 0 | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
Retro12Med | Retro | DCV Parking Garage | Commercial | HVAC | 0.00018689 | 0.99419 | 40.1042 |  | DCV Parking Garage-Retro | 0.23893 | 0.23678 | 0.23465 | 0.23254 | 0.23045 | 0.20554 | 0.16295 | 0.12919 | 0.10242 | 0.081197 | 0.064373 | 0.051035 | 0.040461 | 0.032077 | 0.025431 | 0.020162 | 0.00013628 | 4.8233e-05 | 1.6295e-05 | 5.2658e-06 | 2.0884 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 | 0 | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
Note on A1: Charlie Grist: Lookup in ComMaster
Note on B1: Charlie Grist: New, NR, Retro
Note on C1: Charlie Grist: Measure Index Name
Note on E1: Charlie Grist: Use Massoud's Names
Note on F1: Charlie Grist: From Shaped Savings column 14
Note on G1: Charlie Grist: From SC or from Shaped Savings column 3.
Note on H1: Charlie Grist: From SC or from Shaped Savings column K (column 11)
Note on I1: Charlie Grist: From SC
Note on J1: Charlie Grist: From SC
Note on K1: Charlie Grist: From SC
Note on AF1: Charlie Grist: From Shaped Savings. Copy whole row down since column increment is hardwired into formula.

## SC-Retro
Units Methodology | Savings are based on data from a California Energy Efficiency Standards case. Applied to NW parking garages from CBSA. Assume retrofit only; new ones covered by code in WA and OR
| Vintage | Retro | Stock 2016
End-Use: | Measure Bundle | DCV Parking Garage-Retro | Region
HVAC | Report Year | 2035 | Base
| Total Potential (aMW) | 12.8883 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
UNITS FOR EXISTING STOCK |  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
|  |  |  | FLOOR_2016 | FLOOR_2017 | FLOOR_2018 | FLOOR_2019 | FLOOR_2020 | FLOOR_2021 | FLOOR_2022 | FLOOR_2023 | FLOOR_2024 | FLOOR_2025 | FLOOR_2026 | FLOOR_2027 | FLOOR_2028 | FLOOR_2029 | FLOOR_2030 | FLOOR_2031 | FLOOR_2032 | FLOOR_2033 | FLOOR_2034 | FLOOR_2035
| REG_Office | Large Off |  | 380.0883 | 378.948 | 377.8112 | 376.6777 | 375.5477 | 374.4211 | 373.2978 | 372.1779 | 371.0614 | 369.9482 | 368.8383 | 367.7318 | 366.6286 | 365.5288 | 364.4322 | 363.3389 | 362.2489 | 361.1621 | 360.0786 | 358.9984
| REG_Office | Medium Off |  | 190.7369 | 190.1647 | 189.5942 | 189.0254 | 188.4583 | 187.8929 | 187.3293 | 186.7673 | 186.207 | 185.6483 | 185.0914 | 184.5361 | 183.9825 | 183.4306 | 182.8803 | 182.3316 | 181.7846 | 181.2393 | 180.6956 | 180.1535
| REG_Office | Small Off |  | 184.0914 | 183.5391 | 182.9885 | 182.4395 | 181.8922 | 181.3465 | 180.8025 | 180.2601 | 179.7193 | 179.1801 | 178.6426 | 178.1067 | 177.5723 | 177.0396 | 176.5085 | 175.979 | 175.451 | 174.9247 | 174.3999 | 173.8767
| REG_Retail | XLarge Ret |  | 138.3573 | 137.7209 | 137.0874 | 136.4568 | 135.8291 | 135.2043 | 134.5823 | 133.9632 | 133.347 | 132.7336 | 132.123 | 131.5153 | 130.9103 | 130.3081 | 129.7087 | 129.112 | 128.5181 | 127.9269 | 127.3385 | 126.7527
| REG_Retail | Large Ret |  | 208.9575 | 207.9962 | 207.0395 | 206.0871 | 205.1391 | 204.1954 | 203.2561 | 202.3212 | 201.3905 | 200.4641 | 199.542 | 198.6241 | 197.7104 | 196.8009 | 195.8956 | 194.9945 | 194.0975 | 193.2047 | 192.316 | 191.4313
| REG_Retail | Medium Ret |  | 97.1157 | 96.669 | 96.2243 | 95.7816 | 95.3411 | 94.9025 | 94.4659 | 94.0314 | 93.5988 | 93.1683 | 92.7397 | 92.3131 | 91.8885 | 91.4658 | 91.045 | 90.6262 | 90.2094 | 89.7944 | 89.3813 | 88.9702
| REG_Retail | Small Ret |  | 109.4797 | 108.9761 | 108.4748 | 107.9758 | 107.4791 | 106.9847 | 106.4926 | 106.0027 | 105.5151 | 105.0297 | 104.5466 | 104.0657 | 103.587 | 103.1105 | 102.6362 | 102.164 | 101.6941 | 101.2263 | 100.7606 | 100.2971
| REG_K-12 | School K-12 |  | 241.1176 | 240.1291 | 239.1445 | 238.164 | 237.1876 | 236.2151 | 235.2466 | 234.2821 | 233.3215 | 232.3649 | 231.4122 | 230.4634 | 229.5185 | 228.5775 | 227.6403 | 226.707 | 225.7775 | 224.8518 | 223.9299 | 223.0118
| REG_University | University |  | 122.1534 | 121.6526 | 121.1538 | 120.6571 | 120.1624 | 119.6697 | 119.1791 | 118.6904 | 118.2038 | 117.7192 | 117.2365 | 116.7558 | 116.2771 | 115.8004 | 115.3256 | 114.8528 | 114.3819 | 113.9129 | 113.4459 | 112.9808
| REG_Warehouse | Warehouse |  | 448.6983 | 447.0381 | 445.3841 | 443.7362 | 442.0943 | 440.4586 | 438.8289 | 437.2052 | 435.5876 | 433.9759 | 432.3702 | 430.7704 | 429.1765 | 427.5886 | 426.0065 | 424.4303 | 422.8599 | 421.2953 | 419.7365 | 418.1835
| REG_Grocery | Supermarket |  | 53.7209 | 53.2375 | 52.7583 | 52.2835 | 51.8129 | 51.3466 | 50.8845 | 50.4265 | 49.9727 | 49.5229 | 49.0772 | 48.6355 | 48.1978 | 47.764 | 47.3342 | 46.9082 | 46.486 | 46.0676 | 45.653 | 45.2421
| REG_Grocery Other | MiniMart |  | 22.491 | 22.3849 | 22.2792 | 22.174 | 22.0694 | 21.9652 | 21.8615 | 21.7584 | 21.6557 | 21.5534 | 21.4517 | 21.3505 | 21.2497 | 21.1494 | 21.0496 | 20.9502 | 20.8513 | 20.7529 | 20.6549 | 20.5575
| REG_Restaurant | Restaurant |  | 51.5509 | 51.3075 | 51.0654 | 50.8243 | 50.5844 | 50.3457 | 50.1081 | 49.8715 | 49.6362 | 49.4019 | 49.1687 | 48.9366 | 48.7056 | 48.4757 | 48.2469 | 48.0192 | 47.7926 | 47.567 | 47.3425 | 47.119
| REG_Hotel | Lodging |  | 170.1519 | 169.7435 | 169.3361 | 168.9297 | 168.5243 | 168.1199 | 167.7164 | 167.3138 | 166.9123 | 166.5117 | 166.1121 | 165.7134 | 165.3157 | 164.9189 | 164.5231 | 164.1283 | 163.7344 | 163.3414 | 162.9494 | 162.5583
| REG_hospital | Hospital |  | 105.0295 | 104.8089 | 104.5888 | 104.3692 | 104.15 | 103.9313 | 103.713 | 103.4952 | 103.2779 | 103.061 | 102.8446 | 102.6286 | 102.4131 | 102.198 | 101.9834 | 101.7692 | 101.5555 | 101.3423 | 101.1294 | 100.9171
| REG_Hospital Other | Residential Care |  | 128.7482 | 128.4392 | 128.131 | 127.8234 | 127.5167 | 127.2106 | 126.9053 | 126.6008 | 126.2969 | 125.9938 | 125.6914 | 125.3898 | 125.0888 | 124.7886 | 124.4891 | 124.1903 | 123.8923 | 123.5949 | 123.2983 | 123.0024
| REG_Assembly | Assembly |  | 375.9022 | 374.2157 | 372.5367 | 370.8653 | 369.2013 | 367.5448 | 365.8958 | 364.2541 | 362.6198 | 360.9929 | 359.3732 | 357.7609 | 356.1557 | 354.5577 | 352.967 | 351.3833 | 349.8068 | 348.2373 | 346.6749 | 345.1195
| REG_Other | Other |  | 342.6499 | 339.566 | 336.5099 | 333.4814 | 330.48 | 327.5057 | 324.5581 | 321.6371 | 318.7424 | 315.8737 | 313.0308 | 310.2136 | 307.4216 | 304.6549 | 301.913 | 299.1957 | 296.503 | 293.8345 | 291.1899 | 288.5692
|  |  |  | 3371.0405 | 3356.5369 | 3342.1076 | 3327.752 | 3313.4699 | 3299.2606 | 3285.1238 | 3271.059 | 3257.0658 | 3243.1437 | 3229.2923 | 3215.5112 | 3201.7999 | 3188.1581 | 3174.5852 | 3161.0809 | 3147.6447 | 3134.2763 | 3120.9752 | 3107.7411
|  |  |  | 1 2016: Achievability; 2 2017: Retro12Med | 85%
CUMULATIVE MAX BASED ON APPL, TURN & ACHIEV |  | DCV Parking Garage-Retro | Saturation | 10.94% | 10.94% | 10.94% | 10.94% | 10.94% | 9.844% | 7.875% | 6.3% | 5.04% | 4.032% | 3.226% | 2.58% | 2.064% | 1.652% | 1.321% | 1.057% | 0.007209% | 0.002575% | 0.0008778% | 0.0002862% |  | 0.99689
| 24.69% | Large Off | 20% | 6.9783 | 6.9574 | 6.9365 | 6.9157 | 6.8949 | 6.1868 | 4.9346 | 3.9358 | 3.1392 | 2.5039 | 1.9971 | 1.5929 | 1.2705 | 1.0133 | 0.80823 | 0.64464 | 0.0043838 | 0.0015609 | 0.00053054 | 0.00017248 | 60.2617 | 62.9164
| 0% | Medium Off | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0% | Small Off | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.308% | XLarge Ret | 20% | 0.44335 | 0.44131 | 0.43928 | 0.43726 | 0.43525 | 0.38992 | 0.3105 | 0.24726 | 0.1969 | 0.15679 | 0.12486 | 0.099427 | 0.079176 | 0.063049 | 0.050207 | 0.039981 | 0.00027145 | 9.6499e-05 | 3.2746e-05 | 1.0629e-05 | 3.7135
| 0% | Large Ret | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0% | Medium Ret | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0% | Small Ret | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.266% | School K-12 | 20% | 0.22711 | 0.22618 | 0.22525 | 0.22433 | 0.22341 | 0.20024 | 0.15954 | 0.12711 | 0.10127 | 0.080682 | 0.064281 | 0.051214 | 0.040803 | 0.032509 | 0.0259 | 0.020635 | 0.00014017 | 4.9856e-05 | 1.6927e-05 | 5.4969e-06 | 1.9205
| 6.973% | University | 20% | 0.63348 | 0.63088 | 0.62829 | 0.62572 | 0.62315 | 0.55854 | 0.445 | 0.35454 | 0.28247 | 0.22505 | 0.1793 | 0.14285 | 0.11381 | 0.090677 | 0.072244 | 0.057558 | 0.00039098 | 0.00013906 | 4.7214e-05 | 1.5333e-05 | 5.3569
| 0% | Warehouse | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0% | Supermarket | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0% | MiniMart | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0% | Restaurant | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.941% | Lodging | 20% | 0.6253 | 0.6238 | 0.6223 | 0.62081 | 0.61932 | 0.55605 | 0.44377 | 0.35417 | 0.28265 | 0.22558 | 0.18003 | 0.14368 | 0.11467 | 0.091513 | 0.073035 | 0.058288 | 0.00039661 | 0.00014131 | 4.8057e-05 | 1.5633e-05 | 5.4619
| 6.973% | Hospital | 20% | 0.54467 | 0.54353 | 0.54239 | 0.54125 | 0.54011 | 0.48508 | 0.38725 | 0.30915 | 0.2468 | 0.19703 | 0.15729 | 0.12557 | 0.10024 | 0.080026 | 0.063886 | 0.051002 | 0.00034714 | 0.00012372 | 4.2088e-05 | 1.3696e-05 | 4.7849
| 1.898% | Residential Care | 20% | 0.18173 | 0.1813 | 0.18086 | 0.18043 | 0.18 | 0.16161 | 0.12898 | 0.10293 | 0.082148 | 0.065561 | 0.052323 | 0.041758 | 0.033326 | 0.026597 | 0.021226 | 0.01694 | 0.00011527 | 4.1069e-05 | 1.3967e-05 | 4.5436e-06 | 1.5874
| 3.448% | Assembly | 20% | 0.96411 | 0.95979 | 0.95548 | 0.95119 | 0.94693 | 0.84841 | 0.67568 | 0.53812 | 0.42857 | 0.34131 | 0.27183 | 0.21649 | 0.17241 | 0.13731 | 0.10936 | 0.087092 | 0.00059137 | 0.00021025 | 7.1356e-05 | 2.3164e-05 | 8.0929
| 8.261% | Other | 20% | 2.1053 | 2.0863 | 2.0676 | 2.049 | 2.0305 | 1.811 | 1.4358 | 1.1383 | 0.90243 | 0.71545 | 0.56721 | 0.44968 | 0.35651 | 0.28264 | 0.22408 | 0.17765 | 0.0012008 | 0.00042499 | 0.00014358 | 4.6398e-05 | 16.2105
|  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
Incremental SF |  |  |  | FLOOR_2016 | FLOOR_2017 | FLOOR_2018 | FLOOR_2019 | FLOOR_2020 | FLOOR_2021 | FLOOR_2022 | FLOOR_2023 | FLOOR_2024 | FLOOR_2025 | FLOOR_2026 | FLOOR_2027 | FLOOR_2028 | FLOOR_2029 | FLOOR_2030 | FLOOR_2031 | FLOOR_2032 | FLOOR_2033 | FLOOR_2034 | FLOOR_2035
|  | Large Off |  | 6.9783 | 6.9574 | 6.9365 | 6.9157 | 6.8949 | 6.1868 | 4.9346 | 3.9358 | 3.1392 | 2.5039 | 1.9971 | 1.5929 | 1.2705 | 1.0133 | 0.80823 | 0.64464 | 0.0043838 | 0.0015609 | 0.00053054 | 0.00017248
|  | Medium Off |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Small Off |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | XLarge Ret |  | 0.44335 | 0.44131 | 0.43928 | 0.43726 | 0.43525 | 0.38992 | 0.3105 | 0.24726 | 0.1969 | 0.15679 | 0.12486 | 0.099427 | 0.079176 | 0.063049 | 0.050207 | 0.039981 | 0.00027145 | 9.6499e-05 | 3.2746e-05 | 1.0629e-05
|  | Large Ret |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Medium Ret |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Small Ret |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | School K-12 |  | 0.22711 | 0.22618 | 0.22525 | 0.22433 | 0.22341 | 0.20024 | 0.15954 | 0.12711 | 0.10127 | 0.080682 | 0.064281 | 0.051214 | 0.040803 | 0.032509 | 0.0259 | 0.020635 | 0.00014017 | 4.9856e-05 | 1.6927e-05 | 5.4969e-06
|  | University |  | 0.63348 | 0.63088 | 0.62829 | 0.62572 | 0.62315 | 0.55854 | 0.445 | 0.35454 | 0.28247 | 0.22505 | 0.1793 | 0.14285 | 0.11381 | 0.090677 | 0.072244 | 0.057558 | 0.00039098 | 0.00013906 | 4.7214e-05 | 1.5333e-05
|  | Warehouse |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Supermarket |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | MiniMart |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Restaurant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Lodging |  | 0.6253 | 0.6238 | 0.6223 | 0.62081 | 0.61932 | 0.55605 | 0.44377 | 0.35417 | 0.28265 | 0.22558 | 0.18003 | 0.14368 | 0.11467 | 0.091513 | 0.073035 | 0.058288 | 0.00039661 | 0.00014131 | 4.8057e-05 | 1.5633e-05
|  | Hospital |  | 0.54467 | 0.54353 | 0.54239 | 0.54125 | 0.54011 | 0.48508 | 0.38725 | 0.30915 | 0.2468 | 0.19703 | 0.15729 | 0.12557 | 0.10024 | 0.080026 | 0.063886 | 0.051002 | 0.00034714 | 0.00012372 | 4.2088e-05 | 1.3696e-05
|  | Residential Care |  | 0.18173 | 0.1813 | 0.18086 | 0.18043 | 0.18 | 0.16161 | 0.12898 | 0.10293 | 0.082148 | 0.065561 | 0.052323 | 0.041758 | 0.033326 | 0.026597 | 0.021226 | 0.01694 | 0.00011527 | 4.1069e-05 | 1.3967e-05 | 4.5436e-06
|  | Assembly |  | 0.96411 | 0.95979 | 0.95548 | 0.95119 | 0.94693 | 0.84841 | 0.67568 | 0.53812 | 0.42857 | 0.34131 | 0.27183 | 0.21649 | 0.17241 | 0.13731 | 0.10936 | 0.087092 | 0.00059137 | 0.00021025 | 7.1356e-05 | 2.3164e-05
|  | Other |  | 2.1053 | 2.0863 | 2.0676 | 2.049 | 2.0305 | 1.811 | 1.4358 | 1.1383 | 0.90243 | 0.71545 | 0.56721 | 0.44968 | 0.35651 | 0.28264 | 0.22408 | 0.17765 | 0.0012008 | 0.00042499 | 0.00014358 | 4.6398e-05
SUPPLY CURVE SAVINGS BY BUNDLE | 35.5371 | DCV Parking Garage-Retro |  | 2016: aMW
|  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | MAX
Busbar Savings (kWh) - per sf of parking garage | lvlcost | segment | measure | aMW_2016 | aMW_2017 | aMW_2018 | aMW_2019 | aMW_2020 | aMW_2021 | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | MAX
0.99419 | 40.1042 | Large Off | DCV Parking Garage-Retro | 0.79198 | 0.7896 | 0.78723 | 0.78487 | 0.78252 | 0.70215 | 0.56004 | 0.44669 | 0.35628 | 0.28417 | 0.22665 | 0.18078 | 0.14419 | 0.115 | 0.091727 | 0.073162 | 0.00049752 | 0.00017715 | 6.0212e-05 | 1.9575e-05 | 7.1178 |  | 14.2356
0.99419 | 40.1042 | Medium Off | DCV Parking Garage-Retro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
0.99419 | 40.1042 | Small Off | DCV Parking Garage-Retro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.99419 | 40.1042 | XLarge Ret | DCV Parking Garage-Retro | 0.050317 | 0.050085 | 0.049855 | 0.049625 | 0.049397 | 0.044253 | 0.035239 | 0.028062 | 0.022346 | 0.017795 | 0.01417 | 0.011284 | 0.0089858 | 0.0071555 | 0.0056981 | 0.0045375 | 3.0807e-05 | 1.0952e-05 | 3.7164e-06 | 1.2063e-06 | 0.44885
0.99419 | 40.1042 | Large Ret | DCV Parking Garage-Retro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
0.99419 | 40.1042 | Medium Ret | DCV Parking Garage-Retro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.99419 | 40.1042 | Small Ret | DCV Parking Garage-Retro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.99419 | 40.1042 | School K-12 | DCV Parking Garage-Retro | 0.025775 | 0.025669 | 0.025564 | 0.025459 | 0.025355 | 0.022726 | 0.018106 | 0.014425 | 0.011493 | 0.0091567 | 0.0072954 | 0.0058124 | 0.0046308 | 0.0036895 | 0.0029395 | 0.0023419 | 1.5908e-05 | 5.6582e-06 | 1.921e-06 | 6.2386e-07 | 0.23046
0.99419 | 40.1042 | University | DCV Parking Garage-Retro | 0.071894 | 0.0716 | 0.071306 | 0.071014 | 0.070722 | 0.063389 | 0.050503 | 0.040237 | 0.032058 | 0.025541 | 0.020349 | 0.016212 | 0.012917 | 0.010291 | 0.0081991 | 0.0065324 | 4.4373e-05 | 1.5783e-05 | 5.3584e-06 | 1.7401e-06 | 0.64283
0.99419 | 40.1042 | Warehouse | DCV Parking Garage-Retro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.99419 | 40.1042 | Supermarket | DCV Parking Garage-Retro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.99419 | 40.1042 | MiniMart | DCV Parking Garage-Retro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.99419 | 40.1042 | Restaurant | DCV Parking Garage-Retro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.99419 | 40.1042 | Lodging | DCV Parking Garage-Retro | 0.070966 | 0.070796 | 0.070626 | 0.070456 | 0.070287 | 0.063107 | 0.050364 | 0.040195 | 0.032079 | 0.025601 | 0.020432 | 0.016306 | 0.013014 | 0.010386 | 0.0082888 | 0.0066152 | 4.5012e-05 | 1.6037e-05 | 5.4541e-06 | 1.7742e-06 | 0.63959
0.99419 | 40.1042 | Hospital | DCV Parking Garage-Retro | 0.061816 | 0.061686 | 0.061557 | 0.061427 | 0.061298 | 0.055053 | 0.04395 | 0.035086 | 0.02801 | 0.022361 | 0.017851 | 0.014251 | 0.011377 | 0.0090823 | 0.0072505 | 0.0057883 | 3.9397e-05 | 1.4041e-05 | 4.7766e-06 | 1.5543e-06 | 0.5579
0.99419 | 40.1042 | Residential Care | DCV Parking Garage-Retro | 0.020625 | 0.020576 | 0.020526 | 0.020477 | 0.020428 | 0.018341 | 0.014638 | 0.011682 | 0.0093231 | 0.0074406 | 0.0059382 | 0.0047392 | 0.0037822 | 0.0030185 | 0.002409 | 0.0019226 | 1.3082e-05 | 4.661e-06 | 1.5852e-06 | 5.1566e-07 | 0.18589
0.99419 | 40.1042 | Assembly | DCV Parking Garage-Retro | 0.10942 | 0.10893 | 0.10844 | 0.10795 | 0.10747 | 0.096287 | 0.076684 | 0.061072 | 0.048639 | 0.038736 | 0.03085 | 0.024569 | 0.019567 | 0.015584 | 0.012411 | 0.0098842 | 6.7115e-05 | 2.3862e-05 | 8.0983e-06 | 2.6289e-06 | 0.97659
0.99419 | 40.1042 | Other | DCV Parking Garage-Retro | 0.23893 | 0.23678 | 0.23465 | 0.23254 | 0.23045 | 0.20554 | 0.16295 | 0.12919 | 0.10242 | 0.081197 | 0.064373 | 0.051035 | 0.040461 | 0.032077 | 0.025431 | 0.020162 | 0.00013628 | 4.8233e-05 | 1.6295e-05 | 5.2658e-06 | 2.0884
[24 empty] | 12.8883 |  | 14.2356
RECOMBINE MEASURE BUNDLES INTO SUPPLY CURVE CUMULATIVE
|  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | Max
|  | lvlcost | lvlcost | aMW_2016 | aMW_2017 | aMW_2018 | aMW_2019 | aMW_2020 | aMW_2021 | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | max
| Block 1: <= 0 mills/kWh | >=-9999 | <=0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 2: <= 10 mills/kWh | >0 | <=10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 3: 10-20 mills/kWh | >10 | <=20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 4: 20-30 mills/kWh | >20 | <=30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 5: 30-40 mills/kWh | >30 | <=40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 6: 40-50 mills/kWh | >40 | <=50 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 7: 50-60 mills/kWh | >50 | <=60 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 8: 60-70 mills/kWh | >60 | <=70 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 9: 70-80 mills/kWh | >70 | <=80 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 10: 80-90 mills/kWh | >80 | <=90 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 11: 90-100 mills/kWh | >90 | <=100 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 12: 100-110 mills/kWh | >100 | <=110 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 13: 110-120 mills/kWh | >110 | <=120 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 14: 120-130 mills/kWh | >120 | <=130 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 15: 130-140 mills/kWh | >130 | <=140 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 16: 140-150 mills/kWh | >140 | <=150 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 17: 150-160 mills/kWh | >150 | <=160 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 18: 160-170 mills/kWh | >160 | <=170 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 19: 170-180 mills/kWh | >170 | <=180 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 20: 180-190 mills/kWh | >180 | <=190 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 21: 190-200 mills/kWh | >190 | <=200 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 22: 200-210 mills/kWh | >200 | <=210 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 23: 210-220 mills/kWh | >210 | <=220 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 24: 220-230 mills/kWh | >220 | <=230 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 25: 230-240 mills/kWh | >230 | <=240 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 26: 240-250 mills/kWh | >240 | <=250 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 27: 250-260 mills/kWh | >250 | <=260 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 28: 260-270 mills/kWh | >260 | <=270 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 29: 270-280 mills/kWh | >270 | <=280 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 30: 280-290 mills/kWh | >280 | <=290 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 31: 290-300 mills/kWh | >290 | <=300 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
| Block 32: >300 mills/kWh | >300 | <=999 | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
|  |  |  | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
RECOMBINE MEASURE BUNDLES INTO SUPPLY CURVE INCREMENTAL
|  |  | DCV Parking Garage-Retro | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | Max
|  |  |  | aMW_2016 | aMW_2017 | aMW_2018 | aMW_2019 | aMW_2020 | aMW_2021 | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | aMW_
|  | Block 1: <= 0 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 2: <= 10 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 3: 10-20 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 4: 20-30 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 5: 30-40 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 6: 40-50 mills/kWh |  | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05 | 12.8883
|  | Block 7: 50-60 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 8: 60-70 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 9: 70-80 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 10: 80-90 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 11: 90-100 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 12: 100-110 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 13: 110-120 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 14: 120-130 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 15: 130-140 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 16: 140-150 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 17: 150-160 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 18: 160-170 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 19: 170-180 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 20: 180-190 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 21: 190-200 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 22: 200-210 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 23: 210-220 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 24: 220-230 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 25: 230-240 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 26: 240-250 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 27: 250-260 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 28: 260-270 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 29: 270-280 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 30: 280-290 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 31: 290-300 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 32: >300 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total per Year |  | 1.4417 | 1.4357 | 1.4298 | 1.4238 | 1.4179 | 1.2708 | 1.0125 | 0.80663 | 0.64264 | 0.51199 | 0.40791 | 0.32499 | 0.25892 | 0.20629 | 0.16435 | 0.13095 | 0.0008895 | 0.00031638 | 0.00010742 | 3.4885e-05
|  | Total Cumulative |  | 1.4417 | 2.8774 | 4.3072 | 5.731 | 7.1489 | 8.4198 | 9.4323 | 10.2389 | 10.8815 | 11.3935 | 11.8014 | 12.1264 | 12.3853 | 12.5916 | 12.756 | 12.8869 | 12.8878 | 12.8881 | 12.8882 | 12.8883 | 12.8883

## Measure InputOutput_Out
Shaped Savings Results; By Category and sorted by TRC BC ratio
[14 empty] | Savings Allocation by Category and Month for Segments 1 | [11 empty] | Savings Allocation by Category and Month for Segments 2
Category | Measure | Busbar Savings | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Wholesale KW | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
DCV Parking Garage-Retro |  | 0.99419 | 0.39282 | 0.078563 | 0.47138 | 0.68607 | 0.66164 | 4153.4462 | 14.3364 | 40.1042 | 0.9644 | 0.0094449 | 0.00018689 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649

## Measure InputOutput
Data Set Name
Measure Index Name | DCV Parking Garage
Costs must be denominated in the same year as 'Input Cost Reference Year' = |  | 2012
Results were run through ProCost and pasted below
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105
Input Data | [7 empty] | Periodic Replacement Costs and Savings and Replacement Period | [5 empty] | Gas Inputs |  | Retro or LO | Early Retrofit Parameters
Category Name | Measure Name | Savings (kwh/yr) | Life (yrs) | Capital Cost | Annual O&M | Shape Pointer | Non-E Val ($/yr) | Cost 1 ($) | Period 1 | Cost 2 ($) | Period 2 | Cost 3 ($) | Period 3 | Savings (therms/yr) | Shape Pointer | R or L | Savings 2 (kWh) | Remaining Life (yrs) | Salvage Value ($)
DCV Parking Garage-Retro | DCV Parking Garage-Retro | 0.925 | 15 | 0.39282 |  | C-All-HVAC-Vent-All-All-E |  | 0.05925 | 5 | [6 empty] | R
ProCost Results
Version: | ProCost 3.0 - Beta04
Run Time: | Thursday, 19 March , 2015 at 9:17 AM
Regurgitation of ProData input parameters which were used for this run
| Run Parameters |  | Run Parameters |  |  | Marginal Cost & Conservation Load Shape Parameters | [9 empty] | Sponsor Parameters | [5 empty] | Program Parameters |  |  | Utility System Parameters
| Run Type | Electric | Run Type | Electric |  | Marginal Costs and Savings Shape File | Q:\SeventhPlan\Conservation Analysis\Global EE Inputs\MC Files\MC_AND_LOADSHAPE_v3.0_24segment-7P-D9 - NewSegValues.xlsx |  |  | 6P MidC Final (with carbon) | [6 empty] | Customer | Wholesale Elec | Retail Elec | Nat Gas |  | Program Life (yrs) | 20 |  |  | Electric | Gas
| Negative B/C Ratios | Off | Negative B/C Ratios | Off |  | Marginal Elec Avoided Cost Input Worksheet | 7P Mid |  |  | Conservation Load Shapes | [5 empty] | Real After-Tax Cost of Capital | 0.068013 | 0.043878 | 0.053289 | 0.054479 |  | Program Start Date | 2016 |  | Bulk System T&D Loss Factor | 0.0040389 | 0.01
| Admin Cost @ Category Level | On | Admin Cost @ Category Level | On |  | Elec Savings Shape Input Worksheet | GLSShapes |  |  | 6P_Gas_Final | [5 empty] | Financial Life (years) | 12 | 12 | 1 | 1 |  | Present Value Time Zero | 2016 |  | Bulk System T&D Credit ($/kw-yr)($/dailytherm-yr) | 26 | 0
| Repeat Periodic Replacement | On | Repeat Periodic Replacement | On |  | Marginal Gas Avoided Cost Input Worksheet | 7P Gas |  |  | Conservation Load Shapes | [6 empty] | Customer | Wholesale Elec | Retail Elec | Nat Gas |  | Input Cost Reference Year | 2012 |  | Bulk System T&D I2R Loss Component (%) | 0.9 | N/A
[6 empty] | Gas Savings Shape Input Worksheet | GLSShapes | [8 empty] | Sponsor Share of Initial Capital Cost | 0.35 | 0.195 | 0.455 | 0 |  | Real Discount Rate | 0.04 |  | Local System Dist Loss Factor | 0.047399 | 0
| Run Type: | Electric |  |  |  | Marginal Elec CO2 per kWh Input Worksheet | CO2 lbs per kWh .95 |  |  | CO2 lbs per therm | [5 empty] | Sponsor Share of Annual O&M | 1 | 0 | 0 | 0 |  | Capital Real Escalation Rate | 0 |  | Local System Dist Credit ($/kw-yr)($/dailytherm-yr) | 31 | 0
| Negative B/C Ratios: | False: (Converts Negative B/C Ratios) |  |  |  | Marginal Gas CO2 per therm Input Worksheet | CO2 lbs per therm |  |  | Zero Dollars per ton CO2 | [5 empty] | Sponsor Share of Periodic Replacement Cost | 1 | 0 | 0 | 0 |  | Admin Cost (as % of Initial Capital Cost) | 0.2 |  | Local System Dist I2R Loss Component (%) | 0.7 | N/A
| Admin Cost / Category Level: | True: Admin Costs added at Category Results |  |  |  | Marginal Avoided Cost CO2 Input Worksheet | Zero Dollars per ton CO2 |  |  | LineLossShapes | [5 empty] | Sponsor Share of Admin Cost |  | 0.3 | 0.7 | 0 |  | Regional Act Conservation Credit (%) | 0 |  | Risk-Mitigation Credit (mills/kWh)(mills/therm) - Retro. | 0 | 0
| Periodic O&M Treatment: | True: (Periodic O&M Repeats over measure life) |  |  |  | Line Loss Shape Input Worksheet | LineLossShapes | [8 empty] | Last Year of Non-Customer O&M & Period Replacement |  | 20 |  |  |  | Report Annual Carbon Saved for Year | 2018 |  | Risk-Mitigation Credit (mills/kWh)(mills/therm) - Lost Op. | 0 | 0
Measure Results; Sorted in same order as input
Total Results |  | Measure Input Data | [8 empty] | Savings | [5 empty] | PV Capital |  |  |  | PV Admin |  |  |  | PV O&M |  |  |  | PV Periodic Repl. |  |  |  | Total PV Capital, O&M and Periodic Repl Costs |  |  |  |  | PV Wholesale Electric Utility Costs & Benefits | [6 empty] | PV Retail Electric Utility Costs & Benefits | [6 empty] | PV Electric Utility System Costs & Benefits | [5 empty] | Electric Utility System Economics |  | Sponsor Levelized Cost (mills/kwh) |  |  |  |  | PV Regional Costs & Benefits | [15 empty] | TRC Economics |  | Physical CO2 | [6 empty] | Gas Inputs |  |  |  | PV Gas Utility System Costs & Benefits |  |  |  |  | Gas Utility System Economics
Category | Measure | Measure Life | Site Savings (kWh) | Site Savings (therms) | Capital Cost ($/unit) | Annual O&M Cost ($/unit) | PV Per. Repl. Cost ($/unit) | Load Shape (electric) | Diversified Load Factor (electric) | Wholesale Power Coincidence Factor (electric) | Wholesale Electric Energy (kWh) | Wholesale Electric Demand (kw) | Retail Electric Demand (kW) | Wholesale Gas Energy (therms/yr) | Wholesale Gas Demand (therms/day) | Retail Gas Demand (therms/day) | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Total | Wholesale Utility System Energy | Wholesale Utility System T&D Def. Cap. | Wholesale Utility System Act C-E Credit | Wholesale Utility System Risk Mitigation Benefit | Wholesale Utility System Total System Benefit | Wholesale Utility System Total Non-Consumer Cost | Wholesale Utility System B/C Ratio | Retail Utility System Energy | Retail Utility System T&D Def. Cap. | Retail Utility System Act C-E Credit | Retail Utility System Risk Mitigation Benefit | Retail Utility System Total System Benefit | Retail Utility System Total Non-Consumer Cost | Retail Utility System System B/C Ratio | Utility System Energy | Utility System T&D Def. Cap. | Utility System Act C-E Credit | Utility System Total Risk Mitigation Benefit | Utility System Total System Benefit | Utility System Total Non-Consumer Cost | Utility System Net Levelized Cost (Net of Elec T&D Capacity Benefits, Act Credit & Risk-Mitigation Benefit) in mills/kwh | Utility System System B/C Ratio | Wholesale Electric Levelized Cost | Retail Electric Levelized Cost | Natural Gas Levelized Cost | Customer Levelized Cost | Total Levelized Cost | PV Regional Electric Energy | PV Regional Gas Energy | PV Regional Electric T&D Def. Cap. | PV Regional Gas T&D Def. Cap. | PV Regional Electric System CO2 | PV Regional Gas System CO2 | PV Regional Electric System Risk-Mitigation Benefit | PV Regional Gas System Risk-Mitigation Benefit | PV Regional Non-E Value | PV Regional Act Credit | PV Regional Capital Cost | PV Regional Admin Cost | PV Regional Annual O&M Cost | PV Regional Periodic Replacement Cost | PV Total Regional Benefit | PV Total Regional Cost | TRC B/C Ratio | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | Electric System CO2 Avoided (Lifetime Tons) | Gas System CO2 Avoided (Lifetime Tons) | Total System CO2 Avoided (Lifetime Tons) | Electric System CO2 Avoided (Annual Tons in 2018) | Gas System CO2 Avoided (Annual Tons in 2018) | Total System CO2 Avoided (Annual Tons in 2018) |  | Gas Site Savings (therms) | Load Shape (gas) | Diversitfied Load Factor (gas) | Wholesale Coincidence Factor (gas) | Total Gas Utility System Energy | Gas Utility System T&D Def. Cap. | Gas Utility System Risk Mitigation Benefit | Gas Utility System Total System Benefit | Gas Utility System Total Non-Consumer Cost | Gas Utility System Net Levelized Cost (Net of Gas T&D Capacity Benefits & Risk-Mitigation Benefits) in cents/therm | Gas Utility System System B/C Ratio
DCV Parking Garage-Retro | DCV Parking Garage-Retro | 15 | 0.925 | 0 | 0.39282 | 0 | 0.085314 | C-All-HVAC-Vent-All-All-E |  |  | 0.99419 | 0.00018689 | 0.00018554 | 0 | 0 | 0 | 0.078333 | 0.18102 | 0 | 0.26284 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085314 | 0.078333 | 0.18102 | 0 | 0.34816 | 0.6075 | 0.51743 | 0.066038 | 0 | 0 | 0.58347 | 0.078333 | 7.4486 | 0.51743 | 0.07817 | 0 | 0 | 0.5956 | 0.18102 | 3.2903 | 0.51743 | 0.14421 | 0 | 0 | 0.66164 | 0.25935 | 8.5218 | 2.5512 | 5.7976 | 13.3974 | 0 | 25.7677 | 44.9627 | 0.51743 | 0 | 0.14421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52219 |  | 0 | 0.085314 | 0.66164 | 0.6075 | 1.0891 | 34.2895 | 0.0094449 | 0 | 0.0094449 | 0.00047224 | 0 | 0.00047224 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Category Results; Sorted by TRC Levelized Cost
Total Results |  | Measure Input Data | [8 empty] | Savings | [5 empty] | PV Capital |  |  |  | PV Admin |  |  |  | PV O&M |  |  |  | PV Periodic Repl. |  |  |  | Total PV Capital, O&M and Periodic Repl Costs |  |  |  |  | PV Wholesale Electric Utility Costs & Benefits | [6 empty] | PV Retail Electric Utility Costs & Benefits | [6 empty] | PV Electric Utility System Costs & Benefits | [5 empty] | Electric Utility System Economics |  | Sponsor Levelized Cost (mills/kwh) |  |  |  |  | PV Regional Costs & Benefits | [15 empty] | TRC Economics |  | Physical CO2 | [6 empty] | Gas Inputs |  |  |  | PV Gas Utility System Costs & Benefits |  |  |  |  | Gas Utility System Economics
Category | Measure | Measure Life | Site Savings (kWh) | Site Savings (therms) | Capital Cost ($/unit) | Annual O&M Cost ($/unit) | PV Per. Repl. Cost ($/unit) | Load Shape (electric) | Diversified Load Factor (electric) | Wholesale Power Coincidence Factor (electric) | Wholesale Electric Energy (kWh) | Wholesale Electric Demand (kw) | Retail Electric Demand (kW) | Wholesale Gas Energy (therms/yr) | Wholesale Gas Demand (therms/day) | Retail Gas Demand (therms/day) | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Total | Wholesale Utility System Energy | Wholesale Utility System T&D Def. Cap. | Wholesale Utility System Act C-E Credit | Wholesale Utility System Risk Mitigation Benefit | Wholesale Utility System Total System Benefit | Wholesale Utility System Total Non-Consumer Cost | Wholesale Utility System B/C Ratio | Retail Utility System Energy | Retail Utility System T&D Def. Cap. | Retail Utility System Act C-E Credit | Retail Utility System Risk Mitigation Benefit | Retail Utility System Total System Benefit | Retail Utility System Total Non-Consumer Cost | Retail Utility System System B/C Ratio | Utility System Energy | Utility System T&D Def. Cap. | Utility System Act C-E Credit | Utility System Total Risk Mitigation Benefit | Utility System Total System Benefit | Utility System Total Non-Consumer Cost | Utility System Net Levelized Cost (Net of Elec T&D Capacity Benefits, Act Credit & Risk-Mitigation Benefit) in mills/kwh | Utility System System B/C Ratio | Wholesale Electric Levelized Cost | Retail Electric Levelized Cost | Natural Gas Levelized Cost | Customer Levelized Cost | Total Levelized Cost | PV Regional Electric Energy | PV Regional Gas Energy | PV Regional Electric T&D Def. Cap. | PV Regional Gas T&D Def. Cap. | PV Regional Electric System CO2 | PV Regional Gas System CO2 | PV Regional Electric System Risk-Mitigation Benefit | PV Regional Gas System Risk-Mitigation Benefit | PV Regional Non-E Value | PV Regional Act Credit | PV Regional Capital Cost | PV Regional Admin Cost | PV Regional Annual O&M Cost | PV Regional Periodic Replacement Cost | PV Total Regional Benefit | PV Total Regional Cost | TRC B/C Ratio | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | Electric System CO2 Avoided (Lifetime Tons) | Gas System CO2 Avoided (Lifetime Tons) | Total System CO2 Avoided (Lifetime Tons) | Electric System CO2 Avoided (Annual Tons in 2018) | Gas System CO2 Avoided (Annual Tons in 2018) | Total System CO2 Avoided (Annual Tons in 2018) |  | Gas Site Savings (therms) | Load Shape (gas) | Diversitfied Load Factor (gas) | Wholesale Coincidence Factor (gas) | Total Gas Utility System Energy | Gas Utility System T&D Def. Cap. | Gas Utility System Risk Mitigation Benefit | Gas Utility System Total System Benefit | Gas Utility System Total Non-Consumer Cost | Gas Utility System Net Levelized Cost (Net of Gas T&D Capacity Benefits & Risk-Mitigation Benefits) in cents/therm | Gas Utility System System B/C Ratio
DCV Parking Garage-Retro |  | 15 | 0.925 | 0 | 0.39282 | 0 | 0.085314 |  |  |  | 0.99419 | 0.00018689 | 0.00018554 | 0 | 0 | 0 | 0.078333 | 0.18102 | 0 | 0.26284 | 0.023569 | 0.054994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085314 | 0.1019 | 0.23601 | 0 | 0.34816 | 0.68607 | 0.51743 | 0.066038 | 0 | 0 | 0.58347 | 0.1019 | 5.7258 | 0.51743 | 0.07817 | 0 | 0 | 0.5956 | 0.23601 | 2.5236 | 0.51743 | 0.14421 | 0 | 0 | 0.66164 | 0.33791 | 14.3364 | 1.958 | 7.542 | 17.4676 | 0 | 25.7677 | 50.7773 | 0.51743 | 0 | 0.14421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52219 | 0.078563 | 0 | 0.085314 | 0.66164 | 0.68607 | 0.9644 | 40.1042 | 0.0094449 | 0 | 0.0094449 | 0.00047224 | 0 | 0.00047224 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Supply Curve Results; Categories sorted by TRC Net Levelized Cost
Totals for Categories with Benefits Exceeding Costs. Levelized cost is TRC Net Levelized Cost (Net of Benefits) | [12 empty] | Savings Allocation by Cost Bin and Month for Segments 1 | [12 empty] | Savings Allocation by Cost Bin and Month for Segments 2
| Totals Basis | Busbar Electric Savings in kWh | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Measures with B/C > 1.00 | 0.99419 | 0.39282 | 0 | 0.39282 | 0.6075 | 0.66164 | 3461.2052 | 8.5218 | 34.2895 | 1.0891 | 0.0094449 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 |  | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
| Categories with B/C > 1.00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Supply Curve Results: By TRC Net Levelized Cost - Net of Benefits
| Block 1: <= 0 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 2: <= 10 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 3: 10-20 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 4: 20-30 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 5: 30-40 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 6: 40-50 mills/kWh | 0.99419 | 0.39282 | 0.078563 | 0.47138 | 0.68607 | 0.66164 | 4153.4462 | 14.3364 | 40.1042 | 0.9644 | 0.0094449 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 |  | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
| Block 7: 50-60 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 8: 60-70 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 9: 70-80 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 10: 80-90 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 11: 90-100 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 12: 100-110 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 13: 110-120 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 14: 120-130 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 15: 130-140 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 16: 140-150 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 17: 150-160 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 18: 160-170 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 19: 170-180 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 20: 180-190 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 21: 190-200 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 22: > 200 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Shaped Savings Results; By Category and sorted by TRC BC ratio
[13 empty] | Savings Allocation by Cost Bin and Month for Segments 1 Feb: Savings Allocation by Category and Month for Segments 1 |  |  | Savings Allocation by Category and Month for Segments 2
Category | Measure | Busbar Savings | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Wholesale KW | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
DCV Parking Garage-Retro |  | 0.99419 | 0.39282 | 0.078563 | 0.47138 | 0.68607 | 0.66164 | 4153.4462 | 14.3364 | 40.1042 | 0.9644 | 0.0094449 | 0.00018689 | 0.062341 | 0.056054 | 0.064504 | 0.060009 | 0.061266 | 0.060645 | 0.057614 | 0.060032 | 0.056089 | 0.063952 | 0.056594 | 0.061616 |  | 0.026467 | 0.02274 | 0.021812 | 0.022776 | 0.022346 | 0.019608 | 0.023022 | 0.018881 | 0.023244 | 0.020877 | 0.025048 | 0.026649
Note on I6: :ProCost Perioodic replacement costs and savinsg of the measure. These are costs and savings that occur periodicially, but at different periods than annually. Can be positive or negative. Periodic replacement costs for both the measure and the baseline measure should be included if applicable. ProCost can analysze these costs in two ways dependent on the 'Repeat Periodic Replacemetn' switch in the ProData page. When set to 'On', ProCost repeats replacement costs for multiple times over the life of a measure depending on the input period and measure life. For example fluorescent lamps may have a 4-year replacement cycle that repeats 3 times in a 15-year measure life. When set to 'Off', ProCost reads the period as the year after installation that the replacement cost occurs and does not subsequently reinstall or repeat the replacement costs. For example a compressor may be replaced only once in the life of a heat-pump system. Example: A new fluorescent lighting systems may have a measure life of 15 years, and a lamp life of five years. Two lamps lamps per fixture must be replaced at years 6 and 11. Lamp and labor costs, expressed as positive costs, are entered as a cost and the period would be enetered as 5. The baseline measure may have a four year lamp life and would have required a three-lamp replacement at years 5, 9 and 13. Lamp and labor replacement costs would be entered as annual savings in dollars with a 4-year period. ProCost determines the net present value of the two cost streams.
Note on O6: :ProCost If the measure has gas savings for incfreases, enter the annual savings and shape of the savings here. Example: Clothes washer saves electric motor and dryer energy and gas water heat.
Note on A7: :Procost Category for the measure. Individual measures can be grouped into categories. Procost output is reported by measure and by category. All measures must belong to at least one category. Category name can be the same as measure name. Example: Measures can be combined into one category if they have components with different load shapes or measure lives. On wash machines there may be one load shape for the electric motor savings component, a second load shape for the electric water heat savings component and a third shape for electric dryer savings component.
Note on B7: :ProCost Name of Measure. User-defined. For PTR measures, defined naming conventions apply.
Note on C7: :ProCost Annual electric savings for the measure in kWh at the site. May be positive, negative or zero. Savings are incremental to the baseline alternative.
Note on D7: :ProCost Physical life of the measure in years. Must be >=1.
Note on E7: :ProCost Initial cost to install the measure in dollars. Costs are incremental to the baseline alternative. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on F7: :ProCost Annaul opperations and maintenace cost for the measure in dollars. Must be incremental cost over the baseline alternative. May be positive, negative or zero. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page. O&M costs are enetered as positive values. Negative values represent O&M savings compared to the baseline alternative. Example: Annualized maintenace cost for a heat pump heating system compared to a baseline electric resistance heating system.
Note on G7: :ProCost Name of the pointer to the shape of the savings. The shapes represent the daily and monthly shape of the savings in four time segments for each month of the year. Shape of the savings is relative to the baseline alternative. These shaps are in the MC_AND_Loadshape file.
Note on H7: :ProCost Annual value of any non-energy benefits of the measure, relative to the baseline alternative. Expressed in dollars per year and denominated in dollars of the 'Cost Reference Year'. Positive value represents dollar savings. Negative value represents dollar cost. Example: Water, detergent and sewer savings from efficient clothes washer.
Note on I7: : Cost in dollars that is incurred for Period 1. Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on J7: :ProCost Duration of Period1. The time at which Period 1 costs, or savings, occur. In years.
Note on K7: : Cost in dollars that is incurred for Period 2 Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on L7: :ProCost Duration of Period 2. The time at which Period 2 costs, or savings, occur. In years.
Note on M7: : Cost in dollars that is incurred for Period 3. Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on N7: :ProCost Duration of Period 3. The time at which Period 3 costs, or savings, occur. In years.
Note on O7: : Annual gas savings, or increases, in therms.
Note on P7: :ProCost Name of the pointer to the shape of the savings. The shapes represent the daily and monthly shape of the savings in four time segments for each month of the year. Shape of the savings is relative to the baseline alternative. These shaps are in the MC_AND_Loadshape file.
Note on BH35: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BM35: Direct and program administrative costs of the measure to sponsor. Separate costs for each sponsor. Depends on share of costs incurred by sponsor, sponsor cost of capital, and financing term which are user-defined inputs. Includes applicable Capital, O&M, Periodic Replacement and Program Administrative costs. Sponsor costs are levelized over program life. Does not include any adjustments for benefit. NOTE: Units are per kWh for 'Electric' runs and per therm for 'Gas' runs for all sponsors.
Note on CE35: All costs minus all benefits regardless of which sponsor incurs the cost or accrues the benefits. TRC Net Levelized Cost includes all applicable costs and all benefits. In addition to energy system costs and benefits, TRC Net Levelized Cost includes non-energy, other-fuel, O&M, periodic-replacement and risk-mitigation benefits and costs. TRC Net Levelized Cost corresponds to TRC B/C ratios with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure. The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the TRC B/C ratio and the TRC Net Levelized Cost. If Risk-Mitigation credit is non-zero, TRC Levelized Cost will be reduced by the risk-mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on CW35: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BH41: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BM41: Direct and program administrative costs of the measure to sponsor. Separate costs for each sponsor. Depends on share of costs incurred by sponsor, sponsor cost of capital, and financing term which are user-defined inputs. Includes applicable Capital, O&M, Periodic Replacement and Program Administrative costs. Sponsor costs are levelized over program life. Does not include any adjustments for benefit. NOTE: Units are per kWh for 'Electric' runs and per therm for 'Gas' runs for all sponsors.
Note on CE41: All costs minus all benefits regardless of which sponsor incurs the cost or accrues the benefits. TRC Net Levelized Cost includes all applicable costs and all benefits. In addition to energy system costs and benefits, TRC Net Levelized Cost includes non-energy, other-fuel, O&M, periodic-replacement and risk-mitigation benefits and costs. TRC Net Levelized Cost corresponds to TRC B/C ratios with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure. The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the TRC B/C ratio and the TRC Net Levelized Cost. If Risk-Mitigation credit is non-zero, TRC Levelized Cost will be reduced by the risk-mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on CW41: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.

## Savings and Cost
Source: | 2013 California Building Energy Efficiency Standards
California Utilities Statewide Codes and Standards Team September 2011
[9 empty] | Million SF Region | SF of Parking garage | Applicability (ratio of parking garage sf to total segment sf)
[8 empty] | Large Off | 296.7359 | 73250419.635 | 24.69% | 24.69%
[8 empty] | Medium Off | 140.0123 | 0 | 0%
[8 empty] | Small Off | 150.4045 | 0 | 0%
[8 empty] | XLarge Ret | 139.7346 | 6020373.2367 | 4.308% | 4.308%
[8 empty] | Large Ret | 252.8773 | 0 | 0%
[8 empty] | Medium Ret | 68.0441 | 0 | 0%
[8 empty] | Small Ret | 122.9844 | 0 | 0%
[8 empty] | School K-12 | 248.9199 | 3152378.9261 | 1.266% | 1.266%
[8 empty] | University | 119.8213 |  | 6.973%
[8 empty] | Warehouse | 388.539 | 0 | 0%
[8 empty] | Supermarket | 57.6239 | 0 | 0%
[8 empty] | MiniMart | 23.1677 | 0 | 0%
[8 empty] | Restaurant | 66.5284 | 0 | 0%
[8 empty] | Lodging | 173.7563 | 8585515.689 | 4.941% | 4.941%
[8 empty] | Hospital | 78.9162 |  | 6.973%
[8 empty] | Residential Care | 160.046 | 3037479.1775 | 1.898% | 1.898%
[8 empty] | Assembly | 226.73 | 7818735.4927 | 3.448% | 3.448%
[8 empty] | Other | 417.1806 | 34463583.605 | 8.261% | 8.261%
[9 empty] | 3132.0224 |  |  | 6.973% | Use the average share to backfill for hospitals and universities (no data from CBSA)
Savings
kWh/yr
| Savings per Design CFM | 1.23
| Savings Per Prototype Building | 46.25
| Savings Per Square Foot | 0.925
| Row Labels | Sum of _Wt_PNW | Sum of Wt_PNW_Sf_Parking | kWh per year
| Assembly | 21261.8903 | 7818735.4927 | 7232330.3308
| Grocery | 6846.5638 | 0 | 0
| Lodging | 3557.2085 | 8585515.689 | 7941602.0123
| Office | 61592.8877 | 73250419.635 | 67756638.1624
| Other | 16636.0142 | 34463583.605 | 31878814.8346
| Residential Care | 4242.1114 | 3037479.1775 | 2809668.2392
| Restaurant | 12537.9956 | 0 | 0
| Retail/Service | 48814.4933 | 6020373.2367 | 5568845.2439
| School K-12 | 5777.1979 | 3152378.9261 | 2915950.5066
| Warehouse | 21938.962 | 0 | 0
| Grand Total | 203205.3249 | 136328485.762 | 126103849.3299
|  |  |  | 14.3954 | aMW
|  | Life | 15 | yrs
|  | Cost | 0.97 | per units | [5 empty] | 50000
[10 empty] | exhaust | 15 | 0.97 | 36275 | 0.94 | 35300 | 0.24 | 9061 | 80688 | -35352 | -36327
[13 empty] | 0.7255 |  | 0.706 |  | 0.18122 | 1.6138
|  | SF | $ | $/sf
| Santa Monica Hotel | 159500 | 64965 | 0.4073
| 9601 Wilshire Blvd | 284160 | 79933 | 0.2813
| 8484 Wilshire | 192000 | 82924 | 0.4319
| Pacific Plaza | 77520 | 28605 | 0.369
| Redondo Beach Library | 88500 | 36945 | 0.41746
| First Federal Banks | 218500 | 100498 | 0.45995
|  | 202500 | 86420 | 0.42677
|  | 1222680 | 480290 | 0.39282
The additional components required for CO control over a constant-volume garage are CO sensors,
controllers and fan variable frequency drives (VFDs). In addition to product costs for each of these
items, each item requires additional installation time and commissioning time. Also, these items
require periodic maintenance and replacement over the life of the garage.
Cost estimates for each item as well as the installation of each item were received from
manufacturers. Larger garages tend to have lower cost per item than smaller garages, both for product
and installation. Installation costs vary with local labor rates and the market. The table below shows
the range of the end cost of each item. In addition to this, each garage requires controls and
commissioning work, which is another $1,000 added to each system at installation.
Additionally, over a 15-year life of a garage, the sensors will likely need to be calibrated once per year
and replaced once in five years (can vary depending upon manufacturer’s recommendations).
Calibration procedures vary by manufacturer, but typically take 15 to 30 minutes per sensor, and are
typically required once per year or once per two years. Some sensors require no calibration at all.
Some manufacturers offer replacement sensor options where just the sensing element itself needs to
be replaced, and the casing of the original sensor can be reused. Replacing just the sensing element
itself can save as much as 85% off the original sensor price. Controllers and VFDs do not require
maintenance.
50000
| Product | Cost | Installation Cost | Frequency
| CO Sensor | $250-$400 | $800-$2500 | One Sensor per 5000 sqft |  | 325 | 1650 | 19750
| Controller | 3000-4000 | Included in sensor installation cost | One per 16 or 32 sensors |  |  |  | 3500
| VFD | 2600 | 500 | One per 10,000 cfm |  |  |  | 3100
26350
0.527
| Sensor replacement in 5 yrs | 2962.5 | 0.05925