## 7PSourceSummary
Commercial EM
Item | Methods & Sources | Note
Measures Described | Energy management measures for commercial buildings, excluding single-zone ducted systems. Suite of measures, most of which are focused on making HVAC systems work better through controls changes. This replaces/supercedes the HVAC Commissioning and Controls measure from the 6P | Programs like Strategic Energy Management appear to be acquiring strong savings results at much lower costs than were estimated for the 6P.
Energy Savings Calculation Basis | kWh/sf savings X sf applicable floor area. Savings= 18.5% for electric heated buildings and 15% for gas heated buildings | Compared the savings values with some limited data from ETO on commercial SEM. For office buildings, the data show about 7% total EUI savings. This translates to approximately 18% electric heating eui savings; very similar to the 6P assumption. Therefore, will use the same 6P savings assumptions. Baseline adjustments were made to reflect the reduced EUI's in the 2013 CBSA compared with the 2009 CBSA
Source of Savings Estimates | Various as noted in sheets. Based primarily program data from LBL, PECI, NEEA, SMUD. For retro Cx, savings range 1 to 2.2 kWh/sf from these programs. Savings range 0.5 to 1.2 kWh/sf for New.
Applicable Stock | Used the CBSA filtered by system type. This measure applies to "built up sytems" primarily. See Market data tab. | The 6th Plan measure had significantly more potential due to the estimates of applicable SF. The CBSA data provides solid data for the built up system SF.
Baseline
Baseline Saturation | Signficant achievements were made between 2010 and 2015. However, some of the data are mis-categorized. Saturation is 19% per 6 going on 7 data for "Energy Management Systems/System Controls" category | There are ongoing questions about the persistence of this measure and this type of measure
Permutations | Primarily Retrofit. Also include new, but use a very slow ramp rate - new buildings will need this measure within a few years after they are built. Same cost data for new.
Costs | Cost from 6P data seem to be low when compared to SEM data and other more recent energy management studies. Adjusted the 6P costs to reflect more recent program costs
Measure Life | Reduced the lifetime to 5 years (7 years in the 6P)
Non-Energy Benefits | Gas savings for gas heated buildings
Savings Shape | C-All-HVAC-Vent-All-All-E
Achievable Ramp Rate | Retro12Med, LO2Slow (for new building sf)
v3 | Revised per reviewer feedback
v4 | Added the High/Low Option

## forRPM
Ramp Rate | Resource Type | Measure Category | Sector | End Use | kW per unit | kWh per unit | TRC Net Levelized Cost (Net of All Benefits) | segment | measure | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | MAX | Savings Allocation by Category and Month for Segments 1 | [11 empty] | Savings Allocation by Category and Month for Segments 2
[5 empty] | Wholesale KW | Busbar Savings | lvlcost |  |  | aMW_2016 | aMW_2017 | aMW_2018 | aMW_2019 | aMW_2020 | aMW_2021 | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | MAX | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
RetroEven20 | Retro | Commercial EM | Commercial | HVAC | 0.13639 | 725.5086 | 39.1624 | Large Off | Commercial EM-Retro-Large Off | 1.0893 | 1.086 | 1.0828 | 1.1017 | 1.1209 | 1.1347 | 1.1483 | 1.1649 | 1.1807 | 1.1931 | 1.2098 | 1.2239 | 1.2376 | 1.2533 | 1.2691 | 1.2867 | 1.3063 | 1.324 | 1.3436 | 1.3627 | 27.2544 | 45.4931 | 40.9057 | 47.0719 | 43.792 | 44.709 | 44.2559 | 42.0439 | 43.8081 | 40.9308 | 46.6689 | 41.2994 | 44.9643 | 19.3145 | 16.5945 | 15.9176 | 16.6206 | 16.3071 | 14.309 | 16.8006 | 13.7782 | 16.9624 | 15.2349 | 18.2788 | 19.4474
RetroEven20 | Retro | Commercial EM | Commercial | HVAC | 0.016958 | 90.2112 | 49.6197 | Medium Off | Commercial EM-Retro-Medium Off | 0.067969 | 0.067765 | 0.067562 | 0.069496 | 0.071549 | 0.072996 | 0.074468 | 0.076248 | 0.077933 | 0.079194 | 0.080997 | 0.082543 | 0.084002 | 0.085715 | 0.087424 | 0.089266 | 0.091267 | 0.09314 | 0.095239 | 0.097222 | 1.9444 | 5.6567 | 5.0863 | 5.853 | 5.4452 | 5.5592 | 5.5029 | 5.2278 | 5.4472 | 5.0894 | 5.8029 | 5.1352 | 5.5909 | 2.4016 | 2.0634 | 1.9792 | 2.0666 | 2.0277 | 1.7792 | 2.089 | 1.7132 | 2.1091 | 1.8943 | 2.2728 | 2.4181
RetroEven20 | Retro | Commercial EM | Commercial | HVAC | 0.0046434 | 24.7007 | 158.7645 | Small Off | Commercial EM-Retro-Small Off | 0.017962 | 0.017908 | 0.017855 | 0.017954 | 0.018063 | 0.018129 | 0.018197 | 0.018286 | 0.01837 | 0.018423 | 0.018514 | 0.018588 | 0.018655 | 0.01874 | 0.018825 | 0.018919 | 0.019026 | 0.019123 | 0.019236 | 0.019341 | 0.38682 | 1.5489 | 1.3927 | 1.6026 | 1.4909 | 1.5222 | 1.5067 | 1.4314 | 1.4915 | 1.3935 | 1.5889 | 1.4061 | 1.5309 | 0.65758 | 0.56498 | 0.54193 | 0.56587 | 0.55519 | 0.48716 | 0.57199 | 0.46909 | 0.5775 | 0.51869 | 0.62232 | 0.66211
RetroEven20 | Retro | Commercial EM | Commercial | HVAC | 0.0062942 | 33.4823 | 46.489 | XLarge Ret | Commercial EM-Retro-XLarge Ret | 0.018299 | 0.018215 | 0.018131 | 0.018166 | 0.018321 | 0.018434 | 0.018471 | 0.01851 | 0.018541 | 0.018557 | 0.018573 | 0.018587 | 0.018625 | 0.018682 | 0.018748 | 0.018883 | 0.019045 | 0.019182 | 0.019316 | 0.019442 | 0.38884 | 2.0995 | 1.8878 | 2.1724 | 2.021 | 2.0633 | 2.0424 | 1.9403 | 2.0217 | 1.889 | 2.1538 | 1.906 | 2.0751 | 0.89137 | 0.76584 | 0.7346 | 0.76704 | 0.75257 | 0.66036 | 0.77535 | 0.63586 | 0.78282 | 0.70309 | 0.84357 | 0.8975
RetroEven20 | Retro | Commercial EM | Commercial | HVAC | 0.044502 | 236.7305 | 131.2056 | Large Ret | Commercial EM-Retro-Large Ret | 0.1954 | 0.1945 | 0.19361 | 0.19305 | 0.19284 | 0.19251 | 0.19198 | 0.19145 | 0.1909 | 0.19031 | 0.18972 | 0.18913 | 0.18862 | 0.18817 | 0.18774 | 0.18751 | 0.18735 | 0.18713 | 0.18691 | 0.18666 | 3.7332 | 14.8442 | 13.3474 | 15.3594 | 14.2892 | 14.5884 | 14.4405 | 13.7187 | 14.2944 | 13.3555 | 15.2279 | 13.4758 | 14.6717 | 6.3023 | 5.4147 | 5.1938 | 5.4232 | 5.3209 | 4.669 | 5.482 | 4.4958 | 5.5348 | 4.9711 | 5.9643 | 6.3456
RetroEven20 | Retro | Commercial EM | Commercial | HVAC | 0.0070418 | 37.4593 | 87.8753 | Medium Ret | Commercial EM-Retro-Medium Ret | 0.01437 | 0.014304 | 0.014238 | 0.014372 | 0.01471 | 0.014977 | 0.015118 | 0.015263 | 0.015392 | 0.015491 | 0.01559 | 0.015683 | 0.015823 | 0.015999 | 0.016188 | 0.016489 | 0.016836 | 0.017139 | 0.017438 | 0.017724 | 0.35449 | 2.3489 | 2.112 | 2.4304 | 2.2611 | 2.3084 | 2.285 | 2.1708 | 2.2619 | 2.1133 | 2.4096 | 2.1324 | 2.3216 | 0.99725 | 0.8568 | 0.82186 | 0.85815 | 0.84196 | 0.7388 | 0.86745 | 0.71139 | 0.8758 | 0.78661 | 0.94377 | 1.0041
RetroEven20 | Retro | Commercial EM | Commercial | HVAC | 0.029203 | 155.3447 | 25.9451 | Small Ret | Commercial EM-Retro-Small Ret | 0.067181 | 0.066872 | 0.066564 | 0.066519 | 0.066743 | 0.066877 | 0.066845 | 0.06682 | 0.066774 | 0.066687 | 0.066599 | 0.066506 | 0.06648 | 0.066506 | 0.066552 | 0.06674 | 0.066991 | 0.067185 | 0.067377 | 0.067552 | 1.351 | 9.7409 | 8.7587 | 10.079 | 9.3767 | 9.573 | 9.476 | 9.0024 | 9.3801 | 8.764 | 9.9927 | 8.843 | 9.6277 | 4.1356 | 3.5532 | 3.4083 | 3.5588 | 3.4916 | 3.0638 | 3.5973 | 2.9502 | 3.632 | 3.2621 | 3.9138 | 4.164
RetroEven20 | Retro | Commercial EM | Commercial | HVAC | 0.03744 | 199.1614 | 74.9938 | School K-12 | Commercial EM-Retro-School K-12 | 0.18969 | 0.18891 | 0.18814 | 0.18776 | 0.18738 | 0.18749 | 0.18747 | 0.18728 | 0.18711 | 0.18703 | 0.18706 | 0.18749 | 0.18822 | 0.18877 | 0.18935 | 0.19003 | 0.19076 | 0.19141 | 0.1921 | 0.19265 | 3.853 | 12.4884 | 11.2291 | 12.9218 | 12.0215 | 12.2732 | 12.1488 | 11.5416 | 12.0259 | 11.236 | 12.8112 | 11.3372 | 12.3433 | 5.3021 | 4.5554 | 4.3696 | 4.5626 | 4.4765 | 3.928 | 4.612 | 3.7823 | 4.6564 | 4.1822 | 5.0178 | 5.3386
RetroEven20 | Retro | Commercial EM | Commercial | HVAC | 0.16474 | 876.3554 | 41.4905 | University | Commercial EM-Retro-University | 0.42287 | 0.42113 | 0.4194 | 0.4199 | 0.41916 | 0.41848 | 0.4188 | 0.41998 | 0.42061 | 0.42148 | 0.42203 | 0.42374 | 0.42617 | 0.4286 | 0.43144 | 0.43438 | 0.43768 | 0.44105 | 0.44391 | 0.44638 | 8.9276 | 54.952 | 49.4107 | 56.8591 | 52.8972 | 54.0049 | 53.4575 | 50.7856 | 52.9166 | 49.4411 | 56.3722 | 49.8863 | 54.3132 | 23.3304 | 20.0448 | 19.2272 | 20.0764 | 19.6976 | 17.2841 | 20.2937 | 16.6429 | 20.4892 | 18.4025 | 22.0793 | 23.4909
RetroEven20 | Retro | Commercial EM | Commercial | HVAC | 0.0054564 | 29.0253 | 71.2908 | Warehouse | Commercial EM-Retro-Warehouse | 0.051445 | 0.051255 | 0.051066 | 0.051786 | 0.052476 | 0.053157 | 0.053617 | 0.053982 | 0.054208 | 0.054384 | 0.054667 | 0.055004 | 0.055378 | 0.055734 | 0.05611 | 0.056439 | 0.056702 | 0.05698 | 0.057259 | 0.057594 | 1.1519 | 1.82 | 1.6365 | 1.8832 | 1.752 | 1.7887 | 1.7705 | 1.682 | 1.7526 | 1.6375 | 1.8671 | 1.6523 | 1.7989 | 0.77271 | 0.66389 | 0.63681 | 0.66494 | 0.65239 | 0.57246 | 0.67214 | 0.55122 | 0.67861 | 0.6095 | 0.73128 | 0.77803
RetroEven20 | Retro | Commercial EM | Commercial | HVAC | 0.012478 | 66.3759 | 26.895 | Supermarket | Commercial EM-Retro-Supermarket | 0.014085 | 0.013959 | 0.013833 | 0.013787 | 0.013766 | 0.013734 | 0.013691 | 0.013649 | 0.013607 | 0.013565 | 0.013523 | 0.013481 | 0.013439 | 0.013397 | 0.013356 | 0.013314 | 0.013273 | 0.01323 | 0.01319 | 0.013151 | 0.26303 | 4.1621 | 3.7424 | 4.3066 | 4.0065 | 4.0904 | 4.0489 | 3.8465 | 4.0079 | 3.7447 | 4.2697 | 3.7784 | 4.1137 | 1.7671 | 1.5182 | 1.4563 | 1.5206 | 1.4919 | 1.3091 | 1.5371 | 1.2605 | 1.5519 | 1.3938 | 1.6723 | 1.7792
RetroEven20 | Retro | Commercial EM | Commercial | HVAC | 0 | 0 | 9999 | MiniMart | Commercial EM-Retro-MiniMart | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RetroEven20 | Retro | Commercial EM | Commercial | HVAC | 0.0092599 | 49.2585 | 47.7652 | Restaurant | Commercial EM-Retro-Restaurant | 0.010031 | 0.0099834 | 0.0099363 | 0.010017 | 0.010062 | 0.010107 | 0.010149 | 0.010191 | 0.010232 | 0.010273 | 0.010314 | 0.010354 | 0.010394 | 0.010434 | 0.010475 | 0.010545 | 0.010631 | 0.010714 | 0.010802 | 0.010896 | 0.21791 | 3.0888 | 2.7773 | 3.196 | 2.9733 | 3.0355 | 3.0048 | 2.8546 | 2.9744 | 2.779 | 3.1686 | 2.804 | 3.0529 | 1.3114 | 1.1267 | 1.0807 | 1.1285 | 1.1072 | 0.97151 | 1.1407 | 0.93547 | 1.1517 | 1.0344 | 1.241 | 1.3204
RetroEven20 | Retro | Commercial EM | Commercial | HVAC | 0.02196 | 116.818 | 31.737 | Lodging | Commercial EM-Retro-Lodging | 0.078517 | 0.078328 | 0.07814 | 0.07861 | 0.078899 | 0.079181 | 0.079338 | 0.079503 | 0.07962 | 0.079725 | 0.079822 | 0.079918 | 0.080035 | 0.080172 | 0.080353 | 0.0808 | 0.081358 | 0.081934 | 0.082524 | 0.083154 | 1.6631 | 7.3251 | 6.5864 | 7.5793 | 7.0512 | 7.1988 | 7.1259 | 6.7697 | 7.0538 | 6.5905 | 7.5144 | 6.6498 | 7.2399 | 3.1099 | 2.672 | 2.563 | 2.6762 | 2.6257 | 2.304 | 2.7052 | 2.2185 | 2.7312 | 2.4531 | 2.9432 | 3.1313
RetroEven20 | Retro | Commercial EM | Commercial | HVAC | 0.30852 | 1641.1873 | 11.6522 | Hospital | Commercial EM-Retro-Hospital | 0.6809 | 0.67947 | 0.67805 | 0.69597 | 0.72135 | 0.74301 | 0.76235 | 0.77813 | 0.78887 | 0.79814 | 0.80659 | 0.81383 | 0.8211 | 0.82884 | 0.83829 | 0.84997 | 0.86352 | 0.87551 | 0.88702 | 0.89818 | 17.9637 | 102.9109 | 92.5336 | 106.4823 | 99.0628 | 101.1372 | 100.1121 | 95.1082 | 99.0992 | 92.5903 | 105.5706 | 93.4242 | 101.7145 | 43.6918 | 37.5387 | 36.0075 | 37.5979 | 36.8885 | 32.3687 | 38.0049 | 31.1679 | 38.3711 | 34.4632 | 41.3488 | 43.9924
RetroEven20 | Retro | Commercial EM | Commercial | HVAC | 0.028651 | 152.4085 | 19.7706 | Residential Care | Commercial EM-Retro-Residential Care | 0.077512 | 0.077326 | 0.07714 | 0.07875 | 0.081276 | 0.083547 | 0.085526 | 0.087173 | 0.088376 | 0.089477 | 0.090485 | 0.091393 | 0.092357 | 0.093388 | 0.094595 | 0.096101 | 0.097768 | 0.099241 | 0.10075 | 0.10222 | 2.0443 | 9.5568 | 8.5931 | 9.8885 | 9.1994 | 9.3921 | 9.2969 | 8.8322 | 9.2028 | 8.5984 | 9.8038 | 8.6758 | 9.4457 | 4.0574 | 3.486 | 3.3438 | 3.4915 | 3.4256 | 3.0059 | 3.5293 | 2.8944 | 3.5633 | 3.2004 | 3.8398 | 4.0853
RetroEven20 | Retro | Commercial EM | Commercial | HVAC | 0.032907 | 175.0492 | 33.2569 | Assembly | Commercial EM-Retro-Assembly | 0.25993 | 0.25876 | 0.2576 | 0.25939 | 0.26044 | 0.26149 | 0.26192 | 0.26258 | 0.26303 | 0.2634 | 0.26331 | 0.26327 | 0.26379 | 0.26495 | 0.26635 | 0.26833 | 0.27126 | 0.27465 | 0.27834 | 0.28193 | 5.6386 | 10.9765 | 9.8696 | 11.3574 | 10.566 | 10.7873 | 10.678 | 10.1443 | 10.5699 | 9.8757 | 11.2602 | 9.9646 | 10.8489 | 4.6602 | 4.0039 | 3.8406 | 4.0102 | 3.9345 | 3.4524 | 4.0536 | 3.3244 | 4.0927 | 3.6758 | 4.4103 | 4.6922
RetroEven20 | Retro | Commercial EM | Commercial | HVAC | 0.040837 | 217.2361 | 23.2921 | Other | Commercial EM-Retro-Other | 0.29403 | 0.29139 | 0.28877 | 0.29423 | 0.30269 | 0.30934 | 0.31551 | 0.32113 | 0.32496 | 0.3295 | 0.33389 | 0.33886 | 0.34446 | 0.34986 | 0.35624 | 0.36317 | 0.3703 | 0.37682 | 0.38402 | 0.39031 | 7.8063 | 13.6218 | 12.2482 | 14.0946 | 13.1125 | 13.387 | 13.2514 | 12.589 | 13.1173 | 12.2557 | 13.9739 | 12.3661 | 13.4635 | 5.7833 | 4.9688 | 4.7661 | 4.9766 | 4.8828 | 4.2845 | 5.0305 | 4.1255 | 5.079 | 4.5617 | 5.4731 | 5.8231
Note on A1: Charlie Grist: Lookup in ComMaster
Note on B1: Charlie Grist: New, NR, Retro
Note on C1: Charlie Grist: Measure Index Name
Note on E1: Charlie Grist: Use Massoud's Names
Note on F1: Charlie Grist: From Shaped Savings column 14
Note on G1: Charlie Grist: From SC or from Shaped Savings column 3.
Note on H1: Charlie Grist: From SC or from Shaped Savings column K (column 11)
Note on I1: Charlie Grist: From SC
Note on J1: Charlie Grist: From SC
Note on K1: Charlie Grist: From SC
Note on AF1: Charlie Grist: From Shaped Savings. Copy whole row down since column increment is hardwired into formula.

## SC New
Units Methodology | The new construction portion of the Com-EM measure applies to commercial buildings just a few years after they are built (per RTF input). New square footage in year 1 moved to retrofit starting in year 4.
| Vintage | New | New
End-Use: | Measure Bundle | Commercial EM-New | Region
HVAC | Report Year | 2035
| Total Potential (aMW) | 0 | NEW SF ADDED TO RETROFIT | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
UNITS FOR EXISTING STOCK |  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
|  |  |  | FLOOR_2016 | FLOOR_2017 | FLOOR_2018 | FLOOR_2019 | FLOOR_2020 | FLOOR_2021 | FLOOR_2022 | FLOOR_2023 | FLOOR_2024 | FLOOR_2025 | FLOOR_2026 | FLOOR_2027 | FLOOR_2028 | FLOOR_2029 | FLOOR_2030 | FLOOR_2031 | FLOOR_2032 | FLOOR_2033 | FLOOR_2034 | FLOOR_2035
| REG_Office | Large Off |  | 7.7489 | 7.8067 | 5.9497 | 5.8909 | 6.8916 | 6.641 | 5.4382 | 6.9237 | 6.0406 | 5.862 | 6.6048 | 6.6082 | 7.2276 | 7.9321 | 7.259 | 7.9122 | 7.7623 | 7.6402 | 7.1725 | 7.081
| REG_Office | Medium Off |  | 5.9953 | 6.3307 | 4.6246 | 4.6954 | 5.5562 | 5.2903 | 4.0955 | 5.6166 | 4.8928 | 4.649 | 5.3601 | 5.3451 | 5.7169 | 6.1644 | 5.8004 | 6.4332 | 6.1077 | 6.3133 | 5.5403 | 5.5266
| REG_Office | Small Off |  | 1.5723 | 1.6621 | 1.2171 | 1.2444 | 1.4586 | 1.4004 | 1.0788 | 1.4748 | 1.2896 | 1.2239 | 1.4012 | 1.3991 | 1.4996 | 1.6198 | 1.5187 | 1.6891 | 1.5972 | 1.6405 | 1.4566 | 1.4532
| REG_Retail | XLarge Ret |  | 0.89046 | 1.7994 | 1.4858 | 0.89794 | 0.91202 | 0.85125 | 0.73204 | 0.73428 | 0.71341 | 0.89456 | 1.0321 | 1.0963 | 1.6173 | 1.8239 | 1.6267 | 1.597 | 1.5393 | 1.2961 | 1.3176 | 1.247
| REG_Retail | Large Ret |  | 0.3567 | 0.7196 | 0.59648 | 0.36612 | 0.37318 | 0.34505 | 0.29286 | 0.29376 | 0.28416 | 0.36455 | 0.42647 | 0.44956 | 0.65214 | 0.73354 | 0.65561 | 0.64605 | 0.62178 | 0.52555 | 0.53266 | 0.50454
| REG_Retail | Medium Ret |  | 1.3432 | 2.7276 | 2.2452 | 1.3847 | 1.4143 | 1.3049 | 1.1035 | 1.0932 | 1.0602 | 1.3687 | 1.6102 | 1.7014 | 2.4475 | 2.7643 | 2.4645 | 2.4352 | 2.3437 | 1.9971 | 2.0221 | 1.9075
| REG_Retail | Small Ret |  | 0.42474 | 0.8625 | 0.71244 | 0.43988 | 0.4488 | 0.41374 | 0.34302 | 0.33947 | 0.32966 | 0.43689 | 0.51887 | 0.54817 | 0.7797 | 0.87859 | 0.7842 | 0.77729 | 0.74887 | 0.63964 | 0.64715 | 0.61166
| REG_K-12 | School K-12 |  | 0.50323 | 0.49337 | 1.103 | 0.94992 | 0.71721 | 0.74423 | 0.8514 | 0.99139 | 1.5015 | 1.8698 | 1.6453 | 1.6753 | 1.7943 | 1.8624 | 1.7489 | 1.7976 | 1.6195 | 1.8221 | 1.6337 | 1.7826
| REG_University | University |  | 0.63958 | 0.28002 | 0.2972 | 0.58203 | 0.83189 | 0.6661 | 0.73648 | 0.64334 | 0.97289 | 1.1821 | 1.1785 | 1.2952 | 1.3229 | 1.4229 | 1.443 | 1.2924 | 1.1785 | 1.3434 | 1.2266 | 1.2571
| REG_Warehouse | Warehouse |  | 7.9301 | 7.6587 | 7.5775 | 5.6454 | 4.8008 | 3.5881 | 3.153 | 4.0692 | 4.54 | 4.8555 | 4.6966 | 4.8557 | 4.4518 | 3.8658 | 3.9817 | 3.9952 | 4.4738 | 4.2737 | 4.087 | 4.1377
| REG_Grocery | Supermarket |  | 0.3011 | 0.38925 | 0.34341 | 0.29927 | 0.29689 | 0.2938 | 0.29042 | 0.28614 | 0.28164 | 0.27689 | 0.27358 | 0.27063 | 0.26801 | 0.2666 | 0.25138 | 0.26455 | 0.26299 | 0.26141 | 0.25948 | 0.25751
| REG_Grocery Other | MiniMart |  | 0.15345 | 0.19766 | 0.18601 | 0.095761 | 0.10062 | 0.085647 | 0.065415 | 0.057243 | 0.055087 | 0.073916 | 0.092056 | 0.10394 | 0.15172 | 0.15707 | 0.14511 | 0.15273 | 0.14105 | 0.11701 | 0.12001 | 0.11457
| REG_Restaurant | Restaurant |  | 0.65648 | 0.46895 | 0.47387 | 0.45145 | 0.45051 | 0.44778 | 0.44523 | 0.44274 | 0.43991 | 0.43709 | 0.43514 | 0.4358 | 0.59162 | 0.66468 | 0.65354 | 0.67606 | 0.7056 | 0.63207 | 0.63726 | 0.58284
| REG_Hotel | Lodging |  | 1.4232 | 1.0327 | 1.0159 | 0.74305 | 0.76054 | 0.65616 | 0.62755 | 0.61023 | 0.60572 | 0.65098 | 0.6932 | 0.78844 | 1.3646 | 1.6032 | 1.6413 | 1.6703 | 1.7557 | 1.4871 | 1.44 | 1.35
| REG_hospital | Hospital |  | 2.9844 | 4.1336 | 3.5601 | 3.2008 | 2.6531 | 1.873 | 1.6467 | 1.5196 | 1.3328 | 1.3372 | 1.4087 | 1.6726 | 2.0158 | 2.3034 | 2.0639 | 1.988 | 1.9342 | 1.7745 | 1.6724 | 1.5414
| REG_Hospital Other | Residential Care |  | 2.9816 | 4.5029 | 4.0786 | 3.592 | 3.0401 | 2.3019 | 2.1321 | 1.9772 | 1.8096 | 1.9023 | 2.013 | 2.304 | 2.7992 | 3.0682 | 2.7442 | 2.8047 | 2.7283 | 2.496 | 2.4392 | 2.3387
| REG_Assembly | Assembly |  | 4.2644 | 3.1855 | 3.1699 | 2.2629 | 2.6024 | 2.292 | 2.1556 | 1.482 | 1.5603 | 2.3546 | 3.274 | 3.6242 | 4.442 | 5.8224 | 6.4604 | 6.9015 | 6.7485 | 6.4365 | 6.3053 | 6.2237
| REG_Other | Other |  | 9.3944 | 12.8631 | 10.722 | 10.1421 | 9.4612 | 7.3639 | 8.1591 | 7.9604 | 8.6026 | 9.3208 | 9.0573 | 10.1844 | 10.7877 | 11.0054 | 10.2671 | 11.0275 | 9.9609 | 10.34 | 9.8384 | 9.3283
|  |  |  | 49.5635 | 57.1143 | 49.3587 | 42.884 | 42.7699 | 36.5593 | 33.3471 | 36.5153 | 36.3126 | 39.0609 | 41.7212 | 44.3582 | 49.9305 | 53.9587 | 51.5098 | 54.0605 | 52.2301 | 51.0362 | 48.3482 | 47.246 | 0
Achievability |  |  | Ramp Rate: | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 0%
CUMULATIVE MAX BASED ON APPL, TURN & ACHIEV |  | Commercial EM-New | LO1Slow | 0.2564% | 0.769% | 1.679% | 3.16% | 5.407% | 8.625% | 13% | 18.68% | 25.7% | 33.98% | 43.26% | 53.14% | 63.06% | 72.42% | 80.64% | 87.33% | 92.33% | 95.74% | 97.82% | 98.82%
| 100% | Large Off |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 100% | Medium Off |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 100% | Small Off |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 100% | XLarge Ret |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 100% | Large Ret |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 100% | Medium Ret |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 100% | Small Ret |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 100% | School K-12 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 100% | University |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 100% | Warehouse |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 100% | Supermarket |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 100% | MiniMart |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 100% | Restaurant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 100% | Lodging |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 100% | Hospital |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 100% | Residential Care |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 100% | Assembly |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 100% | Other |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2016.0026 | 2017.0077 | 2018.0168 | 2019.0316 | 2020.0541 | 2021.0863 | 2022.13 | 2023.1868 | 2024.257 | 2025.3398 | 2026.4326 | 2027.5314 | 2028.6306 | 2029.7242 | 2030.8064 | 2031.8733 | 2032.9233 | 2033.9574 | 2034.9782 | 2035.9882 | 0
SUPPLY CURVE SAVINGS BY BUNDLE |  | Commercial EM-New |  | 2016: aMW
|  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | MAX
Busbar Savings (kWh) | lvlcost | segment | measure | aMW_2016 | aMW_2017 | aMW_2018 | aMW_2019 | aMW_2020 | aMW_2021 | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | MAX
918.5124 | 21.9103 | Large Off | Commercial EM-New-Large Off | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290.2939 | 28.9461 | Medium Off | Commercial EM-New-Medium Off | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19.4538 | 138.5786 | Small Off | Commercial EM-New-Small Off | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32.4834 | 42.9489 | XLarge Ret | Commercial EM-New-XLarge Ret | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235.2764 | 108.1114 | Large Ret | Commercial EM-New-Large Ret | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35.0174 | 71.2214 | Medium Ret | Commercial EM-New-Medium Ret | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134.8916 | 20.5497 | Small Ret | Commercial EM-New-Small Ret | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181.5528 | 63.1763 | School K-12 | Commercial EM-New-School K-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
786.8684 | 30.151 | University | Commercial EM-New-University | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28.5557 | 75.8218 | Warehouse | Commercial EM-New-Warehouse | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107.7437 | 13.3316 | Supermarket | Commercial EM-New-Supermarket | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 9999 | MiniMart | Commercial EM-New-MiniMart | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47.1478 | 29.9091 | Restaurant | Commercial EM-New-Restaurant | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104.9849 | 19.0285 | Lodging | Commercial EM-New-Lodging | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1557.8749 | 5.7585 | Hospital | Commercial EM-New-Hospital | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117.9787 | 3.1067 | Residential Care | Commercial EM-New-Residential Care | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153.8362 | 14.1958 | Assembly | Commercial EM-New-Assembly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183.0218 | 13.2052 | Other | Commercial EM-New-Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0%: 0 | 0
RECOMBINE MEASURE BUNDLES INTO SUPPLY CURVE CUMULATIVE
|  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | Max
|  | lvlcost | lvlcost | aMW_2016 | aMW_2017 | aMW_2018 | aMW_2019 | aMW_2020 | aMW_2021 | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | max
| Block 1: <= 0 mills/kWh | >=-9999 | <=0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 2: <= 10 mills/kWh | >0 | <=10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 3: 10-20 mills/kWh | >10 | <=20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 4: 20-30 mills/kWh | >20 | <=30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 5: 30-40 mills/kWh | >30 | <=40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 6: 40-50 mills/kWh | >40 | <=50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 7: 50-60 mills/kWh | >50 | <=60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 8: 60-70 mills/kWh | >60 | <=70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 9: 70-80 mills/kWh | >70 | <=80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 10: 80-90 mills/kWh | >80 | <=90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 11: 90-100 mills/kWh | >90 | <=100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 12: 100-110 mills/kWh | >100 | <=110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 13: 110-120 mills/kWh | >110 | <=120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 14: 120-130 mills/kWh | >120 | <=130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 15: 130-140 mills/kWh | >130 | <=140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 16: 140-150 mills/kWh | >140 | <=150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 17: 150-160 mills/kWh | >150 | <=160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 18: 160-170 mills/kWh | >160 | <=170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 19: 170-180 mills/kWh | >170 | <=180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 20: 180-190 mills/kWh | >180 | <=190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 21: 190-200 mills/kWh | >190 | <=200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 22: 200-210 mills/kWh | >200 | <=210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 23: 210-220 mills/kWh | >210 | <=220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 24: 220-230 mills/kWh | >220 | <=230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 25: 230-240 mills/kWh | >230 | <=240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 26: 240-250 mills/kWh | >240 | <=250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 27: 250-260 mills/kWh | >250 | <=260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 28: 260-270 mills/kWh | >260 | <=270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 29: 270-280 mills/kWh | >270 | <=280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 30: 280-290 mills/kWh | >280 | <=290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 31: 290-300 mills/kWh | >290 | <=300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 32: >300 mills/kWh | >300 | <=999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RECOMBINE MEASURE BUNDLES INTO SUPPLY CURVE INCREMENTAL
|  |  | Commercial EM-New | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | Max
|  |  |  | aMW_2016 | aMW_2017 | aMW_2018 | aMW_2019 | aMW_2020 | aMW_2021 | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | aMW_
|  | Block 1: <= 0 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 2: <= 10 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 3: 10-20 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 4: 20-30 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 5: 30-40 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 6: 40-50 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 7: 50-60 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 8: 60-70 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 9: 70-80 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 10: 80-90 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 11: 90-100 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 12: 100-110 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 13: 110-120 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 14: 120-130 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 15: 130-140 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 16: 140-150 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 17: 150-160 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 18: 160-170 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 19: 170-180 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 20: 180-190 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 21: 190-200 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 22: 200-210 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 23: 210-220 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 24: 220-230 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 25: 230-240 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 26: 240-250 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 27: 250-260 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 28: 260-270 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 29: 270-280 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 30: 280-290 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 31: 290-300 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 32: >300 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total per Year |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total Cumulative |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
cumulative new construction
|  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
|  |  | FLOOR_2016 | FLOOR_2017 | FLOOR_2018 | FLOOR_2019 | FLOOR_2020 | FLOOR_2021 | FLOOR_2022 | FLOOR_2023 | FLOOR_2024 | FLOOR_2025 | FLOOR_2026 | FLOOR_2027 | FLOOR_2028 | FLOOR_2029 | FLOOR_2030 | FLOOR_2031 | FLOOR_2032 | FLOOR_2033 | FLOOR_2034 | FLOOR_2035
REG_Office | Large Off |  | 7.7489 | 15.5555 | 21.5052 | 27.3961 | 34.2877 | 40.9287 | 46.367 | 53.2906 | 59.3312 | 65.1932 | 71.798 | 78.4062 | 85.6339 | 93.566 | 100.825 | 108.7373 | 116.4996 | 124.1398 | 131.3123 | 138.3933
REG_Office | Medium Off |  | 5.9953 | 12.326 | 16.9505 | 21.646 | 27.2022 | 32.4925 | 36.588 | 42.2046 | 47.0974 | 51.7464 | 57.1065 | 62.4516 | 68.1685 | 74.3329 | 80.1333 | 86.5665 | 92.6743 | 98.9876 | 104.5279 | 110.0545
REG_Office | Small Off |  | 1.5723 | 3.2344 | 4.4514 | 5.6959 | 7.1545 | 8.5549 | 9.6337 | 11.1085 | 12.3981 | 13.622 | 15.0233 | 16.4224 | 17.922 | 19.5418 | 21.0606 | 22.7496 | 24.3469 | 25.9873 | 27.4439 | 28.8971
REG_Retail | XLarge Ret |  | 0.89046 | 2.6899 | 4.1756 | 5.0736 | 5.9856 | 6.8368 | 7.5689 | 8.3032 | 9.0166 | 9.9111 | 10.9432 | 12.0396 | 13.6569 | 15.4808 | 17.1075 | 18.7045 | 20.2439 | 21.5399 | 22.8576 | 24.1046
REG_Retail | Large Ret |  | 0.3567 | 1.0763 | 1.6728 | 2.0389 | 2.4121 | 2.7571 | 3.05 | 3.3438 | 3.6279 | 3.9925 | 4.4189 | 4.8685 | 5.5206 | 6.2542 | 6.9098 | 7.5558 | 8.1776 | 8.7032 | 9.2358 | 9.7404
REG_Retail | Medium Ret |  | 1.3432 | 4.0708 | 6.316 | 7.7007 | 9.115 | 10.4199 | 11.5234 | 12.6167 | 13.6769 | 15.0456 | 16.6558 | 18.3573 | 20.8048 | 23.5691 | 26.0336 | 28.4688 | 30.8125 | 32.8096 | 34.8316 | 36.7391
REG_Retail | Small Ret |  | 0.42474 | 1.2872 | 1.9997 | 2.4396 | 2.8884 | 3.3021 | 3.6451 | 3.9846 | 4.3142 | 4.7511 | 5.27 | 5.8182 | 6.5979 | 7.4765 | 8.2607 | 9.0379 | 9.7868 | 10.4265 | 11.0736 | 11.6853
REG_K-12 | School K-12 |  | 0.50323 | 0.9966 | 2.0996 | 3.0495 | 3.7667 | 4.5109 | 5.3623 | 6.3537 | 7.8552 | 9.725 | 11.3702 | 13.0456 | 14.8399 | 16.7023 | 18.4512 | 20.2488 | 21.8683 | 23.6904 | 25.3241 | 27.1067
REG_University | University |  | 0.63958 | 0.9196 | 1.2168 | 1.7988 | 2.6307 | 3.2968 | 4.0333 | 4.6767 | 5.6495 | 6.8316 | 8.0102 | 9.3054 | 10.6283 | 12.0512 | 13.4942 | 14.7866 | 15.9651 | 17.3085 | 18.5351 | 19.7922
REG_Warehouse | Warehouse |  | 7.9301 | 15.5888 | 23.1663 | 28.8117 | 33.6124 | 37.2006 | 40.3536 | 44.4227 | 48.9628 | 53.8183 | 58.515 | 63.3707 | 67.8224 | 71.6882 | 75.67 | 79.6651 | 84.139 | 88.4127 | 92.4997 | 96.6374
REG_Grocery | Supermarket |  | 0.3011 | 0.69035 | 1.0338 | 1.333 | 1.6299 | 1.9237 | 2.2141 | 2.5003 | 2.7819 | 3.0588 | 3.3324 | 3.603 | 3.871 | 4.1376 | 4.389 | 4.6536 | 4.9166 | 5.178 | 5.4375 | 5.695
REG_Grocery Other | MiniMart |  | 0.15345 | 0.3511 | 0.53711 | 0.63287 | 0.73349 | 0.81913 | 0.88455 | 0.94179 | 0.99688 | 1.0708 | 1.1629 | 1.2668 | 1.4185 | 1.5756 | 1.7207 | 1.8734 | 2.0145 | 2.1315 | 2.2515 | 2.366
REG_Restaurant | Restaurant |  | 0.65648 | 1.1254 | 1.5993 | 2.0507 | 2.5013 | 2.949 | 3.3943 | 3.837 | 4.2769 | 4.714 | 5.1491 | 5.5849 | 6.1766 | 6.8412 | 7.4948 | 8.1708 | 8.8764 | 9.5085 | 10.1458 | 10.7286
REG_Hotel | Lodging |  | 1.4232 | 2.4559 | 3.4717 | 4.2148 | 4.9753 | 5.6315 | 6.259 | 6.8693 | 7.475 | 8.126 | 8.8192 | 9.6076 | 10.9722 | 12.5754 | 14.2167 | 15.887 | 17.6426 | 19.1298 | 20.5698 | 21.9197
REG_hospital | Hospital |  | 2.9844 | 7.118 | 10.6781 | 13.8789 | 16.532 | 18.4051 | 20.0518 | 21.5714 | 22.9042 | 24.2415 | 25.6501 | 27.3227 | 29.3386 | 31.6419 | 33.7059 | 35.6939 | 37.6281 | 39.4026 | 41.075 | 42.6164
REG_Hospital Other | Residential Care |  | 2.9816 | 7.4845 | 11.5631 | 15.1551 | 18.1952 | 20.4971 | 22.6292 | 24.6064 | 26.416 | 28.3183 | 30.3313 | 32.6353 | 35.4346 | 38.5028 | 41.247 | 44.0516 | 46.7799 | 49.2759 | 51.7151 | 54.0538
REG_Assembly | Assembly |  | 4.2644 | 7.4499 | 10.6198 | 12.8827 | 15.485 | 17.777 | 19.9327 | 21.4147 | 22.975 | 25.3296 | 28.6037 | 32.2279 | 36.6699 | 42.4923 | 48.9527 | 55.8542 | 62.6027 | 69.0392 | 75.3445 | 81.5682
REG_Other | Other |  | 9.3944 | 22.2575 | 32.9795 | 43.1217 | 52.5829 | 59.9467 | 68.1059 | 76.0662 | 84.6688 | 93.9896 | 103.0469 | 113.2313 | 124.019 | 135.0244 | 145.2914 | 156.3189 | 166.2798 | 176.6199 | 186.4583 | 195.7865
|  |  | 49.5635 | 106.6778 | 156.0365 | 198.9205 | 241.6904 | 278.2497 | 311.5968 | 348.1121 | 384.4247 | 423.4856 | 465.2068 | 509.565 | 559.4954 | 613.4542 | 664.964 | 719.0245 | 771.2545 | 822.2907 | 870.639 | 917.8849

## SC Retro
Units Methodology
| Vintage | Retro | Stock 2016
End-Use: | Measure Bundle | Commercial EM-Retro | Region
HVAC | Report Year | 2035 | Base
| Total Potential (aMW) | 76.9869 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
UNITS FOR EXISTING STOCK |  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
|  |  |  | FLOOR_2016 | FLOOR_2017 | FLOOR_2018 | FLOOR_2019 | FLOOR_2020 | FLOOR_2021 | FLOOR_2022 | FLOOR_2023 | FLOOR_2024 | FLOOR_2025 | FLOOR_2026 | FLOOR_2027 | FLOOR_2028 | FLOOR_2029 | FLOOR_2030 | FLOOR_2031 | FLOOR_2032 | FLOOR_2033 | FLOOR_2034 | FLOOR_2035
|  | Large Off |  | 380.0883 | 378.948 | 377.8112 | 376.6777 | 375.5477 | 374.4211 | 373.2978 | 372.1779 | 371.0614 | 369.9482 | 368.8383 | 367.7318 | 366.6286 | 365.5288 | 364.4322 | 363.3389 | 362.2489 | 361.1621 | 360.0786 | 358.9984
|  | Medium Off |  | 190.7369 | 190.1647 | 189.5942 | 189.0254 | 188.4583 | 187.8929 | 187.3293 | 186.7673 | 186.207 | 185.6483 | 185.0914 | 184.5361 | 183.9825 | 183.4306 | 182.8803 | 182.3316 | 181.7846 | 181.2393 | 180.6956 | 180.1535
|  | Small Off |  | 184.0914 | 183.5391 | 182.9885 | 182.4395 | 181.8922 | 181.3465 | 180.8025 | 180.2601 | 179.7193 | 179.1801 | 178.6426 | 178.1067 | 177.5723 | 177.0396 | 176.5085 | 175.979 | 175.451 | 174.9247 | 174.3999 | 173.8767
|  | XLarge Ret |  | 138.3573 | 137.7209 | 137.0874 | 136.4568 | 135.8291 | 135.2043 | 134.5823 | 133.9632 | 133.347 | 132.7336 | 132.123 | 131.5153 | 130.9103 | 130.3081 | 129.7087 | 129.112 | 128.5181 | 127.9269 | 127.3385 | 126.7527
|  | Large Ret |  | 208.9575 | 207.9962 | 207.0395 | 206.0871 | 205.1391 | 204.1954 | 203.2561 | 202.3212 | 201.3905 | 200.4641 | 199.542 | 198.6241 | 197.7104 | 196.8009 | 195.8956 | 194.9945 | 194.0975 | 193.2047 | 192.316 | 191.4313
|  | Medium Ret |  | 97.1157 | 96.669 | 96.2243 | 95.7816 | 95.3411 | 94.9025 | 94.4659 | 94.0314 | 93.5988 | 93.1683 | 92.7397 | 92.3131 | 91.8885 | 91.4658 | 91.045 | 90.6262 | 90.2094 | 89.7944 | 89.3813 | 88.9702
|  | Small Ret |  | 109.4797 | 108.9761 | 108.4748 | 107.9758 | 107.4791 | 106.9847 | 106.4926 | 106.0027 | 105.5151 | 105.0297 | 104.5466 | 104.0657 | 103.587 | 103.1105 | 102.6362 | 102.164 | 101.6941 | 101.2263 | 100.7606 | 100.2971
|  | School K-12 |  | 241.1176 | 240.1291 | 239.1445 | 238.164 | 237.1876 | 236.2151 | 235.2466 | 234.2821 | 233.3215 | 232.3649 | 231.4122 | 230.4634 | 229.5185 | 228.5775 | 227.6403 | 226.707 | 225.7775 | 224.8518 | 223.9299 | 223.0118
|  | University |  | 122.1534 | 121.6526 | 121.1538 | 120.6571 | 120.1624 | 119.6697 | 119.1791 | 118.6904 | 118.2038 | 117.7192 | 117.2365 | 116.7558 | 116.2771 | 115.8004 | 115.3256 | 114.8528 | 114.3819 | 113.9129 | 113.4459 | 112.9808
|  | Warehouse |  | 448.6983 | 447.0381 | 445.3841 | 443.7362 | 442.0943 | 440.4586 | 438.8289 | 437.2052 | 435.5876 | 433.9759 | 432.3702 | 430.7704 | 429.1765 | 427.5886 | 426.0065 | 424.4303 | 422.8599 | 421.2953 | 419.7365 | 418.1835
|  | Supermarket |  | 53.7209 | 53.2375 | 52.7583 | 52.2835 | 51.8129 | 51.3466 | 50.8845 | 50.4265 | 49.9727 | 49.5229 | 49.0772 | 48.6355 | 48.1978 | 47.764 | 47.3342 | 46.9082 | 46.486 | 46.0676 | 45.653 | 45.2421
|  | MiniMart |  | 22.491 | 22.3849 | 22.2792 | 22.174 | 22.0694 | 21.9652 | 21.8615 | 21.7584 | 21.6557 | 21.5534 | 21.4517 | 21.3505 | 21.2497 | 21.1494 | 21.0496 | 20.9502 | 20.8513 | 20.7529 | 20.6549 | 20.5575
|  | Restaurant |  | 51.5509 | 51.3075 | 51.0654 | 50.8243 | 50.5844 | 50.3457 | 50.1081 | 49.8715 | 49.6362 | 49.4019 | 49.1687 | 48.9366 | 48.7056 | 48.4757 | 48.2469 | 48.0192 | 47.7926 | 47.567 | 47.3425 | 47.119
|  | Lodging |  | 170.1519 | 169.7435 | 169.3361 | 168.9297 | 168.5243 | 168.1199 | 167.7164 | 167.3138 | 166.9123 | 166.5117 | 166.1121 | 165.7134 | 165.3157 | 164.9189 | 164.5231 | 164.1283 | 163.7344 | 163.3414 | 162.9494 | 162.5583
|  | Hospital |  | 105.0295 | 104.8089 | 104.5888 | 104.3692 | 104.15 | 103.9313 | 103.713 | 103.4952 | 103.2779 | 103.061 | 102.8446 | 102.6286 | 102.4131 | 102.198 | 101.9834 | 101.7692 | 101.5555 | 101.3423 | 101.1294 | 100.9171
|  | Residential Care |  | 128.7482 | 128.4392 | 128.131 | 127.8234 | 127.5167 | 127.2106 | 126.9053 | 126.6008 | 126.2969 | 125.9938 | 125.6914 | 125.3898 | 125.0888 | 124.7886 | 124.4891 | 124.1903 | 123.8923 | 123.5949 | 123.2983 | 123.0024
|  | Assembly |  | 375.9022 | 374.2157 | 372.5367 | 370.8653 | 369.2013 | 367.5448 | 365.8958 | 364.2541 | 362.6198 | 360.9929 | 359.3732 | 357.7609 | 356.1557 | 354.5577 | 352.967 | 351.3833 | 349.8068 | 348.2373 | 346.6749 | 345.1195
|  | Other |  | 342.6499 | 339.566 | 336.5099 | 333.4814 | 330.48 | 327.5057 | 324.5581 | 321.6371 | 318.7424 | 315.8737 | 313.0308 | 310.2136 | 307.4216 | 304.6549 | 301.913 | 299.1957 | 296.503 | 293.8345 | 291.1899 | 288.5692
|  |  |  | 3371.0405 | 3356.5369 | 3342.1076 | 3327.752 | 3313.4699 | 3299.2606 | 3285.1238 | 3271.059 | 3257.0658 | 3243.1437 | 3229.2923 | 3215.5112 | 3201.7999 | 3188.1581 | 3174.5852 | 3161.0809 | 3147.6447 | 3134.2763 | 3120.9752 | 3107.7411
New SF added beginning in year 4
ACHIEVABILITY: |  |  | Ramp Rate: | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 85%
CUMULATIVE MAX BASED ON APPL, TURN & ACHIEV |  | Commercial EM-Retro | RetroEven20 | bar: 2016 to New SF added beginning in year 4 2035
| 81.42% | Large Off |  | 13.1524 | 13.1129 | 13.0736 | 13.3025 | 13.5335 | 13.7004 | 13.8654 | 14.0651 | 14.2563 | 14.406 | 14.6071 | 14.7779 | 14.9425 | 15.133 | 15.3238 | 15.536 | 15.7728 | 15.9864 | 16.2227 | 16.4539 | 329.0779
| 81.42% | Medium Off |  | 6.6002 | 6.5804 | 6.5606 | 6.7484 | 6.9478 | 7.0883 | 7.2313 | 7.4041 | 7.5678 | 7.6902 | 7.8652 | 8.0153 | 8.157 | 8.3234 | 8.4893 | 8.6682 | 8.8626 | 9.0444 | 9.2482 | 9.4408 | 188.8159
| 81.42% | Small Off |  | 6.3702 | 6.3511 | 6.332 | 6.3675 | 6.406 | 6.4293 | 6.4535 | 6.4852 | 6.5149 | 6.5336 | 6.5661 | 6.5921 | 6.616 | 6.646 | 6.6761 | 6.7097 | 6.7474 | 6.7818 | 6.8221 | 6.8592 | 137.1846
| 81.42% | XLarge Ret |  | 4.7876 | 4.7656 | 4.7437 | 4.7527 | 4.7932 | 4.823 | 4.8326 | 4.8427 | 4.8509 | 4.855 | 4.8592 | 4.8629 | 4.8729 | 4.8878 | 4.905 | 4.9403 | 4.9829 | 5.0187 | 5.0536 | 5.0866 | 101.7319
| 81.42% | Large Ret |  | 7.2307 | 7.1974 | 7.1643 | 7.1437 | 7.1358 | 7.1238 | 7.1039 | 7.0845 | 7.0642 | 7.0423 | 7.0206 | 6.9986 | 6.9796 | 6.9629 | 6.9471 | 6.9385 | 6.9329 | 6.9247 | 6.9163 | 6.9072 | 138.1433
| 81.42% | Medium Ret |  | 3.3605 | 3.3451 | 3.3297 | 3.3609 | 3.44 | 3.5025 | 3.5353 | 3.5692 | 3.5994 | 3.6227 | 3.6457 | 3.6676 | 3.7003 | 3.7414 | 3.7857 | 3.8559 | 3.9371 | 4.0081 | 4.078 | 4.1449 | 82.898
| 81.42% | Small Ret |  | 3.7884 | 3.771 | 3.7536 | 3.751 | 3.7637 | 3.7712 | 3.7694 | 3.768 | 3.7655 | 3.7605 | 3.7556 | 3.7503 | 3.7489 | 3.7503 | 3.7529 | 3.7635 | 3.7777 | 3.7886 | 3.7994 | 3.8093 | 76.1858
| 81.42% | School K-12 |  | 8.3435 | 8.3093 | 8.2752 | 8.2587 | 8.242 | 8.2465 | 8.2459 | 8.2373 | 8.2298 | 8.2262 | 8.2275 | 8.2467 | 8.2787 | 8.303 | 8.3286 | 8.3584 | 8.3907 | 8.4191 | 8.4494 | 8.4737 | 169.4742
| 81.42% | University |  | 4.2269 | 4.2096 | 4.1923 | 4.1973 | 4.1899 | 4.1831 | 4.1863 | 4.1981 | 4.2043 | 4.2131 | 4.2186 | 4.2357 | 4.26 | 4.2843 | 4.3127 | 4.3421 | 4.375 | 4.4087 | 4.4373 | 4.462 | 89.2396
| 81.42% | Warehouse |  | 15.5265 | 15.4691 | 15.4118 | 15.6292 | 15.8374 | 16.043 | 16.182 | 16.2919 | 16.3601 | 16.4135 | 16.4987 | 16.6004 | 16.7133 | 16.8209 | 16.9342 | 17.0337 | 17.1131 | 17.1967 | 17.281 | 17.3821 | 347.6423
| 81.42% | Supermarket |  | 1.8589 | 1.8422 | 1.8256 | 1.8196 | 1.8168 | 1.8125 | 1.8069 | 1.8013 | 1.7958 | 1.7903 | 1.7848 | 1.7792 | 1.7737 | 1.7681 | 1.7626 | 1.7571 | 1.7518 | 1.746 | 1.7408 | 1.7357 | 34.7133
| 81.42% | MiniMart |  | 0.77827 | 0.77459 | 0.77094 | 0.77261 | 0.77583 | 0.77866 | 0.77839 | 0.7783 | 0.77771 | 0.77643 | 0.77489 | 0.7733 | 0.77237 | 0.77208 | 0.77222 | 0.77404 | 0.77605 | 0.77766 | 0.77956 | 0.78107 | 15.6213
| 81.42% | Restaurant |  | 1.7838 | 1.7754 | 1.767 | 1.7814 | 1.7893 | 1.7975 | 1.8049 | 1.8123 | 1.8196 | 1.8269 | 1.8342 | 1.8414 | 1.8485 | 1.8556 | 1.8628 | 1.8754 | 1.8905 | 1.9053 | 1.921 | 1.9376 | 38.7528
| 81.42% | Lodging |  | 5.8879 | 5.8737 | 5.8596 | 5.8948 | 5.9165 | 5.9377 | 5.9494 | 5.9618 | 5.9706 | 5.9785 | 5.9858 | 5.9929 | 6.0017 | 6.0119 | 6.0255 | 6.0591 | 6.1009 | 6.1441 | 6.1884 | 6.2356 | 124.7117
| 81.42% | Hospital |  | 3.6344 | 3.6268 | 3.6191 | 3.7148 | 3.8503 | 3.9659 | 4.0691 | 4.1534 | 4.2107 | 4.2601 | 4.3052 | 4.3439 | 4.3827 | 4.424 | 4.4744 | 4.5368 | 4.6091 | 4.6731 | 4.7346 | 4.7941 | 95.883
| 81.42% | Residential Care |  | 4.4551 | 4.4444 | 4.4338 | 4.5263 | 4.6715 | 4.8021 | 4.9158 | 5.0104 | 5.0796 | 5.1429 | 5.2008 | 5.253 | 5.3084 | 5.3677 | 5.4371 | 5.5236 | 5.6194 | 5.7041 | 5.7909 | 5.8751 | 117.5012
| 81.42% | Assembly |  | 13.0075 | 12.9492 | 12.8911 | 12.9808 | 13.0335 | 13.0858 | 13.1071 | 13.1403 | 13.1631 | 13.1814 | 13.1766 | 13.1748 | 13.2007 | 13.2587 | 13.3291 | 13.428 | 13.5749 | 13.7442 | 13.9289 | 14.1086 | 282.1723
| 81.42% | Other |  | 11.8569 | 11.7502 | 11.6444 | 11.8647 | 12.206 | 12.4741 | 12.723 | 12.9493 | 13.104 | 13.287 | 13.4641 | 13.6643 | 13.8902 | 14.1079 | 14.3654 | 14.6447 | 14.9324 | 15.1953 | 15.4854 | 15.7394 | 314.7874
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2685.3865
SUPPLY CURVE SAVINGS BY BUNDLE |  | Commercial EM-Retro |  | 2016: aMW
|  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | MAX
Busbar Savings (kWh) | lvlcost | segment | measure | aMW_2016 | aMW_2017 | aMW_2018 | aMW_2019 | aMW_2020 | aMW_2021 | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | MAX
725.5086 | 39.1624 | Large Off | Commercial EM-Retro-Large Off | 1.0893 | 1.086 | 1.0828 | 1.1017 | 1.1209 | 1.1347 | 1.1483 | 1.1649 | 1.1807 | 1.1931 | 1.2098 | 1.2239 | 1.2376 | 1.2533 | 1.2691 | 1.2867 | 1.3063 | 1.324 | 1.3436 | 1.3627 | 27.2544 | 24.1194
90.2112 | 49.6197 | Medium Off | Commercial EM-Retro-Medium Off | 0.067969 | 0.067765 | 0.067562 | 0.069496 | 0.071549 | 0.072996 | 0.074468 | 0.076248 | 0.077933 | 0.079194 | 0.080997 | 0.082543 | 0.084002 | 0.085715 | 0.087424 | 0.089266 | 0.091267 | 0.09314 | 0.095239 | 0.097222 | 1.9444 | 1.612
24.7007 | 158.7645 | Small Off | Commercial EM-Retro-Small Off | 0.017962 | 0.017908 | 0.017855 | 0.017954 | 0.018063 | 0.018129 | 0.018197 | 0.018286 | 0.01837 | 0.018423 | 0.018514 | 0.018588 | 0.018655 | 0.01874 | 0.018825 | 0.018919 | 0.019026 | 0.019123 | 0.019236 | 0.019341 | 0.38682 | 0.37011
33.4823 | 46.489 | XLarge Ret | Commercial EM-Retro-XLarge Ret | 0.018299 | 0.018215 | 0.018131 | 0.018166 | 0.018321 | 0.018434 | 0.018471 | 0.01851 | 0.018541 | 0.018557 | 0.018573 | 0.018587 | 0.018625 | 0.018682 | 0.018748 | 0.018883 | 0.019045 | 0.019182 | 0.019316 | 0.019442 | 0.38884 | 0.37273
236.7305 | 131.2056 | Large Ret | Commercial EM-Retro-Large Ret | 0.1954 | 0.1945 | 0.19361 | 0.19305 | 0.19284 | 0.19251 | 0.19198 | 0.19145 | 0.1909 | 0.19031 | 0.18972 | 0.18913 | 0.18862 | 0.18817 | 0.18774 | 0.18751 | 0.18735 | 0.18713 | 0.18691 | 0.18666 | 3.7332 | 3.8055
37.4593 | 87.8753 | Medium Ret | Commercial EM-Retro-Medium Ret | 0.01437 | 0.014304 | 0.014238 | 0.014372 | 0.01471 | 0.014977 | 0.015118 | 0.015263 | 0.015392 | 0.015491 | 0.01559 | 0.015683 | 0.015823 | 0.015999 | 0.016188 | 0.016489 | 0.016836 | 0.017139 | 0.017438 | 0.017724 | 0.35449 | 0.31315
155.3447 | 25.9451 | Small Ret | Commercial EM-Retro-Small Ret | 0.067181 | 0.066872 | 0.066564 | 0.066519 | 0.066743 | 0.066877 | 0.066845 | 0.06682 | 0.066774 | 0.066687 | 0.066599 | 0.066506 | 0.06648 | 0.066506 | 0.066552 | 0.06674 | 0.066991 | 0.067185 | 0.067377 | 0.067552 | 1.351 | 1.3364
199.1614 | 74.9938 | School K-12 | Commercial EM-Retro-School K-12 | 0.18969 | 0.18891 | 0.18814 | 0.18776 | 0.18738 | 0.18749 | 0.18747 | 0.18728 | 0.18711 | 0.18703 | 0.18706 | 0.18749 | 0.18822 | 0.18877 | 0.18935 | 0.19003 | 0.19076 | 0.19141 | 0.1921 | 0.19265 | 3.853 | 3.7761
876.3554 | 41.4905 | University | Commercial EM-Retro-University | 0.42287 | 0.42113 | 0.4194 | 0.4199 | 0.41916 | 0.41848 | 0.4188 | 0.41998 | 0.42061 | 0.42148 | 0.42203 | 0.42374 | 0.42617 | 0.4286 | 0.43144 | 0.43438 | 0.43768 | 0.44105 | 0.44391 | 0.44638 | 8.9276 | 8.5372
29.0253 | 71.2908 | Warehouse | Commercial EM-Retro-Warehouse | 0.051445 | 0.051255 | 0.051066 | 0.051786 | 0.052476 | 0.053157 | 0.053617 | 0.053982 | 0.054208 | 0.054384 | 0.054667 | 0.055004 | 0.055378 | 0.055734 | 0.05611 | 0.056439 | 0.056702 | 0.05698 | 0.057259 | 0.057594 | 1.1519 | 1.0892
66.3759 | 26.895 | Supermarket | Commercial EM-Retro-Supermarket | 0.014085 | 0.013959 | 0.013833 | 0.013787 | 0.013766 | 0.013734 | 0.013691 | 0.013649 | 0.013607 | 0.013565 | 0.013523 | 0.013481 | 0.013439 | 0.013397 | 0.013356 | 0.013314 | 0.013273 | 0.01323 | 0.01319 | 0.013151 | 0.26303 | 0.27103
0 | 9999 | MiniMart | Commercial EM-Retro-MiniMart | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49.2585 | 47.7652 | Restaurant | Commercial EM-Retro-Restaurant | 0.010031 | 0.0099834 | 0.0099363 | 0.010017 | 0.010062 | 0.010107 | 0.010149 | 0.010191 | 0.010232 | 0.010273 | 0.010314 | 0.010354 | 0.010394 | 0.010434 | 0.010475 | 0.010545 | 0.010631 | 0.010714 | 0.010802 | 0.010896 | 0.21791 | 0.20654
116.818 | 31.737 | Lodging | Commercial EM-Retro-Lodging | 0.078517 | 0.078328 | 0.07814 | 0.07861 | 0.078899 | 0.079181 | 0.079338 | 0.079503 | 0.07962 | 0.079725 | 0.079822 | 0.079918 | 0.080035 | 0.080172 | 0.080353 | 0.0808 | 0.081358 | 0.081934 | 0.082524 | 0.083154 | 1.6631 | 1.5999
1641.1873 | 11.6522 | Hospital | Commercial EM-Retro-Hospital | 0.6809 | 0.67947 | 0.67805 | 0.69597 | 0.72135 | 0.74301 | 0.76235 | 0.77813 | 0.78887 | 0.79814 | 0.80659 | 0.81383 | 0.8211 | 0.82884 | 0.83829 | 0.84997 | 0.86352 | 0.87551 | 0.88702 | 0.89818 | 17.9637 | 15.8091
152.4085 | 19.7706 | Residential Care | Commercial EM-Retro-Residential Care | 0.077512 | 0.077326 | 0.07714 | 0.07875 | 0.081276 | 0.083547 | 0.085526 | 0.087173 | 0.088376 | 0.089477 | 0.090485 | 0.091393 | 0.092357 | 0.093388 | 0.094595 | 0.096101 | 0.097768 | 0.099241 | 0.10075 | 0.10222 | 2.0443 | 1.7844
175.0492 | 33.2569 | Assembly | Commercial EM-Retro-Assembly | 0.25993 | 0.25876 | 0.2576 | 0.25939 | 0.26044 | 0.26149 | 0.26192 | 0.26258 | 0.26303 | 0.2634 | 0.26331 | 0.26327 | 0.26379 | 0.26495 | 0.26635 | 0.26833 | 0.27126 | 0.27465 | 0.27834 | 0.28193 | 5.6386 | 5.3047
217.2361 | 23.2921 | Other | Commercial EM-Retro-Other | 0.29403 | 0.29139 | 0.28877 | 0.29423 | 0.30269 | 0.30934 | 0.31551 | 0.32113 | 0.32496 | 0.3295 | 0.33389 | 0.33886 | 0.34446 | 0.34986 | 0.35624 | 0.36317 | 0.3703 | 0.37682 | 0.38402 | 0.39031 | 7.8063 | 6.6795
|  |  |  | 3.5495 | 3.5361 | 3.5228 | 3.5715 | 3.6306 | 3.6781 | 3.7218 | 3.7651 | 3.7992 | 3.8287 | 3.8615 | 3.8923 | 3.9251 | 3.9613 | 4.0012 | 4.0476 | 4.1001 | 4.1484 | 4.199 | 4.2471 | 84.9427 | 76.9869
RECOMBINE MEASURE BUNDLES INTO SUPPLY CURVE CUMULATIVE
|  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | Max
|  | lvlcost | lvlcost | aMW_2016 | aMW_2017 | aMW_2018 | aMW_2019 | aMW_2020 | aMW_2021 | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | max
| Block 1: <= 0 mills/kWh | >=-9999 | <=0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 2: <= 10 mills/kWh | >0 | <=10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 3: 10-20 mills/kWh | >10 | <=20 | 0.75841 | 0.7568 | 0.75519 | 0.77472 | 0.80262 | 0.82656 | 0.84787 | 0.86531 | 0.87724 | 0.88761 | 0.89707 | 0.90522 | 0.91345 | 0.92222 | 0.93288 | 0.94607 | 0.96128 | 0.97475 | 0.98777 | 1.0004 | 20.008
| Block 4: 20-30 mills/kWh | >20 | <=30 | 1.1337 | 1.129 | 1.1243 | 1.1493 | 1.1858 | 1.2165 | 1.2439 | 1.2669 | 1.2826 | 1.2974 | 1.3111 | 1.3241 | 1.3378 | 1.352 | 1.369 | 1.3893 | 1.4119 | 1.432 | 1.4524 | 1.4714 | 29.4284
| Block 5: 30-40 mills/kWh | >30 | <=40 | 2.5614 | 2.5521 | 2.5429 | 2.589 | 2.646 | 2.6919 | 2.7335 | 2.7739 | 2.806 | 2.8336 | 2.864 | 2.8912 | 2.9192 | 2.9504 | 2.9849 | 3.0251 | 3.0708 | 3.1126 | 3.1568 | 3.1992 | 63.9845
| Block 6: 40-50 mills/kWh | >40 | <=50 | 3.0806 | 3.0692 | 3.0579 | 3.1066 | 3.1651 | 3.2119 | 3.2554 | 3.2988 | 3.3333 | 3.3631 | 3.3959 | 3.4264 | 3.4584 | 3.4939 | 3.533 | 3.5782 | 3.6294 | 3.6767 | 3.7261 | 3.7732 | 75.4632
| Block 7: 50-60 mills/kWh | >50 | <=60 | 3.0806 | 3.0692 | 3.0579 | 3.1066 | 3.1651 | 3.2119 | 3.2554 | 3.2988 | 3.3333 | 3.3631 | 3.3959 | 3.4264 | 3.4584 | 3.4939 | 3.533 | 3.5782 | 3.6294 | 3.6767 | 3.7261 | 3.7732 | 75.4632
| Block 8: 60-70 mills/kWh | >60 | <=70 | 3.0806 | 3.0692 | 3.0579 | 3.1066 | 3.1651 | 3.2119 | 3.2554 | 3.2988 | 3.3333 | 3.3631 | 3.3959 | 3.4264 | 3.4584 | 3.4939 | 3.533 | 3.5782 | 3.6294 | 3.6767 | 3.7261 | 3.7732 | 75.4632
| Block 9: 70-80 mills/kWh | >70 | <=80 | 3.3217 | 3.3094 | 3.2971 | 3.3461 | 3.405 | 3.4525 | 3.4965 | 3.5401 | 3.5746 | 3.6045 | 3.6376 | 3.6689 | 3.702 | 3.7384 | 3.7784 | 3.8247 | 3.8769 | 3.9251 | 3.9754 | 4.0234 | 80.4682
| Block 10: 80-90 mills/kWh | >80 | <=90 | 3.3361 | 3.3237 | 3.3113 | 3.3605 | 3.4197 | 3.4675 | 3.5116 | 3.5553 | 3.59 | 3.62 | 3.6532 | 3.6846 | 3.7178 | 3.7544 | 3.7946 | 3.8412 | 3.8937 | 3.9422 | 3.9929 | 4.0411 | 80.8226
| Block 11: 90-100 mills/kWh | >90 | <=100 | 3.3361 | 3.3237 | 3.3113 | 3.3605 | 3.4197 | 3.4675 | 3.5116 | 3.5553 | 3.59 | 3.62 | 3.6532 | 3.6846 | 3.7178 | 3.7544 | 3.7946 | 3.8412 | 3.8937 | 3.9422 | 3.9929 | 4.0411 | 80.8226
| Block 12: 100-110 mills/kWh | >100 | <=110 | 3.3361 | 3.3237 | 3.3113 | 3.3605 | 3.4197 | 3.4675 | 3.5116 | 3.5553 | 3.59 | 3.62 | 3.6532 | 3.6846 | 3.7178 | 3.7544 | 3.7946 | 3.8412 | 3.8937 | 3.9422 | 3.9929 | 4.0411 | 80.8226
| Block 13: 110-120 mills/kWh | >110 | <=120 | 3.3361 | 3.3237 | 3.3113 | 3.3605 | 3.4197 | 3.4675 | 3.5116 | 3.5553 | 3.59 | 3.62 | 3.6532 | 3.6846 | 3.7178 | 3.7544 | 3.7946 | 3.8412 | 3.8937 | 3.9422 | 3.9929 | 4.0411 | 80.8226
| Block 14: 120-130 mills/kWh | >120 | <=130 | 3.3361 | 3.3237 | 3.3113 | 3.3605 | 3.4197 | 3.4675 | 3.5116 | 3.5553 | 3.59 | 3.62 | 3.6532 | 3.6846 | 3.7178 | 3.7544 | 3.7946 | 3.8412 | 3.8937 | 3.9422 | 3.9929 | 4.0411 | 80.8226
| Block 15: 130-140 mills/kWh | >130 | <=140 | 3.5315 | 3.5182 | 3.5049 | 3.5535 | 3.6125 | 3.66 | 3.7036 | 3.7468 | 3.7809 | 3.8103 | 3.8429 | 3.8737 | 3.9064 | 3.9425 | 3.9823 | 4.0287 | 4.0811 | 4.1293 | 4.1798 | 4.2278 | 84.5558
| Block 16: 140-150 mills/kWh | >140 | <=150 | 3.5315 | 3.5182 | 3.5049 | 3.5535 | 3.6125 | 3.66 | 3.7036 | 3.7468 | 3.7809 | 3.8103 | 3.8429 | 3.8737 | 3.9064 | 3.9425 | 3.9823 | 4.0287 | 4.0811 | 4.1293 | 4.1798 | 4.2278 | 84.5558
| Block 17: 150-160 mills/kWh | >150 | <=160 | 3.5495 | 3.5361 | 3.5228 | 3.5715 | 3.6306 | 3.6781 | 3.7218 | 3.7651 | 3.7992 | 3.8287 | 3.8615 | 3.8923 | 3.9251 | 3.9613 | 4.0012 | 4.0476 | 4.1001 | 4.1484 | 4.199 | 4.2471 | 84.9427
| Block 18: 160-170 mills/kWh | >160 | <=170 | 3.5495 | 3.5361 | 3.5228 | 3.5715 | 3.6306 | 3.6781 | 3.7218 | 3.7651 | 3.7992 | 3.8287 | 3.8615 | 3.8923 | 3.9251 | 3.9613 | 4.0012 | 4.0476 | 4.1001 | 4.1484 | 4.199 | 4.2471 | 84.9427
| Block 19: 170-180 mills/kWh | >170 | <=180 | 3.5495 | 3.5361 | 3.5228 | 3.5715 | 3.6306 | 3.6781 | 3.7218 | 3.7651 | 3.7992 | 3.8287 | 3.8615 | 3.8923 | 3.9251 | 3.9613 | 4.0012 | 4.0476 | 4.1001 | 4.1484 | 4.199 | 4.2471 | 84.9427
| Block 20: 180-190 mills/kWh | >180 | <=190 | 3.5495 | 3.5361 | 3.5228 | 3.5715 | 3.6306 | 3.6781 | 3.7218 | 3.7651 | 3.7992 | 3.8287 | 3.8615 | 3.8923 | 3.9251 | 3.9613 | 4.0012 | 4.0476 | 4.1001 | 4.1484 | 4.199 | 4.2471 | 84.9427
| Block 21: 190-200 mills/kWh | >190 | <=200 | 3.5495 | 3.5361 | 3.5228 | 3.5715 | 3.6306 | 3.6781 | 3.7218 | 3.7651 | 3.7992 | 3.8287 | 3.8615 | 3.8923 | 3.9251 | 3.9613 | 4.0012 | 4.0476 | 4.1001 | 4.1484 | 4.199 | 4.2471 | 84.9427
| Block 22: 200-210 mills/kWh | >200 | <=210 | 3.5495 | 3.5361 | 3.5228 | 3.5715 | 3.6306 | 3.6781 | 3.7218 | 3.7651 | 3.7992 | 3.8287 | 3.8615 | 3.8923 | 3.9251 | 3.9613 | 4.0012 | 4.0476 | 4.1001 | 4.1484 | 4.199 | 4.2471 | 84.9427
| Block 23: 210-220 mills/kWh | >210 | <=220 | 3.5495 | 3.5361 | 3.5228 | 3.5715 | 3.6306 | 3.6781 | 3.7218 | 3.7651 | 3.7992 | 3.8287 | 3.8615 | 3.8923 | 3.9251 | 3.9613 | 4.0012 | 4.0476 | 4.1001 | 4.1484 | 4.199 | 4.2471 | 84.9427
| Block 24: 220-230 mills/kWh | >220 | <=230 | 3.5495 | 3.5361 | 3.5228 | 3.5715 | 3.6306 | 3.6781 | 3.7218 | 3.7651 | 3.7992 | 3.8287 | 3.8615 | 3.8923 | 3.9251 | 3.9613 | 4.0012 | 4.0476 | 4.1001 | 4.1484 | 4.199 | 4.2471 | 84.9427
| Block 25: 230-240 mills/kWh | >230 | <=240 | 3.5495 | 3.5361 | 3.5228 | 3.5715 | 3.6306 | 3.6781 | 3.7218 | 3.7651 | 3.7992 | 3.8287 | 3.8615 | 3.8923 | 3.9251 | 3.9613 | 4.0012 | 4.0476 | 4.1001 | 4.1484 | 4.199 | 4.2471 | 84.9427
| Block 26: 240-250 mills/kWh | >240 | <=250 | 3.5495 | 3.5361 | 3.5228 | 3.5715 | 3.6306 | 3.6781 | 3.7218 | 3.7651 | 3.7992 | 3.8287 | 3.8615 | 3.8923 | 3.9251 | 3.9613 | 4.0012 | 4.0476 | 4.1001 | 4.1484 | 4.199 | 4.2471 | 84.9427
| Block 27: 250-260 mills/kWh | >250 | <=260 | 3.5495 | 3.5361 | 3.5228 | 3.5715 | 3.6306 | 3.6781 | 3.7218 | 3.7651 | 3.7992 | 3.8287 | 3.8615 | 3.8923 | 3.9251 | 3.9613 | 4.0012 | 4.0476 | 4.1001 | 4.1484 | 4.199 | 4.2471 | 84.9427
| Block 28: 260-270 mills/kWh | >260 | <=270 | 3.5495 | 3.5361 | 3.5228 | 3.5715 | 3.6306 | 3.6781 | 3.7218 | 3.7651 | 3.7992 | 3.8287 | 3.8615 | 3.8923 | 3.9251 | 3.9613 | 4.0012 | 4.0476 | 4.1001 | 4.1484 | 4.199 | 4.2471 | 84.9427
| Block 29: 270-280 mills/kWh | >270 | <=280 | 3.5495 | 3.5361 | 3.5228 | 3.5715 | 3.6306 | 3.6781 | 3.7218 | 3.7651 | 3.7992 | 3.8287 | 3.8615 | 3.8923 | 3.9251 | 3.9613 | 4.0012 | 4.0476 | 4.1001 | 4.1484 | 4.199 | 4.2471 | 84.9427
| Block 30: 280-290 mills/kWh | >280 | <=290 | 3.5495 | 3.5361 | 3.5228 | 3.5715 | 3.6306 | 3.6781 | 3.7218 | 3.7651 | 3.7992 | 3.8287 | 3.8615 | 3.8923 | 3.9251 | 3.9613 | 4.0012 | 4.0476 | 4.1001 | 4.1484 | 4.199 | 4.2471 | 84.9427
| Block 31: 290-300 mills/kWh | >290 | <=300 | 3.5495 | 3.5361 | 3.5228 | 3.5715 | 3.6306 | 3.6781 | 3.7218 | 3.7651 | 3.7992 | 3.8287 | 3.8615 | 3.8923 | 3.9251 | 3.9613 | 4.0012 | 4.0476 | 4.1001 | 4.1484 | 4.199 | 4.2471 | 84.9427
| Block 32: >300 mills/kWh | >300 | <=999 | 3.5495 | 3.5361 | 3.5228 | 3.5715 | 3.6306 | 3.6781 | 3.7218 | 3.7651 | 3.7992 | 3.8287 | 3.8615 | 3.8923 | 3.9251 | 3.9613 | 4.0012 | 4.0476 | 4.1001 | 4.1484 | 4.199 | 4.2471 | 84.9427
|  |  |  | 3.5495 | 3.5361 | 3.5228 | 3.5715 | 3.6306 | 3.6781 | 3.7218 | 3.7651 | 3.7992 | 3.8287 | 3.8615 | 3.8923 | 3.9251 | 3.9613 | 4.0012 | 4.0476 | 4.1001 | 4.1484 | 4.199 | 4.2471 | 84.9427
RECOMBINE MEASURE BUNDLES INTO SUPPLY CURVE INCREMENTAL
|  |  | Commercial EM-Retro | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | Max
|  |  |  | aMW_2016 | aMW_2017 | aMW_2018 | aMW_2019 | aMW_2020 | aMW_2021 | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | aMW_
|  | Block 1: <= 0 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 2: <= 10 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 3: 10-20 mills/kWh |  | 0.75841 | 0.7568 | 0.75519 | 0.77472 | 0.80262 | 0.82656 | 0.84787 | 0.86531 | 0.87724 | 0.88761 | 0.89707 | 0.90522 | 0.91345 | 0.92222 | 0.93288 | 0.94607 | 0.96128 | 0.97475 | 0.98777 | 1.0004 | 20.008
|  | Block 4: 20-30 mills/kWh |  | 0.3753 | 0.37222 | 0.36916 | 0.37453 | 0.3832 | 0.38995 | 0.39605 | 0.40159 | 0.40534 | 0.40975 | 0.41401 | 0.41884 | 0.42438 | 0.42976 | 0.43615 | 0.44322 | 0.45057 | 0.45724 | 0.46458 | 0.47102 | 9.4204
|  | Block 5: 30-40 mills/kWh |  | 1.4277 | 1.4231 | 1.4185 | 1.4397 | 1.4602 | 1.4754 | 1.4896 | 1.507 | 1.5234 | 1.5362 | 1.5529 | 1.5671 | 1.5814 | 1.5984 | 1.6158 | 1.6358 | 1.6589 | 1.6806 | 1.7044 | 1.7278 | 34.5561
|  | Block 6: 40-50 mills/kWh |  | 0.51916 | 0.51709 | 0.51503 | 0.51758 | 0.51909 | 0.52002 | 0.52188 | 0.52493 | 0.52731 | 0.5295 | 0.53192 | 0.53522 | 0.53919 | 0.54343 | 0.54809 | 0.55308 | 0.55862 | 0.56409 | 0.56927 | 0.57394 | 11.4788
|  | Block 7: 50-60 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 8: 60-70 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 9: 70-80 mills/kWh |  | 0.24114 | 0.24017 | 0.23921 | 0.23955 | 0.23986 | 0.24064 | 0.24109 | 0.24126 | 0.24132 | 0.24141 | 0.24172 | 0.24249 | 0.2436 | 0.24451 | 0.24546 | 0.24647 | 0.24747 | 0.24839 | 0.24936 | 0.25025 | 5.0049
|  | Block 10: 80-90 mills/kWh |  | 0.01437 | 0.014304 | 0.014238 | 0.014372 | 0.01471 | 0.014977 | 0.015118 | 0.015263 | 0.015392 | 0.015491 | 0.01559 | 0.015683 | 0.015823 | 0.015999 | 0.016188 | 0.016489 | 0.016836 | 0.017139 | 0.017438 | 0.017724 | 0.35449
|  | Block 11: 90-100 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 12: 100-110 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 13: 110-120 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 14: 120-130 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 15: 130-140 mills/kWh |  | 0.1954 | 0.1945 | 0.19361 | 0.19305 | 0.19284 | 0.19251 | 0.19198 | 0.19145 | 0.1909 | 0.19031 | 0.18972 | 0.18913 | 0.18862 | 0.18817 | 0.18774 | 0.18751 | 0.18735 | 0.18713 | 0.18691 | 0.18666 | 3.7332
|  | Block 16: 140-150 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 17: 150-160 mills/kWh |  | 0.017962 | 0.017908 | 0.017855 | 0.017954 | 0.018063 | 0.018129 | 0.018197 | 0.018286 | 0.01837 | 0.018423 | 0.018514 | 0.018588 | 0.018655 | 0.01874 | 0.018825 | 0.018919 | 0.019026 | 0.019123 | 0.019236 | 0.019341 | 0.38682
|  | Block 18: 160-170 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 19: 170-180 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 20: 180-190 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 21: 190-200 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 22: 200-210 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 23: 210-220 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 24: 220-230 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 25: 230-240 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 26: 240-250 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 27: 250-260 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 28: 260-270 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 29: 270-280 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 30: 280-290 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 31: 290-300 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 32: >300 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total per Year |  | 3.5495 | 3.5361 | 3.5228 | 3.5715 | 3.6306 | 3.6781 | 3.7218 | 3.7651 | 3.7992 | 3.8287 | 3.8615 | 3.8923 | 3.9251 | 3.9613 | 4.0012 | 4.0476 | 4.1001 | 4.1484 | 4.199 | 4.2471
|  | Total Cumulative |  | 3.5495 | 7.0856 | 10.6084 | 14.1799 | 17.8104 | 21.4886 | 25.2104 | 28.9754 | 32.7747 | 36.6034 | 40.4649 | 44.3571 | 48.2822 | 52.2435 | 56.2447 | 60.2923 | 64.3924 | 68.5408 | 72.7398 | 76.9869 | 84.9427

## Measure InputOutput_Out
Shaped Savings Results; By Category and sorted by TRC BC ratio
[14 empty] | Savings Allocation by Category and Month for Segments 1 | [11 empty] | Savings Allocation by Category and Month for Segments 2
Category | Measure | Busbar Savings | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Wholesale KW | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Commercial EM-Retro-MiniMart |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commercial EM-Retro-Hospital |  | 1641.1873 | 237.9665 | 47.5933 | 285.5598 | 873.1776 | 1467.4528 | 1524.2035 | -1.4953 | 11.6522 | 1.6806 | 22.3467 | 0.30852 | 102.9109 | 92.5336 | 106.4823 | 99.0628 | 101.1372 | 100.1121 | 95.1082 | 99.0992 | 92.5903 | 105.5706 | 93.4242 | 101.7145 | 43.6918 | 37.5387 | 36.0075 | 37.5979 | 36.8885 | 32.3687 | 38.0049 | 31.1679 | 38.3711 | 34.4632 | 41.3488 | 43.9924
Commercial EM-Retro-Residential Care |  | 152.4085 | 21.2559 | 4.2512 | 25.5071 | 77.995 | 116.3669 | 1466.0743 | -1.8453 | 19.7706 | 1.492 | 1.7168 | 0.028651 | 9.5568 | 8.5931 | 9.8885 | 9.1994 | 9.3921 | 9.2969 | 8.8322 | 9.2028 | 8.5984 | 9.8038 | 8.6758 | 9.4457 | 4.0574 | 3.486 | 3.3438 | 3.4915 | 3.4256 | 3.0059 | 3.5293 | 2.8944 | 3.5633 | 3.2004 | 3.8398 | 4.0853
Commercial EM-Retro-Small Ret |  | 155.3447 | 25.4638 | 5.0928 | 30.5566 | 93.4352 | 119.5107 | 1723.1078 | -0.29763 | 25.9451 | 1.2791 | 1.7661 | 0.029203 | 9.7409 | 8.7587 | 10.079 | 9.3767 | 9.573 | 9.476 | 9.0024 | 9.3801 | 8.764 | 9.9927 | 8.843 | 9.6277 | 4.1356 | 3.5532 | 3.4083 | 3.5588 | 3.4916 | 3.0638 | 3.5973 | 2.9502 | 3.632 | 3.2621 | 3.9138 | 4.164
Commercial EM-Retro-Other |  | 217.2361 | 50.3221 | 10.0644 | 60.3865 | 184.6483 | 228.9451 | 2435.072 | 3.9894 | 23.2921 | 1.2399 | 3.5827 | 0.040837 | 13.6218 | 12.2482 | 14.0946 | 13.1125 | 13.387 | 13.2514 | 12.589 | 13.1173 | 12.2557 | 13.9739 | 12.3661 | 13.4635 | 5.7833 | 4.9688 | 4.7661 | 4.9766 | 4.8828 | 4.2845 | 5.0305 | 4.1255 | 5.079 | 4.5617 | 5.4731 | 5.8231
Commercial EM-Retro-Supermarket |  | 66.3759 | 13.6535 | 2.7307 | 16.3842 | 50.0993 | 60.384 | 2162.3176 | 2.347 | 26.895 | 1.2053 | 0.92241 | 0.012478 | 4.1621 | 3.7424 | 4.3066 | 4.0065 | 4.0904 | 4.0489 | 3.8465 | 4.0079 | 3.7447 | 4.2697 | 3.7784 | 4.1137 | 1.7671 | 1.5182 | 1.4563 | 1.5206 | 1.4919 | 1.3091 | 1.5371 | 1.2605 | 1.5519 | 1.3938 | 1.6723 | 1.7792
Commercial EM-Retro-Lodging |  | 116.818 | 19.913 | 3.9826 | 23.8956 | 73.0675 | 83.4809 | 1791.8972 | 0.11658 | 31.737 | 1.1425 | 1.2131 | 0.02196 | 7.3251 | 6.5864 | 7.5793 | 7.0512 | 7.1988 | 7.1259 | 6.7697 | 7.0538 | 6.5905 | 7.5144 | 6.6498 | 7.2399 | 3.1099 | 2.672 | 2.563 | 2.6762 | 2.6257 | 2.304 | 2.7052 | 2.2185 | 2.7312 | 2.4531 | 2.9432 | 3.1313
Commercial EM-Retro-Assembly |  | 175.0492 | 42.2974 | 8.4595 | 50.7569 | 155.2033 | 167.1917 | 2540.0327 | 4.6214 | 33.2569 | 1.0772 | 2.5757 | 0.032907 | 10.9765 | 9.8696 | 11.3574 | 10.566 | 10.7873 | 10.678 | 10.1443 | 10.5699 | 9.8757 | 11.2602 | 9.9646 | 10.8489 | 4.6602 | 4.0039 | 3.8406 | 4.0102 | 3.9345 | 3.4524 | 4.0536 | 3.3244 | 4.0927 | 3.6758 | 4.4103 | 4.6922
Commercial EM-Retro-Large Off |  | 725.5086 | 158.1234 | 31.6247 | 189.7481 | 580.207 | 571.6665 | 2291.0727 | 3.1223 | 39.1624 | 0.98528 | 8.4917 | 0.13639 | 45.4931 | 40.9057 | 47.0719 | 43.792 | 44.709 | 44.2559 | 42.0439 | 43.8081 | 40.9308 | 46.6689 | 41.2994 | 44.9643 | 19.3145 | 16.5945 | 15.9176 | 16.6206 | 16.3071 | 14.309 | 16.8006 | 13.7782 | 16.9624 | 15.2349 | 18.2788 | 19.4474
Commercial EM-Retro-University |  | 876.3554 | 216.8218 | 43.3644 | 260.1862 | 795.5909 | 757.5473 | 2600.8064 | 4.9874 | 41.4905 | 0.95218 | 11.4638 | 0.16474 | 54.952 | 49.4107 | 56.8591 | 52.8972 | 54.0049 | 53.4575 | 50.7856 | 52.9166 | 49.4411 | 56.3722 | 49.8863 | 54.3132 | 23.3304 | 20.0448 | 19.2272 | 20.0764 | 19.6976 | 17.2841 | 20.2937 | 16.6429 | 20.4892 | 18.4025 | 22.0793 | 23.4909
Commercial EM-Retro-Xlarge Ret |  | 33.4823 | 9.8288 | 1.9658 | 11.7945 | 36.065 | 32.337 | 3085.8102 | 7.9078 | 46.489 | 0.89663 | 0.49909 | 0.0062942 | 2.0995 | 1.8878 | 2.1724 | 2.021 | 2.0633 | 2.0424 | 1.9403 | 2.0217 | 1.889 | 2.1538 | 1.906 | 2.0751 | 0.89137 | 0.76584 | 0.7346 | 0.76704 | 0.75257 | 0.66036 | 0.77535 | 0.63586 | 0.78282 | 0.70309 | 0.84357 | 0.8975
Commercial EM-Retro-Restaurant |  | 49.2585 | 13.1202 | 2.624 | 15.7443 | 48.1424 | 41.8035 | 2799.9157 | 6.1863 | 47.7652 | 0.86833 | 0.63038 | 0.0092599 | 3.0888 | 2.7773 | 3.196 | 2.9733 | 3.0355 | 3.0048 | 2.8546 | 2.9744 | 2.779 | 3.1686 | 2.804 | 3.0529 | 1.3114 | 1.1267 | 1.0807 | 1.1285 | 1.1072 | 0.97151 | 1.1407 | 0.93547 | 1.1517 | 1.0344 | 1.241 | 1.3204
Commercial EM-Retro-Medium Off |  | 90.2112 | 23.5813 | 4.7163 | 28.2976 | 86.5277 | 72.6452 | 2747.8526 | 5.8728 | 49.6197 | 0.83956 | 1.084 | 0.016958 | 5.6567 | 5.0863 | 5.853 | 5.4452 | 5.5592 | 5.5029 | 5.2278 | 5.4472 | 5.0894 | 5.8029 | 5.1352 | 5.5909 | 2.4016 | 2.0634 | 1.9792 | 2.0666 | 2.0277 | 1.7792 | 2.089 | 1.7132 | 2.1091 | 1.8943 | 2.2728 | 2.4181
Commercial EM-Retro-Warehouse |  | 29.0253 | 14.5926 | 2.9185 | 17.5111 | 53.5449 | 40.5298 | 5284.9367 | 21.1496 | 71.2908 | 0.75693 | 0.65765 | 0.0054564 | 1.82 | 1.6365 | 1.8832 | 1.752 | 1.7887 | 1.7705 | 1.682 | 1.7526 | 1.6375 | 1.8671 | 1.6523 | 1.7989 | 0.77271 | 0.66389 | 0.63681 | 0.66494 | 0.65239 | 0.57246 | 0.67214 | 0.55122 | 0.67861 | 0.6095 | 0.73128 | 0.77803
Commercial EM-Retro-School K-12 |  | 199.1614 | 82.3023 | 16.4605 | 98.7628 | 301.9945 | 202.6665 | 4344.0268 | 15.484 | 74.9938 | 0.67109 | 3.1545 | 0.03744 | 12.4884 | 11.2291 | 12.9218 | 12.0215 | 12.2732 | 12.1488 | 11.5416 | 12.0259 | 11.236 | 12.8112 | 11.3372 | 12.3433 | 5.3021 | 4.5554 | 4.3696 | 4.5626 | 4.4765 | 3.928 | 4.612 | 3.7823 | 4.6564 | 4.1822 | 5.0178 | 5.3386
Commercial EM-Retro-Medium Ret |  | 37.4593 | 15.3782 | 3.0756 | 18.4538 | 56.4276 | 31.1877 | 4315.4909 | 15.3122 | 87.8753 | 0.5527 | 0.46853 | 0.0070418 | 2.3489 | 2.112 | 2.4304 | 2.2611 | 2.3084 | 2.285 | 2.1708 | 2.2619 | 2.1133 | 2.4096 | 2.1324 | 2.3216 | 0.99725 | 0.8568 | 0.82186 | 0.85815 | 0.84196 | 0.7388 | 0.86745 | 0.71139 | 0.8758 | 0.78661 | 0.94377 | 1.0041
Commercial EM-Retro-Large Ret |  | 236.7305 | 143.7545 | 28.7509 | 172.5054 | 527.4829 | 228.5709 | 6383.4097 | 27.7639 | 131.2056 | 0.43332 | 3.5276 | 0.044502 | 14.8442 | 13.3474 | 15.3594 | 14.2892 | 14.5884 | 14.4405 | 13.7187 | 14.2944 | 13.3555 | 15.2279 | 13.4758 | 14.6717 | 6.3023 | 5.4147 | 5.1938 | 5.4232 | 5.3209 | 4.669 | 5.482 | 4.4958 | 5.5348 | 4.9711 | 5.9643 | 6.3456
Commercial EM-Retro-Small Off |  | 24.7007 | 16.1766 | 3.2353 | 19.412 | 59.3575 | 18.9174 | 6884.3814 | 30.7805 | 158.7645 | 0.3187 | 0.27929 | 0.0046434 | 1.5489 | 1.3927 | 1.6026 | 1.4909 | 1.5222 | 1.5067 | 1.4314 | 1.4915 | 1.3935 | 1.5889 | 1.4061 | 1.5309 | 0.65758 | 0.56498 | 0.54193 | 0.56587 | 0.55519 | 0.48716 | 0.57199 | 0.46909 | 0.5775 | 0.51869 | 0.62232 | 0.66211

## Measure InputOutput
Data Set Name
Measure Index Name | Commercial EM
Costs must be denominated in the same year as 'Input Cost Reference Year' = |  | 2012
| Savings per 1000 sf of floor area | 1000
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
Input Data | [7 empty] | Periodic Replacement Costs and Savings and Replacement Period | [5 empty] | Gas Inputs |  | Retro or LO | Early Retrofit Parameters
Category Name | Measure Name | Savings (kwh/yr) | Life (yrs) | Capital Cost | Annual O&M | Shape Pointer | Non-E Val ($/yr) | Cost 1 ($) | Period 1 | Cost 2 ($) | Period 2 | Cost 3 ($) | Period 3 | Savings (therms/yr) | Shape Pointer | R or L | Savings 2 (kWh) | Remaining Life (yrs) | Salvage Value ($)
Commercial EM-Retro-Large Off | Commercial EM-Retro-Large Off-GasHt | 325.5954 | 5 | 85.4452 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 13.5337 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Medium Off | Commercial EM-Retro-Medium Off-GasHt | 37.2926 | 5 | 12.1279 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 1.9209 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Small Off | Commercial EM-Retro-Small Off-GasHt | 5.9285 | 5 | 5.2985 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0.37766 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Xlarge Ret | Commercial EM-Retro-Xlarge Ret-GasHt | 27.6862 | 5 | 9.0038 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 1.5318 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Large Ret | Commercial EM-Retro-Large Ret-GasHt | 215.2309 | 5 | 141.3428 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 10.8206 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Medium Ret | Commercial EM-Retro-Medium Ret-GasHt | 26.3853 | 5 | 12.454 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0.95342 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Small Ret | Commercial EM-Retro-Small Ret-GasHt | 71.1826 | 5 | 14.4424 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 2.457 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-School K-12 | Commercial EM-Retro-School K-12-GasHt | 143.2053 | 5 | 69.7741 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 10.6832 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-University | Commercial EM-Retro-University-GasHt | 585.688 | 5 | 173.4574 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 26.5583 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Warehouse | Commercial EM-Retro-Warehouse-GasHt | 26.2232 | 5 | 14.4029 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 3.2318 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Supermarket | Commercial EM-Retro-Supermarket-GasHt | 47.0726 | 5 | 11.2262 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 2.4696 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-MiniMart | Commercial EM-Retro-MiniMart-GasHt | 0 | 5 | 0 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Restaurant | Commercial EM-Retro-Restaurant-GasHt | 34.815 | 5 | 10.4129 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 1.3744 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Lodging | Commercial EM-Retro-Lodging-GasHt | 18.6335 | 5 | 4.9667 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0.87408 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Hospital | Commercial EM-Retro-Hospital-GasHt | 1319.0104 | 5 | 216.5495 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 57.1657 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Residential Care | Commercial EM-Retro-Residential Care-GasHt | 44.5184 | 5 | 8.6207 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 2.2757 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Assembly | Commercial EM-Retro-Assembly-GasHt | 111.3777 | 5 | 32.9139 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 7.7234 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Other | Commercial EM-Retro-Other-GasHt | 123.5787 | 5 | 36.5195 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 12.8541 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Large Off | Commercial EM-Retro-Large Off-ElecHt | 172.4784 | 5 | 33.1162 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Medium Off | Commercial EM-Retro-Medium Off-ElecHt | 23.3419 | 5 | 5.2188 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Small Off | Commercial EM-Retro-Small Off-ElecHt | 8.6636 | 5 | 4.9567 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Xlarge Ret | Commercial EM-Retro-Xlarge Ret-ElecHt | 2.3297 | 5 | 0.52088 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Large Ret | Commercial EM-Retro-Large Ret-ElecHt | 3.3775 | 5 | 1.5228 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Medium Ret | Commercial EM-Retro-Medium Ret-ElecHt | 5.6842 | 5 | 1.8463 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Small Ret | Commercial EM-Retro-Small Ret-ElecHt | 49.1453 | 5 | 6.9591 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-School K-12 | Commercial EM-Retro-School K-12-ElecHt | 19.0832 | 5 | 4.8039 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-University | Commercial EM-Retro-University-ElecHt | 129.1959 | 5 | 21.6822 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Warehouse | Commercial EM-Retro-Warehouse-ElecHt | 0.46323 | 5 | 0.093289 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Supermarket | Commercial EM-Retro-Supermarket-ElecHt | 6.4604 | 5 | 0.93675 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-MiniMart | Commercial EM-Retro-MiniMart-ElecHt | 0 | 5 | 0 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Restaurant | Commercial EM-Retro-Restaurant-ElecHt | 1.8272 | 5 | 0.39427 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Lodging | Commercial EM-Retro-Lodging-ElecHt | 58.9041 | 5 | 8.897 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Hospital | Commercial EM-Retro-Hospital-ElecHt | 189.0603 | 5 | 19.0373 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Residential Care | Commercial EM-Retro-Residential Care-ElecHt | 60.7411 | 5 | 7.224 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Assembly | Commercial EM-Retro-Assembly-ElecHt | 28.1412 | 5 | 4.5005 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Other | Commercial EM-Retro-Other-ElecHt | 53.3014 | 5 | 8.5243 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Large Off | Commercial EM-Retro-Large Off-HtPmpHt | 176.9464 | 5 | 39.5619 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Medium Off | Commercial EM-Retro-Medium Off-HtPmpHt | 23.2988 | 5 | 6.2346 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Small Off | Commercial EM-Retro-Small Off-HtPmpHt | 8.3897 | 5 | 5.9214 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Xlarge Ret | Commercial EM-Retro-Xlarge Ret-HtPmpHt | 1.1363 | 5 | 0.30407 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Large Ret | Commercial EM-Retro-Large Ret-HtPmpHt | 1.6479 | 5 | 0.88895 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Medium Ret | Commercial EM-Retro-Medium Ret-HtPmpHt | 2.783 | 5 | 1.0778 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Small Ret | Commercial EM-Retro-Small Ret-HtPmpHt | 24.2064 | 5 | 4.0624 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-School K-12 | Commercial EM-Retro-School K-12-HtPmpHt | 23.0131 | 5 | 7.7243 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-University | Commercial EM-Retro-University-HtPmpHt | 100.4857 | 5 | 21.6822 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Warehouse | Commercial EM-Retro-Warehouse-HtPmpHt | 0.31898 | 5 | 0.096359 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Supermarket | Commercial EM-Retro-Supermarket-HtPmpHt | 8.2238 | 5 | 1.4906 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-MiniMart | Commercial EM-Retro-MiniMart-HtPmpHt | 0 | 5 | 0 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Restaurant | Commercial EM-Retro-Restaurant-HtPmpHt | 9.1884 | 5 | 2.313 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Lodging | Commercial EM-Retro-Lodging-HtPmpHt | 31.1509 | 5 | 6.0494 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Hospital | Commercial EM-Retro-Hospital-HtPmpHt | 18.906 | 5 | 2.3797 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Residential Care | Commercial EM-Retro-Residential Care-HtPmpHt | 36.5428 | 5 | 5.4113 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Assembly | Commercial EM-Retro-Assembly-HtPmpHt | 23.3486 | 5 | 4.883 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-Retro-Other | Commercial EM-Retro-Other-HtPmpHt | 25.2384 | 5 | 5.2782 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
ProCost Results
Version: | ProCost 3.0 - Beta04
Run Time: | Thursday, 19 March , 2015 at 9:18 AM
Regurgitation of ProData input parameters which were used for this run
| Run Parameters |  | Run Parameters |  |  | Marginal Cost & Conservation Load Shape Parameters | [9 empty] | Sponsor Parameters | [5 empty] | Program Parameters |  |  | Utility System Parameters
| Run Type | Electric | Run Type | Electric |  | Marginal Costs and Savings Shape File | Q:\SeventhPlan\Conservation Analysis\Global EE Inputs\MC Files\MC_AND_LOADSHAPE_v3.0_24segment-7P-D9 - NewSegValues.xlsx |  |  | 6P MidC Final (with carbon) | [6 empty] | Customer | Wholesale Elec | Retail Elec | Nat Gas |  | Program Life (yrs) | 20 |  |  | Electric | Gas
| Negative B/C Ratios | Off | Negative B/C Ratios | Off |  | Marginal Elec Avoided Cost Input Worksheet | 7P Mid |  |  | Conservation Load Shapes | [5 empty] | Real After-Tax Cost of Capital | 0.068013 | 0.043878 | 0.053289 | 0.054479 |  | Program Start Date | 2016 |  | Bulk System T&D Loss Factor | 0.0040389 | 0.01
| Admin Cost @ Category Level | On | Admin Cost @ Category Level | On |  | Elec Savings Shape Input Worksheet | GLSShapes |  |  | 6P_Gas_Final | [5 empty] | Financial Life (years) | 12 | 12 | 1 | 1 |  | Present Value Time Zero | 2016 |  | Bulk System T&D Credit ($/kw-yr)($/dailytherm-yr) | 26 | 0
| Repeat Periodic Replacement | On | Repeat Periodic Replacement | On |  | Marginal Gas Avoided Cost Input Worksheet | 7P Gas |  |  | Conservation Load Shapes | [6 empty] | Customer | Wholesale Elec | Retail Elec | Nat Gas |  | Input Cost Reference Year | 2012 |  | Bulk System T&D I2R Loss Component (%) | 0.9 | N/A
[6 empty] | Gas Savings Shape Input Worksheet | GLSShapes | [8 empty] | Sponsor Share of Initial Capital Cost | 0.35 | 0.195 | 0.455 | 0 |  | Real Discount Rate | 0.04 |  | Local System Dist Loss Factor | 0.047399 | 0
| Run Type: | Electric |  |  |  | Marginal Elec CO2 per kWh Input Worksheet | CO2 lbs per kWh .95 |  |  | CO2 lbs per therm | [5 empty] | Sponsor Share of Annual O&M | 1 | 0 | 0 | 0 |  | Capital Real Escalation Rate | 0 |  | Local System Dist Credit ($/kw-yr)($/dailytherm-yr) | 31 | 0
| Negative B/C Ratios: | False: (Converts Negative B/C Ratios) |  |  |  | Marginal Gas CO2 per therm Input Worksheet | CO2 lbs per therm |  |  | Zero Dollars per ton CO2 | [5 empty] | Sponsor Share of Periodic Replacement Cost | 1 | 0 | 0 | 0 |  | Admin Cost (as % of Initial Capital Cost) | 0.2 |  | Local System Dist I2R Loss Component (%) | 0.7 | N/A
| Admin Cost / Category Level: | True: Admin Costs added at Category Results |  |  |  | Marginal Avoided Cost CO2 Input Worksheet | Zero Dollars per ton CO2 |  |  | LineLossShapes | [5 empty] | Sponsor Share of Admin Cost |  | 0.3 | 0.7 | 0 |  | Regional Act Conservation Credit (%) | 0 |  | Risk-Mitigation Credit (mills/kWh)(mills/therm) - Retro. | 0 | 0
| Periodic O&M Treatment: | True: (Periodic O&M Repeats over measure life) |  |  |  | Line Loss Shape Input Worksheet | LineLossShapes | [8 empty] | Last Year of Non-Customer O&M & Period Replacement |  | 20 |  |  |  | Report Annual Carbon Saved for Year | 2018 |  | Risk-Mitigation Credit (mills/kWh)(mills/therm) - Lost Op. | 0 | 0
Measure Results; Sorted in same order as input
Total Results |  | Measure Input Data | [8 empty] | Savings | [5 empty] | PV Capital |  |  |  | PV Admin |  |  |  | PV O&M |  |  |  | PV Periodic Repl. |  |  |  | Total PV Capital, O&M and Periodic Repl Costs |  |  |  |  | PV Wholesale Electric Utility Costs & Benefits | [6 empty] | PV Retail Electric Utility Costs & Benefits | [6 empty] | PV Electric Utility System Costs & Benefits | [5 empty] | Electric Utility System Economics |  | Sponsor Levelized Cost (mills/kwh) |  |  |  |  | PV Regional Costs & Benefits | [15 empty] | TRC Economics |  | Physical CO2 | [5 empty] | Gas Inputs |  |  |  | PV Gas Utility System Costs & Benefits |  |  |  |  | Gas Utility System Economics
Category | Measure | Measure Life | Site Savings (kWh) | Site Savings (therms) | Capital Cost ($/unit) | Annual O&M Cost ($/unit) | PV Per. Repl. Cost ($/unit) | Load Shape (electric) | Diversified Load Factor (electric) | Wholesale Power Coincidence Factor (electric) | Wholesale Electric Energy (kWh) | Wholesale Electric Demand (kw) | Retail Electric Demand (kW) | Wholesale Gas Energy (therms/yr) | Wholesale Gas Demand (therms/day) | Retail Gas Demand (therms/day) | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Total | Wholesale Utility System Energy | Wholesale Utility System T&D Def. Cap. | Wholesale Utility System Act C-E Credit | Wholesale Utility System Risk Mitigation Benefit | Wholesale Utility System Total System Benefit | Wholesale Utility System Total Non-Consumer Cost | Wholesale Utility System B/C Ratio | Retail Utility System Energy | Retail Utility System T&D Def. Cap. | Retail Utility System Act C-E Credit | Retail Utility System Risk Mitigation Benefit | Retail Utility System Total System Benefit | Retail Utility System Total Non-Consumer Cost | Retail Utility System System B/C Ratio | Utility System Energy | Utility System T&D Def. Cap. | Utility System Act C-E Credit | Utility System Total Risk Mitigation Benefit | Utility System Total System Benefit | Utility System Total Non-Consumer Cost | Utility System Net Levelized Cost (Net of Elec T&D Capacity Benefits, Act Credit & Risk-Mitigation Benefit) in mills/kwh | Utility System System B/C Ratio | Wholesale Electric Levelized Cost | Retail Electric Levelized Cost | Natural Gas Levelized Cost | Customer Levelized Cost | Total Levelized Cost | PV Regional Electric Energy | PV Regional Gas Energy | PV Regional Electric T&D Def. Cap. | PV Regional Gas T&D Def. Cap. | PV Regional Electric System CO2 | PV Regional Gas System CO2 | PV Regional Electric System Risk-Mitigation Benefit | PV Regional Gas System Risk-Mitigation Benefit | PV Regional Non-E Value | PV Regional Act Credit | PV Regional Capital Cost | PV Regional Admin Cost | PV Regional Annual O&M Cost | PV Regional Periodic Replacement Cost | PV Total Regional Benefit | PV Total Regional Cost | TRC B/C Ratio | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | Electric System CO2 Avoided (Lifetime Tons) | Gas System CO2 Avoided (Lifetime Tons) | Total System CO2 Avoided (Lifetime Tons) | Electric System CO2 Avoided (Annual Tons in 2018) | Gas System CO2 Avoided (Annual Tons in 2018) | Total System CO2 Avoided (Annual Tons in 2018) | Gas Site Savings (therms) | Load Shape (gas) | Diversitfied Load Factor (gas) | Wholesale Coincidence Factor (gas) | Total Gas Utility System Energy | Gas Utility System T&D Def. Cap. | Gas Utility System Risk Mitigation Benefit | Gas Utility System Total System Benefit | Gas Utility System Total Non-Consumer Cost | Gas Utility System Net Levelized Cost (Net of Gas T&D Capacity Benefits & Risk-Mitigation Benefits) in cents/therm | Gas Utility System System B/C Ratio
Commercial EM-Retro-Large Off | Commercial EM-Retro-Large Off-GasHt | 5 | 325.5954 | 13.5337 | 85.4452 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 349.9484 | 0.065786 | 0.065311 | 13.6691 | 0 | 0 | 17.0389 | 39.3744 | 0 | 240.0245 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.0389 | 39.3744 | 0 | 240.0245 | 296.4377 | 182.1336 | 23.2452 | 0 | 0 | 205.3789 | 17.0389 | 12.0535 | 182.1336 | 27.5154 | 0 | 0 | 209.649 | 39.3744 | 5.3245 | 182.1336 | 50.7606 | 0 | 0 | 232.8943 | 56.4133 | 1.1885 | 4.1284 | 3.5827 | 8.279 | 0 | 50.4686 | 62.3303 | 182.1336 | 88.8331 | 50.7606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296.4377 |  | 0 | 0 | 321.7273 | 296.4377 | 1.0853 | 32.9787 | 3.3245 | 1.5993 | 4.9238 | 0.16623 | 0.079964 | 0.24619 | 13.5337 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 88.8331 | 0 | 0 | 88.8331 | 0 | 0 | 9999
Commercial EM-Retro-Medium Off | Commercial EM-Retro-Medium Off-GasHt | 5 | 37.2926 | 1.9209 | 12.1279 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 40.0819 | 0.0075349 | 0.0074805 | 1.9402 | 0 | 0 | 2.4185 | 5.5887 | 0 | 34.0685 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4185 | 5.5887 | 0 | 34.0685 | 42.0757 | 20.861 | 2.6624 | 0 | 0 | 23.5234 | 2.4185 | 9.7266 | 20.861 | 3.1515 | 0 | 0 | 24.0125 | 5.5887 | 4.2966 | 20.861 | 5.814 | 0 | 0 | 26.6749 | 8.0072 | 4.0263 | 3.3314 | 4.4398 | 10.2597 | 0 | 62.5425 | 77.2419 | 20.861 | 12.6088 | 5.814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.0757 |  | 0 | 0 | 39.2837 | 42.0757 | 0.93364 | 43.4218 | 0.38078 | 0.227 | 0.60778 | 0.019039 | 0.01135 | 0.030389 | 1.9209 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 12.6088 | 0 | 0 | 12.6088 | 0 | 0 | 9999
Commercial EM-Retro-Small Off | Commercial EM-Retro-Small Off-GasHt | 5 | 5.9285 | 0.37766 | 5.2985 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 6.3719 | 0.0011978 | 0.0011892 | 0.38143 | 0 | 0 | 1.0566 | 2.4416 | 0 | 14.8841 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0566 | 2.4416 | 0 | 14.8841 | 18.3823 | 3.3163 | 0.42325 | 0 | 0 | 3.7396 | 1.0566 | 3.5393 | 3.3163 | 0.50101 | 0 | 0 | 3.8173 | 2.4416 | 1.5634 | 3.3163 | 0.92426 | 0 | 0 | 4.2406 | 3.4982 | 29.7237 | 1.2122 | 12.2014 | 28.1955 | 0 | 171.8787 | 212.2756 | 3.3163 | 2.4789 | 0.92426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.3823 |  | 0 | 0 | 6.7195 | 18.3823 | 0.36554 | 172.9769 | 0.060534 | 0.044628 | 0.10516 | 0.0030267 | 0.0022314 | 0.0052581 | 0.37766 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 2.4789 | 0 | 0 | 2.4789 | 0 | 0 | 9999
Commercial EM-Retro-Xlarge Ret | Commercial EM-Retro-Xlarge Ret-GasHt | 5 | 27.6862 | 1.5318 | 9.0038 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 29.757 | 0.0055939 | 0.0055535 | 1.5471 | 0 | 0 | 1.7955 | 4.1491 | 0 | 25.2926 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7955 | 4.1491 | 0 | 25.2926 | 31.2372 | 15.4873 | 1.9766 | 0 | 0 | 17.4639 | 1.7955 | 9.7266 | 15.4873 | 2.3397 | 0 | 0 | 17.827 | 4.1491 | 4.2966 | 15.4873 | 4.3163 | 0 | 0 | 19.8036 | 5.9446 | 4.0263 | 3.3314 | 4.4398 | 10.2597 | 0 | 62.5425 | 77.2419 | 15.4873 | 10.0542 | 4.3163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.2372 |  | 0 | 0 | 29.8578 | 31.2372 | 0.95584 | 41.7072 | 0.28269 | 0.18101 | 0.4637 | 0.014135 | 0.0090504 | 0.023185 | 1.5318 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 10.0542 | 0 | 0 | 10.0542 | 0 | 0 | 9999
Commercial EM-Retro-Large Ret | Commercial EM-Retro-Large Ret-GasHt | 5 | 215.2309 | 10.8206 | 141.3428 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 231.3292 | 0.043487 | 0.043173 | 10.9288 | 0 | 0 | 28.1856 | 65.1327 | 0 | 397.0464 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.1856 | 65.1327 | 0 | 397.0464 | 490.3648 | 120.3972 | 15.366 | 0 | 0 | 135.7632 | 28.1856 | 4.8168 | 120.3972 | 18.1887 | 0 | 0 | 138.586 | 65.1327 | 2.1277 | 120.3972 | 33.5547 | 0 | 0 | 153.9519 | 93.3184 | 19.0098 | 1.6497 | 8.9654 | 20.7176 | 0 | 126.2935 | 155.9764 | 120.3972 | 71.0243 | 33.5547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490.3648 |  | 0 | 0 | 224.9763 | 490.3648 | 0.45879 | 122.7117 | 2.1976 | 1.2787 | 3.4763 | 0.10988 | 0.063933 | 0.17381 | 10.8206 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 71.0243 | 0 | 0 | 71.0243 | 0 | 0 | 9999
Commercial EM-Retro-Medium Ret | Commercial EM-Retro-Medium Ret-GasHt | 5 | 26.3853 | 0.95342 | 12.454 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 28.3588 | 0.0053311 | 0.0052926 | 0.96296 | 0 | 0 | 2.4835 | 5.739 | 0 | 34.9846 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4835 | 5.739 | 0 | 34.9846 | 43.2071 | 14.7596 | 1.8837 | 0 | 0 | 16.6433 | 2.4835 | 6.7016 | 14.7596 | 2.2298 | 0 | 0 | 16.9894 | 5.739 | 2.9603 | 14.7596 | 4.1135 | 0 | 0 | 18.8731 | 8.2225 | 10.6614 | 2.2953 | 6.4438 | 14.8908 | 0 | 90.7735 | 112.1081 | 14.7596 | 6.2581 | 4.1135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.2071 |  | 0 | 0 | 25.1312 | 43.2071 | 0.58165 | 85.1972 | 0.26941 | 0.11267 | 0.38208 | 0.01347 | 0.0056333 | 0.019104 | 0.95342 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 6.2581 | 0 | 0 | 6.2581 | 0 | 0 | 9999
Commercial EM-Retro-Small Ret | Commercial EM-Retro-Small Ret-GasHt | 5 | 71.1826 | 2.457 | 14.4424 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 76.5067 | 0.014382 | 0.014278 | 2.4816 | 0 | 0 | 2.88 | 6.6552 | 0 | 40.5701 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.88 | 6.6552 | 0 | 40.5701 | 50.1053 | 39.8186 | 5.0819 | 0 | 0 | 44.9005 | 2.88 | 15.5905 | 39.8186 | 6.0155 | 0 | 0 | 45.8341 | 6.6552 | 6.8869 | 39.8186 | 11.0974 | 0 | 0 | 50.916 | 9.5352 | -1.5025 | 5.3398 | 2.7699 | 6.4008 | 0 | 39.019 | 48.1897 | 39.8186 | 16.1272 | 11.0974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.1053 |  | 0 | 0 | 67.0432 | 50.1053 | 1.338 | 22.0059 | 0.72682 | 0.29034 | 1.0172 | 0.036341 | 0.014517 | 0.050858 | 2.457 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 16.1272 | 0 | 0 | 16.1272 | 0 | 0 | 9999
Commercial EM-Retro-School K-12 | Commercial EM-Retro-School K-12-GasHt | 5 | 143.2053 | 10.6832 | 69.7741 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 153.9164 | 0.028934 | 0.028725 | 10.79 | 0 | 0 | 13.9139 | 32.1529 | 0 | 196.0027 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.9139 | 32.1529 | 0 | 196.0027 | 242.0694 | 80.1071 | 10.2239 | 0 | 0 | 90.331 | 13.9139 | 6.4921 | 80.1071 | 12.102 | 0 | 0 | 92.2091 | 32.1529 | 2.8678 | 80.1071 | 22.3258 | 0 | 0 | 102.433 | 46.0668 | 11.3497 | 2.2236 | 6.6517 | 15.3711 | 0 | 93.7016 | 115.7244 | 80.1071 | 70.1226 | 22.3258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242.0694 |  | 0 | 0 | 172.5555 | 242.0694 | 0.71283 | 71.5283 | 1.4622 | 1.2624 | 2.7247 | 0.07311 | 0.063122 | 0.13623 | 10.6832 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 70.1226 | 0 | 0 | 70.1226 | 0 | 0 | 9999
Commercial EM-Retro-University | Commercial EM-Retro-University-GasHt | 5 | 585.688 | 26.5583 | 173.4574 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 629.4948 | 0.11834 | 0.11748 | 26.8238 | 0 | 0 | 34.5897 | 79.9316 | 0 | 487.2599 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.5897 | 79.9316 | 0 | 487.2599 | 601.7812 | 327.6259 | 41.814 | 0 | 0 | 369.4399 | 34.5897 | 10.6806 | 327.6259 | 49.4953 | 0 | 0 | 377.1212 | 79.9316 | 4.718 | 327.6259 | 91.3093 | 0 | 0 | 418.9352 | 114.5213 | 2.7133 | 3.6581 | 4.0432 | 9.3432 | 0 | 56.9559 | 70.3423 | 327.6259 | 174.3238 | 91.3093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 601.7812 |  | 0 | 0 | 593.259 | 601.7812 | 0.98584 | 39.2924 | 5.9803 | 3.1384 | 9.1186 | 0.29901 | 0.15692 | 0.45593 | 26.5583 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 174.3238 | 0 | 0 | 174.3238 | 0 | 0 | 9999
Commercial EM-Retro-Warehouse | Commercial EM-Retro-Warehouse-GasHt | 5 | 26.2232 | 3.2318 | 14.4029 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 28.1846 | 0.0052983 | 0.0052601 | 3.2641 | 0 | 0 | 2.8721 | 6.6371 | 0 | 40.4593 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8721 | 6.6371 | 0 | 40.4593 | 49.9685 | 14.6689 | 1.8722 | 0 | 0 | 16.5411 | 2.8721 | 5.7592 | 14.6689 | 2.2161 | 0 | 0 | 16.885 | 6.6371 | 2.544 | 14.6689 | 4.0882 | 0 | 0 | 18.7571 | 9.5092 | 14.1526 | 1.9725 | 7.4983 | 17.3274 | 0 | 105.6273 | 130.453 | 14.6689 | 21.2131 | 4.0882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.9685 |  | 0 | 0 | 39.9703 | 49.9685 | 0.79991 | 64.3986 | 0.26776 | 0.3819 | 0.64966 | 0.013388 | 0.019095 | 0.032483 | 3.2318 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 21.2131 | 0 | 0 | 21.2131 | 0 | 0 | 9999
Commercial EM-Retro-Supermarket | Commercial EM-Retro-Supermarket-GasHt | 5 | 47.0726 | 2.4696 | 11.2262 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 50.5934 | 0.0095109 | 0.0094422 | 2.4943 | 0 | 0 | 2.2387 | 5.1732 | 0 | 31.5356 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2387 | 5.1732 | 0 | 31.5356 | 38.9474 | 26.3318 | 3.3607 | 0 | 0 | 29.6924 | 2.2387 | 13.2635 | 26.3318 | 3.978 | 0 | 0 | 30.3098 | 5.1732 | 5.859 | 26.3318 | 7.3387 | 0 | 0 | 33.6704 | 7.4118 | 0.10643 | 4.5428 | 3.2558 | 7.5238 | 0 | 45.8645 | 56.6441 | 26.3318 | 16.2102 | 7.3387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.9474 |  | 0 | 0 | 49.8806 | 38.9474 | 1.2807 | 22.3953 | 0.48064 | 0.29184 | 0.77248 | 0.024032 | 0.014592 | 0.038624 | 2.4696 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 16.2102 | 0 | 0 | 16.2102 | 0 | 0 | 9999
Commercial EM-Retro-MiniMart | Commercial EM-Retro-MiniMart-GasHt | 5 | 0 | 0 | 0 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Restaurant | Commercial EM-Retro-Restaurant-GasHt | 5 | 34.815 | 1.3744 | 10.4129 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 37.419 | 0.0070343 | 0.0069835 | 1.3882 | 0 | 0 | 2.0765 | 4.7984 | 0 | 29.2509 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0765 | 4.7984 | 0 | 29.2509 | 36.1258 | 19.475 | 2.4855 | 0 | 0 | 21.9606 | 2.0765 | 10.5759 | 19.475 | 2.9421 | 0 | 0 | 22.4172 | 4.7984 | 4.6718 | 19.475 | 5.4277 | 0 | 0 | 24.9027 | 6.8749 | 2.8458 | 3.6223 | 4.0832 | 9.4357 | 0 | 57.5198 | 71.0388 | 19.475 | 9.0215 | 5.4277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.1258 |  | 0 | 0 | 33.9242 | 36.1258 | 0.93906 | 42.6255 | 0.35548 | 0.16242 | 0.5179 | 0.017774 | 0.0081208 | 0.025895 | 1.3744 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 9.0215 | 0 | 0 | 9.0215 | 0 | 0 | 9999
Commercial EM-Retro-Lodging | Commercial EM-Retro-Lodging-GasHt | 5 | 18.6335 | 0.87408 | 4.9667 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 20.0272 | 0.0037648 | 0.0037377 | 0.88282 | 0 | 0 | 0.99042 | 2.2887 | 0 | 13.9519 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99042 | 2.2887 | 0 | 13.9519 | 17.231 | 10.4233 | 1.3303 | 0 | 0 | 11.7536 | 0.99042 | 11.8674 | 10.4233 | 1.5747 | 0 | 0 | 11.998 | 2.2887 | 5.2423 | 10.4233 | 2.905 | 0 | 0 | 13.3283 | 3.2791 | 1.3746 | 4.0646 | 3.6389 | 8.4089 | 0 | 51.2603 | 63.3081 | 10.4233 | 5.7373 | 2.905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.231 |  | 0 | 0 | 19.0656 | 17.231 | 1.1065 | 31.5555 | 0.19026 | 0.10329 | 0.29355 | 0.0095129 | 0.0051645 | 0.014677 | 0.87408 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 5.7373 | 0 | 0 | 5.7373 | 0 | 0 | 9999
Commercial EM-Retro-Hospital | Commercial EM-Retro-Hospital-GasHt | 5 | 1319.0104 | 57.1657 | 216.5495 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1417.6661 | 0.2665 | 0.26458 | 57.7374 | 0 | 0 | 43.1829 | 99.789 | 0 | 608.3099 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.1829 | 99.789 | 0 | 608.3099 | 751.2817 | 737.8363 | 94.168 | 0 | 0 | 832.0044 | 43.1829 | 19.267 | 737.8363 | 111.4669 | 0 | 0 | 849.3033 | 99.789 | 8.511 | 737.8363 | 205.635 | 0 | 0 | 943.4713 | 142.9719 | -3.2524 | 6.599 | 2.2413 | 5.1794 | 0 | 31.5734 | 38.9941 | 737.8363 | 375.2259 | 205.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 751.2817 |  | 0 | 0 | 1318.6972 | 751.2817 | 1.7553 | 8.8454 | 13.468 | 6.7553 | 20.2232 | 0.67339 | 0.33776 | 1.0112 | 57.1657 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 375.2259 | 0 | 0 | 375.2259 | 0 | 0 | 9999
Commercial EM-Retro-Residential Care | Commercial EM-Retro-Residential Care-GasHt | 5 | 44.5184 | 2.2757 | 8.6207 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 47.8482 | 0.0089948 | 0.0089299 | 2.2985 | 0 | 0 | 1.7191 | 3.9725 | 0 | 24.2164 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7191 | 3.9725 | 0 | 24.2164 | 29.908 | 24.903 | 3.1783 | 0 | 0 | 28.0813 | 1.7191 | 16.3351 | 24.903 | 3.7622 | 0 | 0 | 28.6651 | 3.9725 | 7.2158 | 24.903 | 6.9405 | 0 | 0 | 31.8434 | 5.6916 | -1.9205 | 5.5948 | 2.6436 | 6.109 | 0 | 37.2404 | 45.993 | 24.903 | 14.9375 | 6.9405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.908 |  | 0 | 0 | 46.7809 | 29.908 | 1.5642 | 12.3488 | 0.45456 | 0.26892 | 0.72348 | 0.022728 | 0.013446 | 0.036174 | 2.2757 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 14.9375 | 0 | 0 | 14.9375 | 0 | 0 | 9999
Commercial EM-Retro-Assembly | Commercial EM-Retro-Assembly-GasHt | 5 | 111.3777 | 7.7234 | 32.9139 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 119.7082 | 0.022504 | 0.022341 | 7.8006 | 0 | 0 | 6.5635 | 15.1672 | 0 | 92.4586 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5635 | 15.1672 | 0 | 92.4586 | 114.1893 | 62.3031 | 7.9516 | 0 | 0 | 70.2547 | 6.5635 | 10.7039 | 62.3031 | 9.4123 | 0 | 0 | 71.7155 | 15.1672 | 4.7283 | 62.3031 | 17.3639 | 0 | 0 | 79.667 | 21.7307 | 2.6842 | 3.6661 | 4.0344 | 9.3229 | 0 | 56.8321 | 70.1894 | 62.3031 | 50.6947 | 17.3639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.1893 |  | 0 | 0 | 130.3617 | 114.1893 | 1.1416 | 28.3554 | 1.1372 | 0.91267 | 2.0499 | 0.056861 | 0.045633 | 0.10249 | 7.7234 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 50.6947 | 0 | 0 | 50.6947 | 0 | 0 | 9999
Commercial EM-Retro-Other | Commercial EM-Retro-Other-GasHt | 5 | 123.5787 | 12.8541 | 36.5195 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 132.8218 | 0.024969 | 0.024788 | 12.9827 | 0 | 0 | 7.2825 | 16.8287 | 0 | 102.5871 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2825 | 16.8287 | 0 | 102.5871 | 126.6983 | 69.1282 | 8.8226 | 0 | 0 | 77.9509 | 7.2825 | 10.7039 | 69.1282 | 10.4434 | 0 | 0 | 79.5716 | 16.8287 | 4.7283 | 69.1282 | 19.266 | 0 | 0 | 88.3943 | 24.1112 | 2.6842 | 3.6661 | 4.0344 | 9.3229 | 0 | 56.8321 | 70.1894 | 69.1282 | 84.3722 | 19.266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.6983 |  | 0 | 0 | 172.7665 | 126.6983 | 1.3636 | 12.775 | 1.2618 | 1.519 | 2.7808 | 0.06309 | 0.075949 | 0.13904 | 12.8541 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 84.3722 | 0 | 0 | 84.3722 | 0 | 0 | 9999
Commercial EM-Retro-Large Off | Commercial EM-Retro-Large Off-ElecHt | 5 | 172.4784 | 0 | 33.1162 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 185.379 | 0.034849 | 0.034597 | 0 | 0 | 0 | 6.6038 | 15.2604 | 0 | 93.0269 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6038 | 15.2604 | 0 | 93.0269 | 114.8911 | 96.4821 | 12.3137 | 0 | 0 | 108.7958 | 6.6038 | 16.4747 | 96.4821 | 14.5758 | 0 | 0 | 111.0579 | 15.2604 | 7.2775 | 96.4821 | 26.8896 | 0 | 0 | 123.3716 | 21.8642 | -1.9947 | 5.6426 | 2.6212 | 6.0573 | 0 | 36.9248 | 45.6033 | 96.4821 | 0 | 26.8896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.8911 |  | 0 | 0 | 123.3716 | 114.8911 | 1.0738 | 34.9301 | 1.7611 | 0 | 1.7611 | 0.088055 | 0 | 0.088055 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Medium Off | Commercial EM-Retro-Medium Off-ElecHt | 5 | 23.3419 | 0 | 5.2188 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 25.0878 | 0.0047162 | 0.0046821 | 0 | 0 | 0 | 1.0407 | 2.4049 | 0 | 14.6602 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0407 | 2.4049 | 0 | 14.6602 | 18.1058 | 13.0572 | 1.6664 | 0 | 0 | 14.7236 | 1.0407 | 14.1478 | 13.0572 | 1.9726 | 0 | 0 | 15.0297 | 2.4049 | 6.2496 | 13.0572 | 3.639 | 0 | 0 | 16.6962 | 3.4456 | -0.5673 | 4.8456 | 3.0523 | 7.0535 | 0 | 42.998 | 53.1038 | 13.0572 | 0 | 3.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.1058 |  | 0 | 0 | 16.6962 | 18.1058 | 0.92214 | 42.4307 | 0.23834 | 0 | 0.23834 | 0.011917 | 0 | 0.011917 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Small Off | Commercial EM-Retro-Small Off-ElecHt | 5 | 8.6636 | 0 | 4.9567 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 9.3116 | 0.0017505 | 0.0017378 | 0 | 0 | 0 | 0.98843 | 2.2841 | 0 | 13.9238 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98843 | 2.2841 | 0 | 13.9238 | 17.1963 | 4.8463 | 0.61852 | 0 | 0 | 5.4648 | 0.98843 | 5.5288 | 4.8463 | 0.73214 | 0 | 0 | 5.5784 | 2.2841 | 2.4423 | 4.8463 | 1.3507 | 0 | 0 | 6.197 | 3.2725 | 15.187 | 1.8936 | 7.8107 | 18.0494 | 0 | 110.0284 | 135.8886 | 4.8463 | 0 | 1.3507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.1963 |  | 0 | 0 | 6.197 | 17.1963 | 0.36036 | 125.2154 | 0.088461 | 0 | 0.088461 | 0.004423 | 0 | 0.004423 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Xlarge Ret | Commercial EM-Retro-Xlarge Ret-ElecHt | 5 | 2.3297 | 0 | 0.52088 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 2.504 | 0.00047071 | 0.00046732 | 0 | 0 | 0 | 0.10387 | 0.24003 | 0 | 1.4632 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10387 | 0.24003 | 0 | 1.4632 | 1.8071 | 1.3032 | 0.16633 | 0 | 0 | 1.4695 | 0.10387 | 14.1478 | 1.3032 | 0.19688 | 0 | 0 | 1.5001 | 0.24003 | 6.2496 | 1.3032 | 0.36321 | 0 | 0 | 1.6664 | 0.3439 | -0.5673 | 4.8456 | 3.0523 | 7.0535 | 0 | 42.998 | 53.1038 | 1.3032 | 0 | 0.36321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8071 |  | 0 | 0 | 1.6664 | 1.8071 | 0.92214 | 42.4307 | 0.023788 | 0 | 0.023788 | 0.0011894 | 0 | 0.0011894 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Large Ret | Commercial EM-Retro-Large Ret-ElecHt | 5 | 3.3775 | 0 | 1.5228 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 3.6301 | 0.00068241 | 0.00067748 | 0 | 0 | 0 | 0.30367 | 0.70173 | 0 | 4.2777 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30367 | 0.70173 | 0 | 4.2777 | 5.2831 | 1.8893 | 0.24113 | 0 | 0 | 2.1304 | 0.30367 | 7.0157 | 1.8893 | 0.28542 | 0 | 0 | 2.1747 | 0.70173 | 3.0991 | 1.8893 | 0.52655 | 0 | 0 | 2.4159 | 1.0054 | 9.7062 | 2.4029 | 6.1553 | 14.224 | 0 | 86.709 | 107.0883 | 1.8893 | 0 | 0.52655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2831 |  | 0 | 0 | 2.4159 | 5.2831 | 0.45728 | 96.4151 | 0.034486 | 0 | 0.034486 | 0.0017243 | 0 | 0.0017243 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Medium Ret | Commercial EM-Retro-Medium Ret-ElecHt | 5 | 5.6842 | 0 | 1.8463 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 6.1093 | 0.0011485 | 0.0011402 | 0 | 0 | 0 | 0.36819 | 0.85082 | 0 | 5.1866 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36819 | 0.85082 | 0 | 5.1866 | 6.4056 | 3.1797 | 0.40581 | 0 | 0 | 3.5855 | 0.36819 | 9.7382 | 3.1797 | 0.48036 | 0 | 0 | 3.66 | 0.85082 | 4.3017 | 3.1797 | 0.88617 | 0 | 0 | 4.0658 | 1.219 | 4.0087 | 3.3354 | 4.4345 | 10.2474 | 0 | 62.4678 | 77.1496 | 3.1797 | 0 | 0.88617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4056 |  | 0 | 0 | 4.0658 | 6.4056 | 0.63473 | 66.4765 | 0.058039 | 0 | 0.058039 | 0.0029019 | 0 | 0.0029019 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Small Ret | Commercial EM-Retro-Small Ret-ElecHt | 5 | 49.1453 | 0 | 6.9591 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 52.8211 | 0.0099297 | 0.009858 | 0 | 0 | 0 | 1.3877 | 3.2068 | 0 | 19.5487 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3877 | 3.2068 | 0 | 19.5487 | 24.1433 | 27.4912 | 3.5086 | 0 | 0 | 30.9998 | 1.3877 | 22.3386 | 27.4912 | 4.1532 | 0 | 0 | 31.6444 | 3.2068 | 9.8678 | 27.4912 | 7.6618 | 0 | 0 | 35.153 | 4.5946 | -4.2728 | 7.651 | 1.9332 | 4.4672 | 0 | 27.232 | 33.6324 | 27.4912 | 0 | 7.6618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.1433 |  | 0 | 0 | 35.153 | 24.1433 | 1.456 | 22.9593 | 0.50181 | 0 | 0.50181 | 0.02509 | 0 | 0.02509 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-School K-12 | Commercial EM-Retro-School K-12-ElecHt | 5 | 19.0832 | 0 | 4.8039 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 20.5105 | 0.0038557 | 0.0038279 | 0 | 0 | 0 | 0.95797 | 2.2137 | 0 | 13.4947 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95797 | 2.2137 | 0 | 13.4947 | 16.6664 | 10.6749 | 1.3624 | 0 | 0 | 12.0373 | 0.95797 | 12.5654 | 10.6749 | 1.6127 | 0 | 0 | 12.2876 | 2.2137 | 5.5506 | 10.6749 | 2.9751 | 0 | 0 | 13.65 | 3.1717 | 0.70529 | 4.3037 | 3.4367 | 7.9417 | 0 | 48.4125 | 59.791 | 10.6749 | 0 | 2.9751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6664 |  | 0 | 0 | 13.65 | 16.6664 | 0.81901 | 49.1178 | 0.19485 | 0 | 0.19485 | 0.0097425 | 0 | 0.0097425 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-University | Commercial EM-Retro-University-ElecHt | 5 | 129.1959 | 0 | 21.6822 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 138.8591 | 0.026104 | 0.025915 | 0 | 0 | 0 | 4.3237 | 9.9915 | 0 | 60.9075 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3237 | 9.9915 | 0 | 60.9075 | 75.2227 | 72.2704 | 9.2237 | 0 | 0 | 81.4941 | 4.3237 | 18.8482 | 72.2704 | 10.9181 | 0 | 0 | 83.1885 | 9.9915 | 8.326 | 72.2704 | 20.1418 | 0 | 0 | 92.4122 | 14.3152 | -3.0875 | 6.4555 | 2.2911 | 5.2945 | 0 | 32.275 | 39.8606 | 72.2704 | 0 | 20.1418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2227 |  | 0 | 0 | 92.4122 | 75.2227 | 1.2285 | 29.1875 | 1.3192 | 0 | 1.3192 | 0.065958 | 0 | 0.065958 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Warehouse | Commercial EM-Retro-Warehouse-ElecHt | 5 | 0.46323 | 0 | 0.093289 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.49788 | 9.3594e-05 | 9.2918e-05 | 0 | 0 | 0 | 0.018603 | 0.042989 | 0 | 0.26206 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018603 | 0.042989 | 0 | 0.26206 | 0.32365 | 0.25912 | 0.033071 | 0 | 0 | 0.29219 | 0.018603 | 15.7068 | 0.25912 | 0.039146 | 0 | 0 | 0.29827 | 0.042989 | 6.9383 | 0.25912 | 0.072218 | 0 | 0 | 0.33134 | 0.061592 | -1.5704 | 5.3796 | 2.7494 | 6.3534 | 0 | 38.73 | 47.8328 | 0.25912 | 0 | 0.072218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32365 |  | 0 | 0 | 0.33134 | 0.32365 | 1.0238 | 37.1596 | 0.0047299 | 0 | 0.0047299 | 0.00023649 | 0 | 0.00023649 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Supermarket | Commercial EM-Retro-Supermarket-ElecHt | 5 | 6.4604 | 0 | 0.93675 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 6.9436 | 0.0013053 | 0.0012959 | 0 | 0 | 0 | 0.1868 | 0.43167 | 0 | 2.6314 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1868 | 0.43167 | 0 | 2.6314 | 3.2499 | 3.6138 | 0.46122 | 0 | 0 | 4.0751 | 0.1868 | 21.815 | 3.6138 | 0.54595 | 0 | 0 | 4.1598 | 0.43167 | 9.6365 | 3.6138 | 1.0072 | 0 | 0 | 4.621 | 0.61847 | -4.1192 | 7.4717 | 1.9796 | 4.5744 | 0 | 27.8856 | 34.4396 | 3.6138 | 0 | 1.0072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2499 |  | 0 | 0 | 4.621 | 3.2499 | 1.4219 | 23.7664 | 0.065964 | 0 | 0.065964 | 0.0032982 | 0 | 0.0032982 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-MiniMart | Commercial EM-Retro-MiniMart-ElecHt | 5 | 0 | 0 | 0 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Restaurant | Commercial EM-Retro-Restaurant-ElecHt | 5 | 1.8272 | 0 | 0.39427 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.9639 | 0.00036919 | 0.00036652 | 0 | 0 | 0 | 0.078623 | 0.18169 | 0 | 1.1075 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.078623 | 0.18169 | 0 | 1.1075 | 1.3679 | 1.0221 | 0.13045 | 0 | 0 | 1.1526 | 0.078623 | 14.6597 | 1.0221 | 0.15442 | 0 | 0 | 1.1765 | 0.18169 | 6.4758 | 1.0221 | 0.28487 | 0 | 0 | 1.307 | 0.26031 | -0.9202 | 5.021 | 2.9458 | 6.8072 | 0 | 41.4964 | 51.2494 | 1.0221 | 0 | 0.28487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3679 |  | 0 | 0 | 1.307 | 1.3679 | 0.95551 | 40.5762 | 0.018657 | 0 | 0.018657 | 0.00093286 | 0 | 0.00093286 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Lodging | Commercial EM-Retro-Lodging-ElecHt | 5 | 58.9041 | 0 | 8.897 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 63.3099 | 0.011901 | 0.011815 | 0 | 0 | 0 | 1.7742 | 4.0999 | 0 | 24.9925 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7742 | 4.0999 | 0 | 24.9925 | 30.8666 | 32.9502 | 4.2053 | 0 | 0 | 37.1555 | 1.7742 | 20.9424 | 32.9502 | 4.9779 | 0 | 0 | 37.928 | 4.0999 | 9.2511 | 32.9502 | 9.1832 | 0 | 0 | 42.1334 | 5.874 | -3.8461 | 7.1728 | 2.062 | 4.765 | 0 | 29.0475 | 35.8746 | 32.9502 | 0 | 9.1832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.8666 |  | 0 | 0 | 42.1334 | 30.8666 | 1.365 | 25.2014 | 0.60145 | 0 | 0.60145 | 0.030072 | 0 | 0.030072 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Hospital | Commercial EM-Retro-Hospital-ElecHt | 5 | 189.0603 | 0 | 19.0373 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 203.2011 | 0.038199 | 0.037923 | 0 | 0 | 0 | 3.7963 | 8.7727 | 0 | 53.4778 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7963 | 8.7727 | 0 | 53.4778 | 66.0467 | 105.7577 | 13.4976 | 0 | 0 | 119.2553 | 3.7963 | 31.4136 | 105.7577 | 15.9771 | 0 | 0 | 121.7348 | 8.7727 | 13.8766 | 105.7577 | 29.4747 | 0 | 0 | 135.2324 | 12.569 | -6.1218 | 10.7592 | 1.3747 | 3.1767 | 0 | 19.365 | 23.9164 | 105.7577 | 0 | 29.4747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.0467 |  | 0 | 0 | 135.2324 | 66.0467 | 2.0475 | 13.2432 | 1.9304 | 0 | 1.9304 | 0.096521 | 0 | 0.096521 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Residential Care | Commercial EM-Retro-Residential Care-ElecHt | 5 | 60.7411 | 0 | 7.224 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 65.2843 | 0.012273 | 0.012184 | 0 | 0 | 0 | 1.4406 | 3.3289 | 0 | 20.2929 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4406 | 3.3289 | 0 | 20.2929 | 25.0623 | 33.9778 | 4.3365 | 0 | 0 | 38.3142 | 1.4406 | 26.5968 | 33.9778 | 5.1331 | 0 | 0 | 39.1109 | 3.3289 | 11.7489 | 33.9778 | 9.4696 | 0 | 0 | 43.4474 | 4.7695 | -5.2975 | 9.1095 | 1.6236 | 3.752 | 0 | 22.8721 | 28.2477 | 33.9778 | 0 | 9.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.0623 |  | 0 | 0 | 43.4474 | 25.0623 | 1.7336 | 17.5745 | 0.62021 | 0 | 0.62021 | 0.03101 | 0 | 0.03101 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Assembly | Commercial EM-Retro-Assembly-ElecHt | 5 | 28.1412 | 0 | 4.5005 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 30.2461 | 0.0056858 | 0.0056448 | 0 | 0 | 0 | 0.89747 | 2.0739 | 0 | 12.6424 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89747 | 2.0739 | 0 | 12.6424 | 15.6138 | 15.7418 | 2.0091 | 0 | 0 | 17.7509 | 0.89747 | 19.7789 | 15.7418 | 2.3782 | 0 | 0 | 18.12 | 2.0739 | 8.7371 | 15.7418 | 4.3872 | 0 | 0 | 20.1291 | 2.9714 | -3.4445 | 6.7743 | 2.1833 | 5.0453 | 0 | 30.7562 | 37.9848 | 15.7418 | 0 | 4.3872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6138 |  | 0 | 0 | 20.1291 | 15.6138 | 1.2892 | 27.3117 | 0.28734 | 0 | 0.28734 | 0.014367 | 0 | 0.014367 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Other | Commercial EM-Retro-Other-ElecHt | 5 | 53.3014 | 0 | 8.5243 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 57.2881 | 0.010769 | 0.010692 | 0 | 0 | 0 | 1.6999 | 3.9281 | 0 | 23.9457 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6999 | 3.9281 | 0 | 23.9457 | 29.5737 | 29.8161 | 3.8053 | 0 | 0 | 33.6214 | 1.6999 | 19.7789 | 29.8161 | 4.5044 | 0 | 0 | 34.3205 | 3.9281 | 8.7371 | 29.8161 | 8.3097 | 0 | 0 | 38.1258 | 5.628 | -3.4445 | 6.7743 | 2.1833 | 5.0453 | 0 | 30.7562 | 37.9848 | 29.8161 | 0 | 8.3097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.5737 |  | 0 | 0 | 38.1258 | 29.5737 | 1.2892 | 27.3117 | 0.54424 | 0 | 0.54424 | 0.027212 | 0 | 0.027212 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Large Off | Commercial EM-Retro-Large Off-HtPmpHt | 5 | 176.9464 | 0 | 39.5619 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 190.1812 | 0.035751 | 0.035493 | 0 | 0 | 0 | 7.8892 | 18.2307 | 0 | 111.1336 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8892 | 18.2307 | 0 | 111.1336 | 137.2534 | 98.9814 | 12.6327 | 0 | 0 | 111.6141 | 7.8892 | 14.1478 | 98.9814 | 14.9534 | 0 | 0 | 113.9348 | 18.2307 | 6.2496 | 98.9814 | 27.5861 | 0 | 0 | 126.5675 | 26.1199 | -0.5673 | 4.8456 | 3.0523 | 7.0535 | 0 | 42.998 | 53.1038 | 98.9814 | 0 | 27.5861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.2534 |  | 0 | 0 | 126.5675 | 137.2534 | 0.92214 | 42.4307 | 1.8067 | 0 | 1.8067 | 0.090336 | 0 | 0.090336 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Medium Off | Commercial EM-Retro-Medium Off-HtPmpHt | 5 | 23.2988 | 0 | 6.2346 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 25.0415 | 0.0047075 | 0.0046735 | 0 | 0 | 0 | 1.2433 | 2.873 | 0 | 17.5137 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2433 | 2.873 | 0 | 17.5137 | 21.6299 | 13.033 | 1.6634 | 0 | 0 | 14.6964 | 1.2433 | 11.8208 | 13.033 | 1.9689 | 0 | 0 | 15.002 | 2.873 | 5.2217 | 13.033 | 3.6323 | 0 | 0 | 16.6653 | 4.1163 | 1.422 | 4.0487 | 3.6532 | 8.442 | 0 | 51.4621 | 63.5573 | 13.033 | 0 | 3.6323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.6299 |  | 0 | 0 | 16.6653 | 21.6299 | 0.77048 | 52.8842 | 0.2379 | 0 | 0.2379 | 0.011895 | 0 | 0.011895 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Small Off | Commercial EM-Retro-Small Off-HtPmpHt | 5 | 8.3897 | 0 | 5.9214 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 9.0172 | 0.0016951 | 0.0016829 | 0 | 0 | 0 | 1.1808 | 2.7287 | 0 | 16.6339 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1808 | 2.7287 | 0 | 16.6339 | 20.5434 | 4.6931 | 0.59896 | 0 | 0 | 5.292 | 1.1808 | 4.4817 | 4.6931 | 0.70899 | 0 | 0 | 5.4021 | 2.7287 | 1.9797 | 4.6931 | 1.308 | 0 | 0 | 6.001 | 3.9095 | 21.2291 | 1.535 | 9.6357 | 22.2666 | 0 | 135.736 | 167.6382 | 4.6931 | 0 | 1.308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.5434 |  | 0 | 0 | 6.001 | 20.5434 | 0.29211 | 156.9651 | 0.085664 | 0 | 0.085664 | 0.0042832 | 0 | 0.0042832 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Xlarge Ret | Commercial EM-Retro-Xlarge Ret-HtPmpHt | 5 | 1.1363 | 0 | 0.30407 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.2213 | 0.00022959 | 0.00022793 | 0 | 0 | 0 | 0.060636 | 0.14012 | 0 | 0.85417 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.060636 | 0.14012 | 0 | 0.85417 | 1.0549 | 0.63564 | 0.081125 | 0 | 0 | 0.71676 | 0.060636 | 11.8208 | 0.63564 | 0.096028 | 0 | 0 | 0.73167 | 0.14012 | 5.2217 | 0.63564 | 0.17715 | 0 | 0 | 0.81279 | 0.20076 | 1.422 | 4.0487 | 3.6532 | 8.442 | 0 | 51.4621 | 63.5573 | 0.63564 | 0 | 0.17715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0549 |  | 0 | 0 | 0.81279 | 1.0549 | 0.77048 | 52.8842 | 0.011603 | 0 | 0.011603 | 0.00058012 | 0 | 0.00058012 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Large Ret | Commercial EM-Retro-Large Ret-HtPmpHt | 5 | 1.6479 | 0 | 0.88895 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.7712 | 0.00033296 | 0.00033056 | 0 | 0 | 0 | 0.17727 | 0.40964 | 0 | 2.4972 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17727 | 0.40964 | 0 | 2.4972 | 3.0841 | 0.92183 | 0.11765 | 0 | 0 | 1.0395 | 0.17727 | 5.8639 | 0.92183 | 0.13926 | 0 | 0 | 1.0611 | 0.40964 | 2.5903 | 0.92183 | 0.25691 | 0 | 0 | 1.1787 | 0.58691 | 13.7092 | 2.0084 | 7.3644 | 17.018 | 0 | 103.7411 | 128.1235 | 0.92183 | 0 | 0.25691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0841 |  | 0 | 0 | 1.1787 | 3.0841 | 0.3822 | 117.4503 | 0.016826 | 0 | 0.016826 | 0.00084132 | 0 | 0.00084132 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Medium Ret | Commercial EM-Retro-Medium Ret-HtPmpHt | 5 | 2.783 | 0 | 1.0778 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 2.9912 | 0.0005623 | 0.00055824 | 0 | 0 | 0 | 0.21493 | 0.49667 | 0 | 3.0277 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21493 | 0.49667 | 0 | 3.0277 | 3.7393 | 1.5568 | 0.19869 | 0 | 0 | 1.7555 | 0.21493 | 8.1675 | 1.5568 | 0.23519 | 0 | 0 | 1.792 | 0.49667 | 3.6079 | 1.5568 | 0.43387 | 0 | 0 | 1.9906 | 0.71161 | 6.8322 | 2.7974 | 5.2873 | 12.2181 | 0 | 74.4808 | 91.9861 | 1.5568 | 0 | 0.43387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7393 |  | 0 | 0 | 1.9906 | 3.7393 | 0.53236 | 81.3129 | 0.028416 | 0 | 0.028416 | 0.0014208 | 0 | 0.0014208 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Small Ret | Commercial EM-Retro-Small Ret-HtPmpHt | 5 | 24.2064 | 0 | 4.0624 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 26.0169 | 0.0048908 | 0.0048555 | 0 | 0 | 0 | 0.8101 | 1.872 | 0 | 11.4117 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8101 | 1.872 | 0 | 11.4117 | 14.0938 | 13.5407 | 1.7282 | 0 | 0 | 15.2689 | 0.8101 | 18.8482 | 13.5407 | 2.0456 | 0 | 0 | 15.5863 | 1.872 | 8.326 | 13.5407 | 3.7738 | 0 | 0 | 17.3145 | 2.6821 | -3.0875 | 6.4555 | 2.2911 | 5.2945 | 0 | 32.275 | 39.8606 | 13.5407 | 0 | 3.7738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.0938 |  | 0 | 0 | 17.3145 | 14.0938 | 1.2285 | 29.1875 | 0.24716 | 0 | 0.24716 | 0.012358 | 0 | 0.012358 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-School K-12 | Commercial EM-Retro-School K-12-HtPmpHt | 5 | 23.0131 | 0 | 7.7243 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 24.7344 | 0.0046497 | 0.0046162 | 0 | 0 | 0 | 1.5403 | 3.5595 | 0 | 21.6984 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5403 | 3.5595 | 0 | 21.6984 | 26.7982 | 12.8732 | 1.643 | 0 | 0 | 14.5162 | 1.5403 | 9.4241 | 12.8732 | 1.9448 | 0 | 0 | 14.818 | 3.5595 | 4.163 | 12.8732 | 3.5878 | 0 | 0 | 16.461 | 5.0998 | 4.4981 | 3.2278 | 4.5823 | 10.589 | 0 | 64.55 | 79.7213 | 12.8732 | 0 | 3.5878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.7982 |  | 0 | 0 | 16.461 | 26.7982 | 0.61426 | 69.0481 | 0.23498 | 0 | 0.23498 | 0.011749 | 0 | 0.011749 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-University | Commercial EM-Retro-University-HtPmpHt | 5 | 100.4857 | 0 | 21.6822 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 108.0016 | 0.020303 | 0.020156 | 0 | 0 | 0 | 4.3237 | 9.9915 | 0 | 60.9075 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3237 | 9.9915 | 0 | 60.9075 | 75.2227 | 56.2103 | 7.174 | 0 | 0 | 63.3843 | 4.3237 | 14.6597 | 56.2103 | 8.4918 | 0 | 0 | 64.7022 | 9.9915 | 6.4758 | 56.2103 | 15.6658 | 0 | 0 | 71.8761 | 14.3152 | -0.9202 | 5.021 | 2.9458 | 6.8072 | 0 | 41.4964 | 51.2494 | 56.2103 | 0 | 15.6658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2227 |  | 0 | 0 | 71.8761 | 75.2227 | 0.95551 | 40.5762 | 1.026 | 0 | 1.026 | 0.051301 | 0 | 0.051301 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Warehouse | Commercial EM-Retro-Warehouse-HtPmpHt | 5 | 0.31898 | 0 | 0.096359 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.34284 | 6.4449e-05 | 6.3984e-05 | 0 | 0 | 0 | 0.019215 | 0.044403 | 0 | 0.27068 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019215 | 0.044403 | 0 | 0.27068 | 0.3343 | 0.17843 | 0.022773 | 0 | 0 | 0.20121 | 0.019215 | 10.4712 | 0.17843 | 0.026956 | 0 | 0 | 0.20539 | 0.044403 | 4.6255 | 0.17843 | 0.049729 | 0 | 0 | 0.22816 | 0.063619 | 2.981 | 3.5864 | 4.1241 | 9.5301 | 0 | 58.095 | 71.7492 | 0.17843 | 0 | 0.049729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3343 |  | 0 | 0 | 0.22816 | 0.3343 | 0.68251 | 61.076 | 0.003257 | 0 | 0.003257 | 0.00016285 | 0 | 0.00016285 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Supermarket | Commercial EM-Retro-Supermarket-HtPmpHt | 5 | 8.2238 | 0 | 1.4906 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 8.8389 | 0.0016616 | 0.0016496 | 0 | 0 | 0 | 0.29724 | 0.68687 | 0 | 4.1871 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29724 | 0.68687 | 0 | 4.1871 | 5.1713 | 4.6003 | 0.58712 | 0 | 0 | 5.1874 | 0.29724 | 17.452 | 4.6003 | 0.69498 | 0 | 0 | 5.2953 | 0.68687 | 7.7092 | 4.6003 | 1.2821 | 0 | 0 | 5.8824 | 0.98411 | -2.4807 | 5.9774 | 2.4744 | 5.7181 | 0 | 34.857 | 43.0495 | 4.6003 | 0 | 1.2821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1713 |  | 0 | 0 | 5.8824 | 5.1713 | 1.1375 | 32.3763 | 0.08397 | 0 | 0.08397 | 0.0041985 | 0 | 0.0041985 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-MiniMart | Commercial EM-Retro-MiniMart-HtPmpHt | 5 | 0 | 0 | 0 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Restaurant | Commercial EM-Retro-Restaurant-HtPmpHt | 5 | 9.1884 | 0 | 2.313 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 9.8756 | 0.0018565 | 0.0018431 | 0 | 0 | 0 | 0.46125 | 1.0659 | 0 | 6.4976 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46125 | 1.0659 | 0 | 6.4976 | 8.0247 | 5.1399 | 0.65599 | 0 | 0 | 5.7958 | 0.46125 | 12.5654 | 5.1399 | 0.77649 | 0 | 0 | 5.9164 | 1.0659 | 5.5506 | 5.1399 | 1.4325 | 0 | 0 | 6.5723 | 1.5271 | 0.70529 | 4.3037 | 3.4367 | 7.9417 | 0 | 48.4125 | 59.791 | 5.1399 | 0 | 1.4325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0247 |  | 0 | 0 | 6.5723 | 8.0247 | 0.81901 | 49.1178 | 0.093819 | 0 | 0.093819 | 0.0046909 | 0 | 0.0046909 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Lodging | Commercial EM-Retro-Lodging-HtPmpHt | 5 | 31.1509 | 0 | 6.0494 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 33.4808 | 0.0062939 | 0.0062485 | 0 | 0 | 0 | 1.2063 | 2.7876 | 0 | 16.9934 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2063 | 2.7876 | 0 | 16.9934 | 20.9873 | 17.4254 | 2.224 | 0 | 0 | 19.6493 | 1.2063 | 16.2885 | 17.4254 | 2.6325 | 0 | 0 | 20.0579 | 2.7876 | 7.1953 | 17.4254 | 4.8565 | 0 | 0 | 22.2818 | 3.994 | -1.8955 | 5.5789 | 2.6512 | 6.1265 | 0 | 37.3468 | 46.1245 | 17.4254 | 0 | 4.8565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9873 |  | 0 | 0 | 22.2818 | 20.9873 | 1.0617 | 35.4513 | 0.31807 | 0 | 0.31807 | 0.015903 | 0 | 0.015903 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Hospital | Commercial EM-Retro-Hospital-HtPmpHt | 5 | 18.906 | 0 | 2.3797 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 20.3201 | 0.0038199 | 0.0037923 | 0 | 0 | 0 | 0.47454 | 1.0966 | 0 | 6.6847 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47454 | 1.0966 | 0 | 6.6847 | 8.2558 | 10.5758 | 1.3498 | 0 | 0 | 11.9255 | 0.47454 | 25.1309 | 10.5758 | 1.5977 | 0 | 0 | 12.1735 | 1.0966 | 11.1013 | 10.5758 | 2.9475 | 0 | 0 | 13.5232 | 1.5711 | -4.9839 | 8.6074 | 1.7184 | 3.9709 | 0 | 24.2063 | 29.8955 | 10.5758 | 0 | 2.9475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2558 |  | 0 | 0 | 13.5232 | 8.2558 | 1.638 | 19.2223 | 0.19304 | 0 | 0.19304 | 0.0096521 | 0 | 0.0096521 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Residential Care | Commercial EM-Retro-Residential Care-HtPmpHt | 5 | 36.5428 | 0 | 5.4113 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 39.2761 | 0.0073834 | 0.0073301 | 0 | 0 | 0 | 1.0791 | 2.4936 | 0 | 15.2008 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0791 | 2.4936 | 0 | 15.2008 | 18.7735 | 20.4416 | 2.6089 | 0 | 0 | 23.0505 | 1.0791 | 21.3612 | 20.4416 | 3.0882 | 0 | 0 | 23.5297 | 2.4936 | 9.4361 | 20.4416 | 5.6971 | 0 | 0 | 26.1386 | 3.5727 | -3.98 | 7.3163 | 2.0216 | 4.6716 | 0 | 28.4779 | 35.1712 | 20.4416 | 0 | 5.6971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.7735 |  | 0 | 0 | 26.1386 | 18.7735 | 1.3923 | 24.498 | 0.37313 | 0 | 0.37313 | 0.018656 | 0 | 0.018656 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Assembly | Commercial EM-Retro-Assembly-HtPmpHt | 5 | 23.3486 | 0 | 4.883 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 25.0949 | 0.0047175 | 0.0046835 | 0 | 0 | 0 | 0.97373 | 2.2502 | 0 | 13.7168 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97373 | 2.2502 | 0 | 13.7168 | 16.9407 | 13.0609 | 1.6669 | 0 | 0 | 14.7278 | 0.97373 | 15.1251 | 13.0609 | 1.9731 | 0 | 0 | 15.034 | 2.2502 | 6.6813 | 13.0609 | 3.6401 | 0 | 0 | 16.7009 | 3.2239 | -1.2203 | 5.1804 | 2.8551 | 6.5978 | 0 | 40.2196 | 49.6725 | 13.0609 | 0 | 3.6401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.9407 |  | 0 | 0 | 16.7009 | 16.9407 | 0.98585 | 38.9993 | 0.2384 | 0 | 0.2384 | 0.01192 | 0 | 0.01192 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Other | Commercial EM-Retro-Other-HtPmpHt | 5 | 25.2384 | 0 | 5.2782 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 27.1261 | 0.0050993 | 0.0050625 | 0 | 0 | 0 | 1.0525 | 2.4323 | 0 | 14.8271 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0525 | 2.4323 | 0 | 14.8271 | 18.3119 | 14.118 | 1.8018 | 0 | 0 | 15.9199 | 1.0525 | 15.1251 | 14.118 | 2.1328 | 0 | 0 | 16.2509 | 2.4323 | 6.6813 | 14.118 | 3.9347 | 0 | 0 | 18.0527 | 3.4848 | -1.2203 | 5.1804 | 2.8551 | 6.5978 | 0 | 40.2196 | 49.6725 | 14.118 | 0 | 3.9347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.3119 |  | 0 | 0 | 18.0527 | 18.3119 | 0.98585 | 38.9993 | 0.2577 | 0 | 0.2577 | 0.012885 | 0 | 0.012885 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Category Results; Sorted by TRC Levelized Cost
Total Results |  | Measure Input Data | [8 empty] | Savings | [5 empty] | PV Capital |  |  |  | PV Admin |  |  |  | PV O&M |  |  |  | PV Periodic Repl. |  |  |  | Total PV Capital, O&M and Periodic Repl Costs |  |  |  |  | PV Wholesale Electric Utility Costs & Benefits | [6 empty] | PV Retail Electric Utility Costs & Benefits | [6 empty] | PV Electric Utility System Costs & Benefits | [5 empty] | Electric Utility System Economics |  | Sponsor Levelized Cost (mills/kwh) |  |  |  |  | PV Regional Costs & Benefits | [15 empty] | TRC Economics |  | Physical CO2 | [5 empty] | Gas Inputs |  |  |  | PV Gas Utility System Costs & Benefits |  |  |  |  | Gas Utility System Economics
Category | Measure | Measure Life | Site Savings (kWh) | Site Savings (therms) | Capital Cost ($/unit) | Annual O&M Cost ($/unit) | PV Per. Repl. Cost ($/unit) | Load Shape (electric) | Diversified Load Factor (electric) | Wholesale Power Coincidence Factor (electric) | Wholesale Electric Energy (kWh) | Wholesale Electric Demand (kw) | Retail Electric Demand (kW) | Wholesale Gas Energy (therms/yr) | Wholesale Gas Demand (therms/day) | Retail Gas Demand (therms/day) | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Total | Wholesale Utility System Energy | Wholesale Utility System T&D Def. Cap. | Wholesale Utility System Act C-E Credit | Wholesale Utility System Risk Mitigation Benefit | Wholesale Utility System Total System Benefit | Wholesale Utility System Total Non-Consumer Cost | Wholesale Utility System B/C Ratio | Retail Utility System Energy | Retail Utility System T&D Def. Cap. | Retail Utility System Act C-E Credit | Retail Utility System Risk Mitigation Benefit | Retail Utility System Total System Benefit | Retail Utility System Total Non-Consumer Cost | Retail Utility System System B/C Ratio | Utility System Energy | Utility System T&D Def. Cap. | Utility System Act C-E Credit | Utility System Total Risk Mitigation Benefit | Utility System Total System Benefit | Utility System Total Non-Consumer Cost | Utility System Net Levelized Cost (Net of Elec T&D Capacity Benefits, Act Credit & Risk-Mitigation Benefit) in mills/kwh | Utility System System B/C Ratio | Wholesale Electric Levelized Cost | Retail Electric Levelized Cost | Natural Gas Levelized Cost | Customer Levelized Cost | Total Levelized Cost | PV Regional Electric Energy | PV Regional Gas Energy | PV Regional Electric T&D Def. Cap. | PV Regional Gas T&D Def. Cap. | PV Regional Electric System CO2 | PV Regional Gas System CO2 | PV Regional Electric System Risk-Mitigation Benefit | PV Regional Gas System Risk-Mitigation Benefit | PV Regional Non-E Value | PV Regional Act Credit | PV Regional Capital Cost | PV Regional Admin Cost | PV Regional Annual O&M Cost | PV Regional Periodic Replacement Cost | PV Total Regional Benefit | PV Total Regional Cost | TRC B/C Ratio | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | Electric System CO2 Avoided (Lifetime Tons) | Gas System CO2 Avoided (Lifetime Tons) | Total System CO2 Avoided (Lifetime Tons) | Electric System CO2 Avoided (Annual Tons in 2018) | Gas System CO2 Avoided (Annual Tons in 2018) | Total System CO2 Avoided (Annual Tons in 2018) | Gas Site Savings (therms) | Load Shape (gas) | Diversitfied Load Factor (gas) | Wholesale Coincidence Factor (gas) | Total Gas Utility System Energy | Gas Utility System T&D Def. Cap. | Gas Utility System Risk Mitigation Benefit | Gas Utility System Total System Benefit | Gas Utility System Total Non-Consumer Cost | Gas Utility System Net Levelized Cost (Net of Gas T&D Capacity Benefits & Risk-Mitigation Benefits) in cents/therm | Gas Utility System System B/C Ratio
Commercial EM-Retro-MiniMart |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-Retro-Hospital |  | 5 | 1526.9766 | 57.1657 | 237.9665 | 0 | 0 |  |  |  | 1641.1873 | 0.30852 | 0.30629 | 57.7374 | 0 | 0 | 47.4537 | 109.6583 | 0 | 668.4724 | 14.278 | 33.3153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.7317 | 142.9736 | 0 | 668.4724 | 873.1776 | 854.1698 | 109.0154 | 0 | 0 | 963.1852 | 61.7317 | 15.6028 | 854.1698 | 129.0417 | 0 | 0 | 983.2116 | 142.9736 | 6.8769 | 854.1698 | 238.0571 | 0 | 0 | 1092.2269 | 204.7052 | -1.4953 | 5.3356 | 2.7677 | 6.4101 | 0 | 29.9706 | 39.1484 | 854.1698 | 375.2259 | 238.0571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 825.5843 | 47.5933 | 0 | 0 | 1467.4528 | 873.1776 | 1.6806 | 11.6522 | 15.5914 | 6.7553 | 22.3467 | 0.77956 | 0.33776 | 1.1173 | 57.7374 |  | 0 | 0 | 375.2259 | 0 | 0 | 375.2259 | 0 | 0 | 9999
Commercial EM-Retro-Residential Care |  | 5 | 141.8024 | 2.2757 | 21.2559 | 0 | 0 |  |  |  | 152.4085 | 0.028651 | 0.028444 | 2.2985 | 0 | 0 | 4.2387 | 9.795 | 0 | 59.7101 | 1.2754 | 2.9758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5141 | 12.7709 | 0 | 59.7101 | 77.995 | 79.3223 | 10.1237 | 0 | 0 | 89.446 | 5.5141 | 16.2214 | 79.3223 | 11.9834 | 0 | 0 | 91.3057 | 12.7709 | 7.1495 | 79.3223 | 22.1071 | 0 | 0 | 101.4294 | 18.2849 | -1.8453 | 5.5472 | 2.6622 | 6.1657 | 0 | 28.8276 | 37.6554 | 79.3223 | 14.9375 | 22.1071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.7438 | 4.2512 | 0 | 0 | 116.3669 | 77.995 | 1.492 | 19.7706 | 1.4479 | 0.26892 | 1.7168 | 0.072394 | 0.013446 | 0.08584 | 2.2985 |  | 0 | 0 | 14.9375 | 0 | 0 | 14.9375 | 0 | 0 | 9999
Commercial EM-Retro-Small Ret |  | 5 | 144.5342 | 2.457 | 25.4638 | 0 | 0 |  |  |  | 155.3447 | 0.029203 | 0.028992 | 2.4816 | 0 | 0 | 5.0778 | 11.7341 | 0 | 71.5305 | 1.5278 | 3.5649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6057 | 15.299 | 0 | 71.5305 | 93.4352 | 80.8505 | 10.3187 | 0 | 0 | 91.1692 | 6.6057 | 13.8017 | 80.8505 | 12.2143 | 0 | 0 | 93.0648 | 15.299 | 6.0831 | 80.8505 | 22.533 | 0 | 0 | 103.3835 | 21.9047 | -0.29763 | 4.7197 | 3.1289 | 7.2466 | 0 | 33.8817 | 44.2572 | 80.8505 | 16.1272 | 22.533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3424 | 5.0928 | 0 | 0 | 119.5107 | 93.4352 | 1.2791 | 25.9451 | 1.4758 | 0.29034 | 1.7661 | 0.073789 | 0.014517 | 0.088306 | 2.4816 |  | 0 | 0 | 16.1272 | 0 | 0 | 16.1272 | 0 | 0 | 9999
Commercial EM-Retro-Other |  | 5 | 202.1186 | 12.8541 | 50.3221 | 0 | 0 |  |  |  | 217.2361 | 0.040837 | 0.040543 | 12.9827 | 0 | 0 | 10.0349 | 23.1891 | 0 | 141.3599 | 3.0193 | 7.0451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.0542 | 30.2342 | 0 | 141.3599 | 184.6483 | 113.0624 | 14.4298 | 0 | 0 | 127.4922 | 13.0542 | 9.7664 | 113.0624 | 17.0806 | 0 | 0 | 130.143 | 30.2342 | 4.3045 | 113.0624 | 31.5105 | 0 | 0 | 144.5728 | 43.2884 | 3.9894 | 3.3398 | 4.4217 | 10.2409 | 0 | 47.8811 | 62.5437 | 113.0624 | 84.3722 | 31.5105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174.5839 | 10.0644 | 0 | 0 | 228.9451 | 184.6483 | 1.2399 | 23.2921 | 2.0638 | 1.519 | 3.5827 | 0.10319 | 0.075949 | 0.17914 | 12.9827 |  | 0 | 0 | 84.3722 | 0 | 0 | 84.3722 | 0 | 0 | 9999
Commercial EM-Retro-Supermarket |  | 5 | 61.7568 | 2.4696 | 13.6535 | 0 | 0 |  |  |  | 66.3759 | 0.012478 | 0.012388 | 2.4943 | 0 | 0 | 2.7227 | 6.2917 | 0 | 38.3541 | 0.81921 | 1.9115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5419 | 8.2032 | 0 | 38.3541 | 50.0993 | 34.5459 | 4.409 | 0 | 0 | 38.9549 | 3.5419 | 10.9983 | 34.5459 | 5.2189 | 0 | 0 | 39.7648 | 8.2032 | 4.8475 | 34.5459 | 9.6279 | 0 | 0 | 44.1738 | 11.7451 | 2.347 | 3.761 | 3.9264 | 9.0938 | 0 | 42.5179 | 55.5381 | 34.5459 | 16.2102 | 9.6279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.3686 | 2.7307 | 0 | 0 | 60.384 | 50.0993 | 1.2053 | 26.895 | 0.63058 | 0.29184 | 0.92241 | 0.031529 | 0.014592 | 0.04612 | 2.4943 |  | 0 | 0 | 16.2102 | 0 | 0 | 16.2102 | 0 | 0 | 9999
Commercial EM-Retro-Lodging |  | 5 | 108.6886 | 0.87408 | 19.913 | 0 | 0 |  |  |  | 116.818 | 0.02196 | 0.021802 | 0.88282 | 0 | 0 | 3.9709 | 9.1762 | 0 | 55.9378 | 1.1948 | 2.7878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1657 | 11.964 | 0 | 55.9378 | 73.0675 | 60.7989 | 7.7596 | 0 | 0 | 68.5585 | 5.1657 | 13.2719 | 60.7989 | 9.1851 | 0 | 0 | 69.984 | 11.964 | 5.8495 | 60.7989 | 16.9447 | 0 | 0 | 77.7436 | 17.1297 | 0.11658 | 4.5385 | 3.2538 | 7.5359 | 0 | 35.2343 | 46.024 | 60.7989 | 5.7373 | 16.9447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.0849 | 3.9826 | 0 | 0 | 83.4809 | 73.0675 | 1.1425 | 31.737 | 1.1098 | 0.10329 | 1.2131 | 0.055489 | 0.0051645 | 0.060653 | 0.88282 |  | 0 | 0 | 5.7373 | 0 | 0 | 5.7373 | 0 | 0 | 9999
Commercial EM-Retro-Assembly |  | 5 | 162.8675 | 7.7234 | 42.2974 | 0 | 0 |  |  |  | 175.0492 | 0.032907 | 0.032669 | 7.8006 | 0 | 0 | 8.4347 | 19.4913 | 0 | 118.8179 | 2.5378 | 5.9216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.9725 | 25.4129 | 0 | 118.8179 | 155.2033 | 91.1058 | 11.6276 | 0 | 0 | 102.7334 | 10.9725 | 9.3628 | 91.1058 | 13.7636 | 0 | 0 | 104.8694 | 25.4129 | 4.1266 | 91.1058 | 25.3912 | 0 | 0 | 116.497 | 36.3854 | 4.6214 | 3.2018 | 4.6123 | 10.6823 | 0 | 49.945 | 65.2395 | 91.1058 | 50.6947 | 25.3912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.7438 | 8.4595 | 0 | 0 | 167.1917 | 155.2033 | 1.0772 | 33.2569 | 1.663 | 0.91267 | 2.5757 | 0.083148 | 0.045633 | 0.12878 | 7.8006 |  | 0 | 0 | 50.6947 | 0 | 0 | 50.6947 | 0 | 0 | 9999
Commercial EM-Retro-Large Off |  | 5 | 675.0203 | 13.5337 | 158.1234 | 0 | 0 |  |  |  | 725.5086 | 0.13639 | 0.1354 | 13.6691 | 0 | 0 | 31.5319 | 72.8655 | 0 | 444.1849 | 9.4874 | 22.1373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.0193 | 95.0027 | 0 | 444.1849 | 580.207 | 377.5971 | 48.1917 | 0 | 0 | 425.7888 | 41.0193 | 10.3802 | 377.5971 | 57.0446 | 0 | 0 | 434.6417 | 95.0027 | 4.575 | 377.5971 | 105.2363 | 0 | 0 | 482.8334 | 136.0221 | 3.1223 | 3.5497 | 4.1602 | 9.6353 | 0 | 45.0496 | 58.8451 | 377.5971 | 88.8331 | 105.2363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 548.5823 | 31.6247 | 0 | 0 | 571.6665 | 580.207 | 0.98528 | 39.1624 | 6.8924 | 1.5993 | 8.4917 | 0.34462 | 0.079964 | 0.42458 | 13.6691 |  | 0 | 0 | 88.8331 | 0 | 0 | 88.8331 | 0 | 0 | 9999
Commercial EM-Retro-University |  | 5 | 815.3696 | 26.5583 | 216.8218 | 0 | 0 |  |  |  | 876.3554 | 0.16474 | 0.16355 | 26.8238 | 0 | 0 | 43.2372 | 99.9145 | 0 | 609.0748 | 13.0093 | 30.3551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.2465 | 130.2696 | 0 | 609.0748 | 795.5909 | 456.1066 | 58.2116 | 0 | 0 | 514.3183 | 56.2465 | 9.144 | 456.1066 | 68.9053 | 0 | 0 | 525.0119 | 130.2696 | 4.0302 | 456.1066 | 127.1169 | 0 | 0 | 583.2235 | 186.516 | 4.9874 | 3.1269 | 4.7226 | 10.9379 | 0 | 51.14 | 66.8005 | 456.1066 | 174.3238 | 127.1169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752.2265 | 43.3644 | 0 | 0 | 757.5473 | 795.5909 | 0.95218 | 41.4905 | 8.3255 | 3.1384 | 11.4638 | 0.41627 | 0.15692 | 0.57319 | 26.8238 |  | 0 | 0 | 174.3238 | 0 | 0 | 174.3238 | 0 | 0 | 9999
Commercial EM-Retro-Xlarge Ret |  | 5 | 31.1522 | 1.5318 | 9.8288 | 0 | 0 |  |  |  | 33.4823 | 0.0062942 | 0.0062488 | 1.5471 | 0 | 0 | 1.96 | 4.5292 | 0 | 27.61 | 0.58973 | 1.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5497 | 5.9053 | 0 | 27.61 | 36.065 | 17.4261 | 2.224 | 0 | 0 | 19.6502 | 2.5497 | 7.7068 | 17.4261 | 2.6326 | 0 | 0 | 20.0587 | 5.9053 | 3.3968 | 17.4261 | 4.8567 | 0 | 0 | 22.2828 | 8.455 | 7.9078 | 2.6355 | 5.6033 | 12.9776 | 0 | 60.6767 | 79.2576 | 17.4261 | 10.0542 | 4.8567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.0992 | 1.9658 | 0 | 0 | 32.337 | 36.065 | 0.89663 | 46.489 | 0.31808 | 0.18101 | 0.49909 | 0.015904 | 0.0090504 | 0.024954 | 1.5471 |  | 0 | 0 | 10.0542 | 0 | 0 | 10.0542 | 0 | 0 | 9999
Commercial EM-Retro-Restaurant |  | 5 | 45.8306 | 1.3744 | 13.1202 | 0 | 0 |  |  |  | 49.2585 | 0.0092599 | 0.0091931 | 1.3882 | 0 | 0 | 2.6163 | 6.046 | 0 | 36.856 | 0.78721 | 1.8368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4036 | 7.8828 | 0 | 36.856 | 48.1424 | 25.637 | 3.272 | 0 | 0 | 28.909 | 3.4036 | 8.4938 | 25.637 | 3.8731 | 0 | 0 | 29.5101 | 7.8828 | 3.7436 | 25.637 | 7.145 | 0 | 0 | 32.7821 | 11.2864 | 6.1863 | 2.9046 | 5.0842 | 11.7752 | 0 | 55.0551 | 71.9145 | 25.637 | 9.0215 | 7.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.5184 | 2.624 | 0 | 0 | 41.8035 | 48.1424 | 0.86833 | 47.7652 | 0.46796 | 0.16242 | 0.63038 | 0.023398 | 0.0081208 | 0.031519 | 1.3882 |  | 0 | 0 | 9.0215 | 0 | 0 | 9.0215 | 0 | 0 | 9999
Commercial EM-Retro-Medium Off |  | 5 | 83.9333 | 1.9209 | 23.5813 | 0 | 0 |  |  |  | 90.2112 | 0.016958 | 0.016836 | 1.9402 | 0 | 0 | 4.7024 | 10.8666 | 0 | 66.2424 | 1.4149 | 3.3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1173 | 14.168 | 0 | 66.2424 | 86.5277 | 46.9512 | 5.9922 | 0 | 0 | 52.9434 | 6.1173 | 8.6547 | 46.9512 | 7.093 | 0 | 0 | 54.0442 | 14.168 | 3.8145 | 46.9512 | 13.0853 | 0 | 0 | 60.0365 | 20.2853 | 5.8728 | 2.9596 | 4.9897 | 11.5563 | 0 | 54.0314 | 70.5773 | 46.9512 | 12.6088 | 13.0853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8114 | 4.7163 | 0 | 0 | 72.6452 | 86.5277 | 0.83956 | 49.6197 | 0.85701 | 0.227 | 1.084 | 0.04285 | 0.01135 | 0.0542 | 1.9402 |  | 0 | 0 | 12.6088 | 0 | 0 | 12.6088 | 0 | 0 | 9999
Commercial EM-Retro-Warehouse |  | 5 | 27.0054 | 3.2318 | 14.5926 | 0 | 0 |  |  |  | 29.0253 | 0.0054564 | 0.005417 | 3.2641 | 0 | 0 | 2.91 | 6.7245 | 0 | 40.992 | 0.87555 | 2.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7855 | 8.7674 | 0 | 40.992 | 53.5449 | 15.1065 | 1.928 | 0 | 0 | 17.0345 | 3.7855 | 4.4999 | 15.1065 | 2.2822 | 0 | 0 | 17.3886 | 8.7674 | 1.9833 | 15.1065 | 4.2102 | 0 | 0 | 19.3166 | 12.5529 | 21.1496 | 1.5388 | 9.5966 | 22.2262 | 0 | 103.9184 | 135.7411 | 15.1065 | 21.2131 | 4.2102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.6264 | 2.9185 | 0 | 0 | 40.5298 | 53.5449 | 0.75693 | 71.2908 | 0.27574 | 0.3819 | 0.65765 | 0.013787 | 0.019095 | 0.032882 | 3.2641 |  | 0 | 0 | 21.2131 | 0 | 0 | 21.2131 | 0 | 0 | 9999
Commercial EM-Retro-School K-12 |  | 5 | 185.3017 | 10.6832 | 82.3023 | 0 | 0 |  |  |  | 199.1614 | 0.03744 | 0.037169 | 10.79 | 0 | 0 | 16.4122 | 37.9261 | 0 | 231.1958 | 4.9381 | 11.5223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.3503 | 49.4484 | 0 | 231.1958 | 301.9945 | 103.6552 | 13.2292 | 0 | 0 | 116.8845 | 21.3503 | 5.4746 | 103.6552 | 15.6595 | 0 | 0 | 119.3147 | 49.4484 | 2.4129 | 103.6552 | 28.8887 | 0 | 0 | 132.5439 | 70.7987 | 15.484 | 1.8721 | 7.888 | 18.2691 | 0 | 85.4171 | 111.5743 | 103.6552 | 70.1226 | 28.8887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285.5341 | 16.4605 | 0 | 0 | 202.6665 | 301.9945 | 0.67109 | 74.9938 | 1.8921 | 1.2624 | 3.1545 | 0.094602 | 0.063122 | 0.15772 | 10.79 |  | 0 | 0 | 70.1226 | 0 | 0 | 70.1226 | 0 | 0 | 9999
Commercial EM-Retro-Medium Ret |  | 5 | 34.8525 | 0.95342 | 15.3782 | 0 | 0 |  |  |  | 37.4593 | 0.0070418 | 0.006991 | 0.96296 | 0 | 0 | 3.0666 | 7.0865 | 0 | 43.1989 | 0.92269 | 2.1529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9893 | 9.2394 | 0 | 43.1989 | 56.4276 | 19.496 | 2.4882 | 0 | 0 | 21.9843 | 3.9893 | 5.5108 | 19.496 | 2.9453 | 0 | 0 | 22.4413 | 9.2394 | 2.4289 | 19.496 | 5.4335 | 0 | 0 | 24.9296 | 13.2287 | 15.3122 | 1.8845 | 7.8362 | 18.1491 | 0 | 84.856 | 110.8414 | 19.496 | 6.2581 | 5.4335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.352 | 3.0756 | 0 | 0 | 31.1877 | 56.4276 | 0.5527 | 87.8753 | 0.35587 | 0.11267 | 0.46853 | 0.017793 | 0.0056333 | 0.023426 | 0.96296 |  | 0 | 0 | 6.2581 | 0 | 0 | 6.2581 | 0 | 0 | 9999
Commercial EM-Retro-Large Ret |  | 5 | 220.2563 | 10.8206 | 143.7545 | 0 | 0 |  |  |  | 236.7305 | 0.044502 | 0.044181 | 10.9288 | 0 | 0 | 28.6666 | 66.2441 | 0 | 403.8213 | 8.6253 | 20.1256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.2918 | 86.3697 | 0 | 403.8213 | 527.4829 | 123.2084 | 15.7247 | 0 | 0 | 138.9331 | 37.2918 | 3.7256 | 123.2084 | 18.6134 | 0 | 0 | 141.8218 | 86.3697 | 1.642 | 123.2084 | 34.3382 | 0 | 0 | 157.5465 | 123.6616 | 27.7639 | 1.274 | 11.5912 | 26.8459 | 0 | 125.5178 | 163.9549 | 123.2084 | 71.0243 | 34.3382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 498.732 | 28.7509 | 0 | 0 | 228.5709 | 527.4829 | 0.43332 | 131.2056 | 2.249 | 1.2787 | 3.5276 | 0.11245 | 0.063933 | 0.17638 | 10.9288 |  | 0 | 0 | 71.0243 | 0 | 0 | 71.0243 | 0 | 0 | 9999
Commercial EM-Retro-Small Off |  | 5 | 22.9817 | 0.37766 | 16.1766 | 0 | 0 |  |  |  | 24.7007 | 0.0046434 | 0.0046099 | 0.38143 | 0 | 0 | 3.2258 | 7.4544 | 0 | 45.4419 | 0.9706 | 2.2647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1964 | 9.7192 | 0 | 45.4419 | 59.3575 | 12.8557 | 1.6407 | 0 | 0 | 14.4964 | 4.1964 | 3.4545 | 12.8557 | 1.9421 | 0 | 0 | 14.7978 | 9.7192 | 1.5225 | 12.8557 | 3.5829 | 0 | 0 | 16.4386 | 13.9156 | 30.7805 | 1.1813 | 12.5009 | 28.9527 | 0 | 135.3684 | 176.8221 | 12.8557 | 2.4789 | 3.5829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.1221 | 3.2353 | 0 | 0 | 18.9174 | 59.3575 | 0.3187 | 158.7645 | 0.23466 | 0.044628 | 0.27929 | 0.011733 | 0.0022314 | 0.013964 | 0.38143 |  | 0 | 0 | 2.4789 | 0 | 0 | 2.4789 | 0 | 0 | 9999
Supply Curve Results; Categories sorted by TRC Net Levelized Cost
Totals for Categories with Benefits Exceeding Costs. Levelized cost is TRC Net Levelized Cost (Net of Benefits) | [12 empty] | Savings Allocation by Cost Bin and Month for Segments 1 | [12 empty] | Savings Allocation by Cost Bin and Month for Segments 2
| Totals Basis | Busbar Electric Savings in kWh | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Measures with B/C > 1.00 | 3146.8831 | 541.048 | 0 | 541.048 | 1877.0742 | 2746.421 | 1506.1189 | -2.3206 | 17.9688 | 1.5257 | 41.6363 | 197.3257 | 177.4278 | 204.1738 | 189.9472 | 193.9248 | 191.9593 | 182.3646 | 190.017 | 177.5366 | 202.4255 | 179.1356 | 195.0318 |  | 83.7765 | 71.9784 | 69.0424 | 72.0918 | 70.7317 | 62.0651 | 72.8723 | 59.7627 | 73.5743 | 66.0812 | 79.2839 | 84.3529
| Categories with B/C > 1.00 | 2524.4197 | 410.8722 | 82.1744 | 493.0467 | 1507.6261 | 2243.3321 | 1710.9235 | -0.371 | 16.8519 | 1.5273 | 34.1235 | 19.2785 | 17.3345 | 19.9476 | 18.5576 | 18.9463 | 18.7542 | 17.8168 | 18.5645 | 17.3451 | 19.7768 | 17.5014 | 19.0544 |  | 8.1849 | 7.0322 | 6.7454 | 7.0433 | 6.9104 | 6.0637 | 7.1195 | 5.8388 | 7.1881 | 6.4561 | 7.746 | 8.2412
Supply Curve Results: By TRC Net Levelized Cost - Net of Benefits
| Block 1: <= 0 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 2: <= 10 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 3: 10-20 mills/kWh | 1793.5958 | 259.2224 | 51.8445 | 311.0669 | 951.1726 | 1583.8197 | 1519.264 | -1.5251 | 12.3421 | 1.6646 | 24.0635 | 112.4677 | 101.1267 | 116.3708 | 108.2622 | 110.5293 | 109.409 | 103.9405 | 108.302 | 101.1887 | 115.3743 | 102.1 | 111.1602 |  | 47.7492 | 41.0247 | 39.3514 | 41.0894 | 40.3142 | 35.3746 | 41.5343 | 34.0623 | 41.9344 | 37.6636 | 45.1886 | 48.0777
| Block 4: 20-30 mills/kWh | 438.9567 | 89.4394 | 17.8879 | 107.3273 | 328.1827 | 408.8398 | 2141.8672 | 2.2239 | 24.7758 | 1.2485 | 6.2713 | 27.5248 | 24.7493 | 28.4801 | 26.4956 | 27.0504 | 26.7763 | 25.4379 | 26.5054 | 24.7645 | 28.2362 | 24.9875 | 27.2049 |  | 11.6859 | 10.0402 | 9.6307 | 10.056 | 9.8663 | 8.6574 | 10.1649 | 8.3363 | 10.2628 | 9.2176 | 11.0593 | 11.7663
| Block 5: 30-40 mills/kWh | 1017.3758 | 220.3339 | 44.0668 | 264.4006 | 808.4778 | 822.3391 | 2276.5919 | 3.0351 | 37.2937 | 1.0192 | 12.2804 | 63.7947 | 57.3618 | 66.0087 | 61.4092 | 62.6952 | 62.0598 | 58.9578 | 61.4318 | 57.397 | 65.4434 | 57.9139 | 63.0531 |  | 27.0847 | 23.2703 | 22.3212 | 23.307 | 22.8673 | 20.0654 | 23.5594 | 19.3211 | 23.7863 | 21.3638 | 25.6322 | 27.271
| Block 6: 40-50 mills/kWh | 1049.3074 | 263.3521 | 52.6704 | 316.0225 | 966.326 | 904.333 | 2638.2712 | 5.2129 | 42.6434 | 0.93679 | 13.6773 | 65.797 | 59.1621 | 68.0804 | 63.3366 | 64.663 | 64.0076 | 60.8083 | 63.3599 | 59.1984 | 67.4975 | 59.7316 | 65.0321 |  | 27.9347 | 24.0007 | 23.0217 | 24.0385 | 23.585 | 20.6952 | 24.2988 | 19.9275 | 24.5329 | 22.0343 | 26.4367 | 28.1269
| Block 7: 50-60 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 8: 60-70 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 9: 70-80 mills/kWh | 228.1867 | 96.8949 | 19.379 | 116.2739 | 355.5395 | 243.1963 | 4463.7105 | 16.2047 | 74.5228 | 0.68201 | 3.8121 | 14.3085 | 12.8656 | 14.805 | 13.7734 | 14.0619 | 13.9193 | 13.2236 | 13.7785 | 12.8735 | 14.6783 | 12.9895 | 14.1421 |  | 6.0748 | 5.2193 | 5.0064 | 5.2275 | 5.1289 | 4.5005 | 5.2841 | 4.3335 | 5.335 | 4.7917 | 5.749 | 6.1166
| Block 10: 80-90 mills/kWh | 37.4593 | 15.3782 | 3.0756 | 18.4538 | 56.4276 | 31.1877 | 4315.4909 | 15.3122 | 87.8753 | 0.5527 | 0.46853 | 2.3489 | 2.112 | 2.4304 | 2.2611 | 2.3084 | 2.285 | 2.1708 | 2.2619 | 2.1133 | 2.4096 | 2.1324 | 2.3216 |  | 0.99725 | 0.8568 | 0.82186 | 0.85815 | 0.84196 | 0.7388 | 0.86745 | 0.71139 | 0.8758 | 0.78661 | 0.94377 | 1.0041
| Block 11: 90-100 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 12: 100-110 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 13: 110-120 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 14: 120-130 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 15: 130-140 mills/kWh | 236.7305 | 143.7545 | 28.7509 | 172.5054 | 527.4829 | 228.5709 | 6383.4097 | 27.7639 | 131.2056 | 0.43332 | 3.5276 | 14.8442 | 13.3474 | 15.3594 | 14.2892 | 14.5884 | 14.4405 | 13.7187 | 14.2944 | 13.3555 | 15.2279 | 13.4758 | 14.6717 |  | 6.3023 | 5.4147 | 5.1938 | 5.4232 | 5.3209 | 4.669 | 5.482 | 4.4958 | 5.5348 | 4.9711 | 5.9643 | 6.3456
| Block 16: 140-150 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 17: 150-160 mills/kWh | 24.7007 | 16.1766 | 3.2353 | 19.412 | 59.3575 | 18.9174 | 6884.3814 | 30.7805 | 158.7645 | 0.3187 | 0.27929 | 1.5489 | 1.3927 | 1.6026 | 1.4909 | 1.5222 | 1.5067 | 1.4314 | 1.4915 | 1.3935 | 1.5889 | 1.4061 | 1.5309 |  | 0.65758 | 0.56498 | 0.54193 | 0.56587 | 0.55519 | 0.48716 | 0.57199 | 0.46909 | 0.5775 | 0.51869 | 0.62232 | 0.66211
| Block 18: 160-170 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 19: 170-180 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 20: 180-190 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 21: 190-200 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 22: > 200 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Shaped Savings Results; By Category and sorted by TRC BC ratio
[13 empty] | Savings Allocation by Cost Bin and Month for Segments 1 Feb: Savings Allocation by Category and Month for Segments 1 |  |  | Savings Allocation by Category and Month for Segments 2
Category | Measure | Busbar Savings | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Wholesale KW | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Commercial EM-Retro-MiniMart |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commercial EM-Retro-Hospital |  | 1641.1873 | 237.9665 | 47.5933 | 285.5598 | 873.1776 | 1467.4528 | 1524.2035 | -1.4953 | 11.6522 | 1.6806 | 22.3467 | 0.30852 | 102.9109 | 92.5336 | 106.4823 | 99.0628 | 101.1372 | 100.1121 | 95.1082 | 99.0992 | 92.5903 | 105.5706 | 93.4242 | 101.7145 |  | 43.6918 | 37.5387 | 36.0075 | 37.5979 | 36.8885 | 32.3687 | 38.0049 | 31.1679 | 38.3711 | 34.4632 | 41.3488 | 43.9924
Commercial EM-Retro-Residential Care |  | 152.4085 | 21.2559 | 4.2512 | 25.5071 | 77.995 | 116.3669 | 1466.0743 | -1.8453 | 19.7706 | 1.492 | 1.7168 | 0.028651 | 9.5568 | 8.5931 | 9.8885 | 9.1994 | 9.3921 | 9.2969 | 8.8322 | 9.2028 | 8.5984 | 9.8038 | 8.6758 | 9.4457 |  | 4.0574 | 3.486 | 3.3438 | 3.4915 | 3.4256 | 3.0059 | 3.5293 | 2.8944 | 3.5633 | 3.2004 | 3.8398 | 4.0853
Commercial EM-Retro-Small Ret |  | 155.3447 | 25.4638 | 5.0928 | 30.5566 | 93.4352 | 119.5107 | 1723.1078 | -0.29763 | 25.9451 | 1.2791 | 1.7661 | 0.029203 | 9.7409 | 8.7587 | 10.079 | 9.3767 | 9.573 | 9.476 | 9.0024 | 9.3801 | 8.764 | 9.9927 | 8.843 | 9.6277 |  | 4.1356 | 3.5532 | 3.4083 | 3.5588 | 3.4916 | 3.0638 | 3.5973 | 2.9502 | 3.632 | 3.2621 | 3.9138 | 4.164
Commercial EM-Retro-Other |  | 217.2361 | 50.3221 | 10.0644 | 60.3865 | 184.6483 | 228.9451 | 2435.072 | 3.9894 | 23.2921 | 1.2399 | 3.5827 | 0.040837 | 13.6218 | 12.2482 | 14.0946 | 13.1125 | 13.387 | 13.2514 | 12.589 | 13.1173 | 12.2557 | 13.9739 | 12.3661 | 13.4635 |  | 5.7833 | 4.9688 | 4.7661 | 4.9766 | 4.8828 | 4.2845 | 5.0305 | 4.1255 | 5.079 | 4.5617 | 5.4731 | 5.8231
Commercial EM-Retro-Supermarket |  | 66.3759 | 13.6535 | 2.7307 | 16.3842 | 50.0993 | 60.384 | 2162.3176 | 2.347 | 26.895 | 1.2053 | 0.92241 | 0.012478 | 4.1621 | 3.7424 | 4.3066 | 4.0065 | 4.0904 | 4.0489 | 3.8465 | 4.0079 | 3.7447 | 4.2697 | 3.7784 | 4.1137 |  | 1.7671 | 1.5182 | 1.4563 | 1.5206 | 1.4919 | 1.3091 | 1.5371 | 1.2605 | 1.5519 | 1.3938 | 1.6723 | 1.7792
Commercial EM-Retro-Lodging |  | 116.818 | 19.913 | 3.9826 | 23.8956 | 73.0675 | 83.4809 | 1791.8972 | 0.11658 | 31.737 | 1.1425 | 1.2131 | 0.02196 | 7.3251 | 6.5864 | 7.5793 | 7.0512 | 7.1988 | 7.1259 | 6.7697 | 7.0538 | 6.5905 | 7.5144 | 6.6498 | 7.2399 |  | 3.1099 | 2.672 | 2.563 | 2.6762 | 2.6257 | 2.304 | 2.7052 | 2.2185 | 2.7312 | 2.4531 | 2.9432 | 3.1313
Commercial EM-Retro-Assembly |  | 175.0492 | 42.2974 | 8.4595 | 50.7569 | 155.2033 | 167.1917 | 2540.0327 | 4.6214 | 33.2569 | 1.0772 | 2.5757 | 0.032907 | 10.9765 | 9.8696 | 11.3574 | 10.566 | 10.7873 | 10.678 | 10.1443 | 10.5699 | 9.8757 | 11.2602 | 9.9646 | 10.8489 |  | 4.6602 | 4.0039 | 3.8406 | 4.0102 | 3.9345 | 3.4524 | 4.0536 | 3.3244 | 4.0927 | 3.6758 | 4.4103 | 4.6922
Commercial EM-Retro-Large Off |  | 725.5086 | 158.1234 | 31.6247 | 189.7481 | 580.207 | 571.6665 | 2291.0727 | 3.1223 | 39.1624 | 0.98528 | 8.4917 | 0.13639 | 45.4931 | 40.9057 | 47.0719 | 43.792 | 44.709 | 44.2559 | 42.0439 | 43.8081 | 40.9308 | 46.6689 | 41.2994 | 44.9643 |  | 19.3145 | 16.5945 | 15.9176 | 16.6206 | 16.3071 | 14.309 | 16.8006 | 13.7782 | 16.9624 | 15.2349 | 18.2788 | 19.4474
Commercial EM-Retro-University |  | 876.3554 | 216.8218 | 43.3644 | 260.1862 | 795.5909 | 757.5473 | 2600.8064 | 4.9874 | 41.4905 | 0.95218 | 11.4638 | 0.16474 | 54.952 | 49.4107 | 56.8591 | 52.8972 | 54.0049 | 53.4575 | 50.7856 | 52.9166 | 49.4411 | 56.3722 | 49.8863 | 54.3132 |  | 23.3304 | 20.0448 | 19.2272 | 20.0764 | 19.6976 | 17.2841 | 20.2937 | 16.6429 | 20.4892 | 18.4025 | 22.0793 | 23.4909
Commercial EM-Retro-Xlarge Ret |  | 33.4823 | 9.8288 | 1.9658 | 11.7945 | 36.065 | 32.337 | 3085.8102 | 7.9078 | 46.489 | 0.89663 | 0.49909 | 0.0062942 | 2.0995 | 1.8878 | 2.1724 | 2.021 | 2.0633 | 2.0424 | 1.9403 | 2.0217 | 1.889 | 2.1538 | 1.906 | 2.0751 |  | 0.89137 | 0.76584 | 0.7346 | 0.76704 | 0.75257 | 0.66036 | 0.77535 | 0.63586 | 0.78282 | 0.70309 | 0.84357 | 0.8975
Commercial EM-Retro-Restaurant |  | 49.2585 | 13.1202 | 2.624 | 15.7443 | 48.1424 | 41.8035 | 2799.9157 | 6.1863 | 47.7652 | 0.86833 | 0.63038 | 0.0092599 | 3.0888 | 2.7773 | 3.196 | 2.9733 | 3.0355 | 3.0048 | 2.8546 | 2.9744 | 2.779 | 3.1686 | 2.804 | 3.0529 |  | 1.3114 | 1.1267 | 1.0807 | 1.1285 | 1.1072 | 0.97151 | 1.1407 | 0.93547 | 1.1517 | 1.0344 | 1.241 | 1.3204
Commercial EM-Retro-Medium Off |  | 90.2112 | 23.5813 | 4.7163 | 28.2976 | 86.5277 | 72.6452 | 2747.8526 | 5.8728 | 49.6197 | 0.83956 | 1.084 | 0.016958 | 5.6567 | 5.0863 | 5.853 | 5.4452 | 5.5592 | 5.5029 | 5.2278 | 5.4472 | 5.0894 | 5.8029 | 5.1352 | 5.5909 |  | 2.4016 | 2.0634 | 1.9792 | 2.0666 | 2.0277 | 1.7792 | 2.089 | 1.7132 | 2.1091 | 1.8943 | 2.2728 | 2.4181
Commercial EM-Retro-Warehouse |  | 29.0253 | 14.5926 | 2.9185 | 17.5111 | 53.5449 | 40.5298 | 5284.9367 | 21.1496 | 71.2908 | 0.75693 | 0.65765 | 0.0054564 | 1.82 | 1.6365 | 1.8832 | 1.752 | 1.7887 | 1.7705 | 1.682 | 1.7526 | 1.6375 | 1.8671 | 1.6523 | 1.7989 |  | 0.77271 | 0.66389 | 0.63681 | 0.66494 | 0.65239 | 0.57246 | 0.67214 | 0.55122 | 0.67861 | 0.6095 | 0.73128 | 0.77803
Commercial EM-Retro-School K-12 |  | 199.1614 | 82.3023 | 16.4605 | 98.7628 | 301.9945 | 202.6665 | 4344.0268 | 15.484 | 74.9938 | 0.67109 | 3.1545 | 0.03744 | 12.4884 | 11.2291 | 12.9218 | 12.0215 | 12.2732 | 12.1488 | 11.5416 | 12.0259 | 11.236 | 12.8112 | 11.3372 | 12.3433 |  | 5.3021 | 4.5554 | 4.3696 | 4.5626 | 4.4765 | 3.928 | 4.612 | 3.7823 | 4.6564 | 4.1822 | 5.0178 | 5.3386
Commercial EM-Retro-Medium Ret |  | 37.4593 | 15.3782 | 3.0756 | 18.4538 | 56.4276 | 31.1877 | 4315.4909 | 15.3122 | 87.8753 | 0.5527 | 0.46853 | 0.0070418 | 2.3489 | 2.112 | 2.4304 | 2.2611 | 2.3084 | 2.285 | 2.1708 | 2.2619 | 2.1133 | 2.4096 | 2.1324 | 2.3216 |  | 0.99725 | 0.8568 | 0.82186 | 0.85815 | 0.84196 | 0.7388 | 0.86745 | 0.71139 | 0.8758 | 0.78661 | 0.94377 | 1.0041
Commercial EM-Retro-Large Ret |  | 236.7305 | 143.7545 | 28.7509 | 172.5054 | 527.4829 | 228.5709 | 6383.4097 | 27.7639 | 131.2056 | 0.43332 | 3.5276 | 0.044502 | 14.8442 | 13.3474 | 15.3594 | 14.2892 | 14.5884 | 14.4405 | 13.7187 | 14.2944 | 13.3555 | 15.2279 | 13.4758 | 14.6717 |  | 6.3023 | 5.4147 | 5.1938 | 5.4232 | 5.3209 | 4.669 | 5.482 | 4.4958 | 5.5348 | 4.9711 | 5.9643 | 6.3456
Commercial EM-Retro-Small Off |  | 24.7007 | 16.1766 | 3.2353 | 19.412 | 59.3575 | 18.9174 | 6884.3814 | 30.7805 | 158.7645 | 0.3187 | 0.27929 | 0.0046434 | 1.5489 | 1.3927 | 1.6026 | 1.4909 | 1.5222 | 1.5067 | 1.4314 | 1.4915 | 1.3935 | 1.5889 | 1.4061 | 1.5309 |  | 0.65758 | 0.56498 | 0.54193 | 0.56587 | 0.55519 | 0.48716 | 0.57199 | 0.46909 | 0.5775 | 0.51869 | 0.62232 | 0.66211
Note on I6: :ProCost Perioodic replacement costs and savinsg of the measure. These are costs and savings that occur periodicially, but at different periods than annually. Can be positive or negative. Periodic replacement costs for both the measure and the baseline measure should be included if applicable. ProCost can analysze these costs in two ways dependent on the 'Repeat Periodic Replacemetn' switch in the ProData page. When set to 'On', ProCost repeats replacement costs for multiple times over the life of a measure depending on the input period and measure life. For example fluorescent lamps may have a 4-year replacement cycle that repeats 3 times in a 15-year measure life. When set to 'Off', ProCost reads the period as the year after installation that the replacement cost occurs and does not subsequently reinstall or repeat the replacement costs. For example a compressor may be replaced only once in the life of a heat-pump system. Example: A new fluorescent lighting systems may have a measure life of 15 years, and a lamp life of five years. Two lamps lamps per fixture must be replaced at years 6 and 11. Lamp and labor costs, expressed as positive costs, are entered as a cost and the period would be enetered as 5. The baseline measure may have a four year lamp life and would have required a three-lamp replacement at years 5, 9 and 13. Lamp and labor replacement costs would be entered as annual savings in dollars with a 4-year period. ProCost determines the net present value of the two cost streams.
Note on O6: :ProCost If the measure has gas savings for incfreases, enter the annual savings and shape of the savings here. Example: Clothes washer saves electric motor and dryer energy and gas water heat.
Note on A7: :Procost Category for the measure. Individual measures can be grouped into categories. Procost output is reported by measure and by category. All measures must belong to at least one category. Category name can be the same as measure name. Example: Measures can be combined into one category if they have components with different load shapes or measure lives. On wash machines there may be one load shape for the electric motor savings component, a second load shape for the electric water heat savings component and a third shape for electric dryer savings component.
Note on B7: :ProCost Name of Measure. User-defined. For PTR measures, defined naming conventions apply.
Note on C7: :ProCost Annual electric savings for the measure in kWh at the site. May be positive, negative or zero. Savings are incremental to the baseline alternative.
Note on D7: :ProCost Physical life of the measure in years. Must be >=1.
Note on E7: :ProCost Initial cost to install the measure in dollars. Costs are incremental to the baseline alternative. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on F7: :ProCost Annaul opperations and maintenace cost for the measure in dollars. Must be incremental cost over the baseline alternative. May be positive, negative or zero. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page. O&M costs are enetered as positive values. Negative values represent O&M savings compared to the baseline alternative. Example: Annualized maintenace cost for a heat pump heating system compared to a baseline electric resistance heating system.
Note on G7: :ProCost Name of the pointer to the shape of the savings. The shapes represent the daily and monthly shape of the savings in four time segments for each month of the year. Shape of the savings is relative to the baseline alternative. These shaps are in the MC_AND_Loadshape file.
Note on H7: :ProCost Annual value of any non-energy benefits of the measure, relative to the baseline alternative. Expressed in dollars per year and denominated in dollars of the 'Cost Reference Year'. Positive value represents dollar savings. Negative value represents dollar cost. Example: Water, detergent and sewer savings from efficient clothes washer.
Note on I7: : Cost in dollars that is incurred for Period 1. Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on J7: :ProCost Duration of Period1. The time at which Period 1 costs, or savings, occur. In years.
Note on K7: : Cost in dollars that is incurred for Period 2 Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on L7: :ProCost Duration of Period 2. The time at which Period 2 costs, or savings, occur. In years.
Note on M7: : Cost in dollars that is incurred for Period 3. Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on N7: :ProCost Duration of Period 3. The time at which Period 3 costs, or savings, occur. In years.
Note on O7: : Annual gas savings, or increases, in therms.
Note on P7: :ProCost Name of the pointer to the shape of the savings. The shapes represent the daily and monthly shape of the savings in four time segments for each month of the year. Shape of the savings is relative to the baseline alternative. These shaps are in the MC_AND_Loadshape file.
Note on BH88: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BM88: Direct and program administrative costs of the measure to sponsor. Separate costs for each sponsor. Depends on share of costs incurred by sponsor, sponsor cost of capital, and financing term which are user-defined inputs. Includes applicable Capital, O&M, Periodic Replacement and Program Administrative costs. Sponsor costs are levelized over program life. Does not include any adjustments for benefit. NOTE: Units are per kWh for 'Electric' runs and per therm for 'Gas' runs for all sponsors.
Note on CE88: All costs minus all benefits regardless of which sponsor incurs the cost or accrues the benefits. TRC Net Levelized Cost includes all applicable costs and all benefits. In addition to energy system costs and benefits, TRC Net Levelized Cost includes non-energy, other-fuel, O&M, periodic-replacement and risk-mitigation benefits and costs. TRC Net Levelized Cost corresponds to TRC B/C ratios with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure. The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the TRC B/C ratio and the TRC Net Levelized Cost. If Risk-Mitigation credit is non-zero, TRC Levelized Cost will be reduced by the risk-mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on CW88: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BH147: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BM147: Direct and program administrative costs of the measure to sponsor. Separate costs for each sponsor. Depends on share of costs incurred by sponsor, sponsor cost of capital, and financing term which are user-defined inputs. Includes applicable Capital, O&M, Periodic Replacement and Program Administrative costs. Sponsor costs are levelized over program life. Does not include any adjustments for benefit. NOTE: Units are per kWh for 'Electric' runs and per therm for 'Gas' runs for all sponsors.
Note on CE147: All costs minus all benefits regardless of which sponsor incurs the cost or accrues the benefits. TRC Net Levelized Cost includes all applicable costs and all benefits. In addition to energy system costs and benefits, TRC Net Levelized Cost includes non-energy, other-fuel, O&M, periodic-replacement and risk-mitigation benefits and costs. TRC Net Levelized Cost corresponds to TRC B/C ratios with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure. The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the TRC B/C ratio and the TRC Net Levelized Cost. If Risk-Mitigation credit is non-zero, TRC Levelized Cost will be reduced by the risk-mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on CW147: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.

## Measure InputOutput-New_Out (hidden)
Shaped Savings Results; By Category and sorted by TRC BC ratio
[14 empty] | Savings Allocation by Category and Month for Segments 1 | [11 empty] | Savings Allocation by Category and Month for Segments 2
Category | Measure | Busbar Savings | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Wholesale KW | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Commercial EM-New-MiniMart |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commercial EM-New-Hospital |  | 1557.8749 | 237.9665 | 47.5933 | 285.5598 | 653.8149 | 1342.7047 | 1605.7152 | -1.0045 | 5.7585 | 2.0536 | 20.3076 | 0.29286 | 97.6868 | 87.8362 | 101.0769 | 94.034 | 96.0031 | 95.0301 | 90.2802 | 94.0686 | 87.8901 | 100.2114 | 88.6817 | 96.5511 | 41.4739 | 35.6331 | 34.1797 | 35.6893 | 35.016 | 30.7255 | 36.0757 | 29.5857 | 36.4232 | 32.7137 | 39.2498 | 41.7592
Commercial EM-New-Residential Care |  | 117.9787 | 21.2559 | 4.2512 | 25.5071 | 58.4008 | 114.8226 | 1893.9206 | 0.7309 | 3.1067 | 1.9661 | 1.7744 | 0.022178 | 7.3979 | 6.6519 | 7.6546 | 7.1212 | 7.2704 | 7.1967 | 6.837 | 7.1239 | 6.656 | 7.5891 | 6.7159 | 7.3119 | 3.1408 | 2.6985 | 2.5884 | 2.7028 | 2.6518 | 2.3269 | 2.732 | 2.2405 | 2.7583 | 2.4774 | 2.9724 | 3.1624
Commercial EM-New-Supermarket |  | 107.7437 | 23.9073 | 4.7815 | 28.6888 | 65.6855 | 102.2405 | 2332.5127 | 3.3718 | 13.3316 | 1.5565 | 1.5733 | 0.020254 | 6.7561 | 6.0748 | 6.9906 | 6.5035 | 6.6396 | 6.5723 | 6.2438 | 6.5058 | 6.0785 | 6.9307 | 6.1333 | 6.6775 | 2.8684 | 2.4644 | 2.3639 | 2.4683 | 2.4217 | 2.125 | 2.495 | 2.0462 | 2.5191 | 2.2625 | 2.7145 | 2.8881
Commercial EM-New-Lodging |  | 104.9849 | 19.913 | 3.9826 | 23.8956 | 54.7112 | 82.202 | 1993.8663 | 1.3327 | 19.0285 | 1.5025 | 1.2194 | 0.019736 | 6.5831 | 5.9193 | 6.8116 | 6.3369 | 6.4696 | 6.4041 | 6.084 | 6.3393 | 5.9229 | 6.7532 | 5.9762 | 6.5066 | 2.7949 | 2.4013 | 2.3034 | 2.4051 | 2.3597 | 2.0706 | 2.4311 | 1.9938 | 2.4546 | 2.2046 | 2.645 | 2.8141
Commercial EM-New-Small Ret |  | 134.8916 | 25.4638 | 5.0928 | 30.5566 | 69.9621 | 102.4954 | 1984.3765 | 1.2756 | 20.5497 | 1.465 | 1.5105 | 0.025358 | 8.4584 | 7.6055 | 8.7519 | 8.1421 | 8.3126 | 8.2284 | 7.8171 | 8.1451 | 7.6101 | 8.677 | 7.6787 | 8.3601 | 3.5911 | 3.0854 | 2.9595 | 3.0902 | 3.0319 | 2.6604 | 3.1237 | 2.5617 | 3.1538 | 2.8326 | 3.3985 | 3.6158
Commercial EM-New-Other |  | 183.0218 | 50.3221 | 10.0644 | 60.3865 | 138.2603 | 200.6699 | 2890.2874 | 6.7304 | 13.2052 | 1.4514 | 3.1586 | 0.034406 | 11.4764 | 10.3191 | 11.8747 | 11.0473 | 11.2786 | 11.1643 | 10.6063 | 11.0513 | 10.3255 | 11.773 | 10.4185 | 11.343 | 4.8724 | 4.1862 | 4.0155 | 4.1928 | 4.1137 | 3.6097 | 4.2382 | 3.4758 | 4.2791 | 3.8433 | 4.6111 | 4.9059
Commercial EM-New-Assembly |  | 153.8362 | 42.2974 | 8.4595 | 50.7569 | 116.2126 | 166.5991 | 2890.2874 | 6.7304 | 14.1958 | 1.4336 | 2.6176 | 0.028919 | 9.6463 | 8.6736 | 9.9811 | 9.2856 | 9.4801 | 9.384 | 8.9149 | 9.289 | 8.6789 | 9.8956 | 8.7571 | 9.5342 | 4.0954 | 3.5187 | 3.3752 | 3.5242 | 3.4577 | 3.0341 | 3.5624 | 2.9215 | 3.5967 | 3.2304 | 3.8758 | 4.1236
Commercial EM-New-Large Off |  | 918.5124 | 213.3173 | 42.6635 | 255.9808 | 586.0912 | 790.6352 | 2441.3296 | 4.0271 | 21.9103 | 1.349 | 11.9549 | 0.17267 | 57.5954 | 51.7876 | 59.5943 | 55.4418 | 56.6028 | 56.0291 | 53.2286 | 55.4622 | 51.8194 | 59.084 | 52.2861 | 56.9259 | 24.4527 | 21.009 | 20.1521 | 21.0421 | 20.6452 | 18.1156 | 21.27 | 17.4435 | 21.4749 | 19.2878 | 23.1414 | 24.6209
Commercial EM-New-Medium Off |  | 290.2939 | 87.8365 | 17.5673 | 105.4038 | 241.3317 | 278.2196 | 3180.6991 | 8.4791 | 28.9461 | 1.1529 | 4.2886 | 0.054571 | 18.2029 | 16.3674 | 18.8346 | 17.5223 | 17.8892 | 17.7079 | 16.8228 | 17.5287 | 16.3774 | 18.6734 | 16.5249 | 17.9913 | 7.7282 | 6.6399 | 6.369 | 6.6503 | 6.5249 | 5.7254 | 6.7223 | 5.513 | 6.7871 | 6.0959 | 7.3138 | 7.7814
Commercial EM-New-Restaurant |  | 47.1478 | 13.1202 | 2.624 | 15.7443 | 36.0479 | 41.422 | 2925.2634 | 6.941 | 29.9091 | 1.1491 | 0.62874 | 0.0088631 | 2.9564 | 2.6583 | 3.059 | 2.8459 | 2.9055 | 2.876 | 2.7323 | 2.8469 | 2.6599 | 3.0328 | 2.6839 | 2.922 | 1.2552 | 1.0784 | 1.0344 | 1.0801 | 1.0597 | 0.92988 | 1.0918 | 0.89539 | 1.1023 | 0.99005 | 1.1879 | 1.2638
Commercial EM-New-University |  | 786.8684 | 216.8218 | 43.3644 | 260.1862 | 595.7198 | 682.8233 | 2896.5844 | 6.7684 | 30.151 | 1.1462 | 10.3406 | 0.14792 | 49.3407 | 44.3653 | 51.053 | 47.4957 | 48.4903 | 47.9988 | 45.5997 | 47.5132 | 44.3925 | 50.6159 | 44.7923 | 48.7671 | 20.9481 | 17.998 | 17.2638 | 18.0263 | 17.6862 | 15.5192 | 18.2215 | 14.9435 | 18.397 | 16.5234 | 19.8247 | 21.0922
Commercial EM-New-Xlarge Ret |  | 32.4834 | 9.8288 | 1.9658 | 11.7945 | 27.0046 | 24.9506 | 3180.6991 | 8.4791 | 42.9489 | 0.92394 | 0.36859 | 0.0061064 | 2.0369 | 1.8315 | 2.1076 | 1.9607 | 2.0018 | 1.9815 | 1.8824 | 1.9614 | 1.8326 | 2.0895 | 1.8491 | 2.0132 | 0.86478 | 0.74299 | 0.71268 | 0.74416 | 0.73012 | 0.64066 | 0.75222 | 0.61689 | 0.75946 | 0.68212 | 0.8184 | 0.87072
Commercial EM-New-School K-12 |  | 181.5528 | 82.3023 | 16.4605 | 98.7628 | 226.1264 | 164.7382 | 4765.3485 | 18.0209 | 63.1763 | 0.72852 | 2.5153 | 0.034129 | 11.3843 | 10.2363 | 11.7794 | 10.9586 | 11.1881 | 11.0747 | 10.5211 | 10.9626 | 10.2426 | 11.6785 | 10.3348 | 11.2519 | 4.8333 | 4.1526 | 3.9833 | 4.1592 | 4.0807 | 3.5807 | 4.2042 | 3.4479 | 4.2447 | 3.8124 | 4.5741 | 4.8666
Commercial EM-New-Warehouse |  | 28.5557 | 14.5926 | 2.9185 | 17.5111 | 40.0932 | 25.5302 | 5371.8474 | 21.6729 | 75.8218 | 0.63677 | 0.38877 | 0.0053681 | 1.7906 | 1.61 | 1.8527 | 1.7236 | 1.7597 | 1.7419 | 1.6548 | 1.7243 | 1.611 | 1.8369 | 1.6255 | 1.7698 | 0.76021 | 0.65315 | 0.62651 | 0.65418 | 0.64184 | 0.5632 | 0.66126 | 0.5423 | 0.66763 | 0.59964 | 0.71944 | 0.76544
Commercial EM-New-Medium Ret |  | 35.0174 | 15.3782 | 3.0756 | 18.4538 | 42.2517 | 26.5827 | 4616.4313 | 17.1242 | 71.2214 | 0.62915 | 0.39169 | 0.0065828 | 2.1958 | 1.9744 | 2.272 | 2.1137 | 2.1579 | 2.1361 | 2.0293 | 2.1144 | 1.9756 | 2.2525 | 1.9934 | 2.1702 | 0.93224 | 0.80095 | 0.76828 | 0.80221 | 0.78708 | 0.69064 | 0.8109 | 0.66502 | 0.81871 | 0.73533 | 0.88224 | 0.93865
Commercial EM-New-Large Ret |  | 235.2764 | 143.7545 | 28.7509 | 172.5054 | 394.9668 | 171.7342 | 6422.861 | 28.0015 | 108.1114 | 0.43481 | 2.508 | 0.044229 | 14.753 | 13.2654 | 15.265 | 14.2014 | 14.4988 | 14.3518 | 13.6345 | 14.2066 | 13.2735 | 15.1343 | 13.3931 | 14.5815 | 6.2635 | 5.3815 | 5.1619 | 5.3899 | 5.2882 | 4.6403 | 5.4483 | 4.4681 | 5.5008 | 4.9406 | 5.9277 | 6.3066
Commercial EM-New-Small Off |  | 19.4538 | 16.1766 | 3.2353 | 19.412 | 44.4455 | 17.9325 | 8741.1718 | 41.961 | 138.5786 | 0.40347 | 0.27457 | 0.003657 | 1.2199 | 1.0968 | 1.2622 | 1.1742 | 1.1988 | 1.1867 | 1.1274 | 1.1747 | 1.0975 | 1.2514 | 1.1074 | 1.2057 | 0.5179 | 0.44496 | 0.42681 | 0.44567 | 0.43726 | 0.38368 | 0.45049 | 0.36945 | 0.45483 | 0.40851 | 0.49013 | 0.52146

## Measure InputOutput-New (hidden)
Data Set Name
Measure Index Name | Commercial EM
Costs must be denominated in the same year as 'Input Cost Reference Year' = |  | 2012
Savings per 1000 sf of floor area
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
Input Data | [7 empty] | Periodic Replacement Costs and Savings and Replacement Period | [5 empty] | Gas Inputs |  | Retro or LO | Early Retrofit Parameters
Category Name | Measure Name | Savings (kwh/yr) | Life (yrs) | Capital Cost | Annual O&M | Shape Pointer | Non-E Val ($/yr) | Cost 1 ($) | Period 1 | Cost 2 ($) | Period 2 | Cost 3 ($) | Period 3 | Savings (therms/yr) | Shape Pointer | R or L | Savings 2 (kWh) | Remaining Life (yrs) | Salvage Value ($)
Commercial EM-New-Large Off | Commercial EM-New-Large Off-GasHt | 657.3838 | 7 | 172.5156 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 27.3249 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Medium Off | Commercial EM-New-Medium Off-GasHt | 251.4791 | 7 | 81.7833 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 12.9537 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Small Off | Commercial EM-New-Small Off-GasHt | 11.9241 | 7 | 10.657 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0.75959 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Xlarge Ret | Commercial EM-New-Xlarge Ret-GasHt | 9.177 | 7 | 2.9844 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0.50772 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Large Ret | Commercial EM-New-Large Ret-GasHt | 45.9264 | 7 | 30.16 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 2.3089 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Medium Ret | Commercial EM-New-Medium Ret-GasHt | 13.8216 | 7 | 6.5238 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0.49944 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Small Ret | Commercial EM-New-Small Ret-GasHt | 56.16 | 7 | 11.3944 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 1.9385 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-School K-12 | Commercial EM-New-School K-12-GasHt | 89.6797 | 7 | 43.6948 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 6.6902 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-University | Commercial EM-New-University-GasHt | 534.7222 | 7 | 158.3634 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 24.2472 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Warehouse | Commercial EM-New-Warehouse-GasHt | 8.0674 | 7 | 4.431 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0.99425 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Supermarket | Commercial EM-New-Supermarket-GasHt | 88.6733 | 7 | 21.1474 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 4.6522 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-MiniMart | Commercial EM-New-MiniMart-GasHt | 0 | 7 | 0 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Restaurant | Commercial EM-New-Restaurant-GasHt | 38.7637 | 7 | 11.5939 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 1.5303 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Lodging | Commercial EM-New-Lodging-GasHt | 40.0566 | 7 | 10.6768 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 1.879 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Hospital | Commercial EM-New-Hospital-GasHt | 1075.3938 | 7 | 176.5536 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 46.6074 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Residential Care | Commercial EM-New-Residential Care-GasHt | 108.2051 | 7 | 20.9532 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 5.5313 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Assembly | Commercial EM-New-Assembly-GasHt | 141.0921 | 7 | 41.695 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 9.7839 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Other | Commercial EM-New-Other-GasHt | 115.5154 | 7 | 34.1367 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 12.0154 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Large Off | Commercial EM-New-Large Off-ElecHt | 104.2022 | 7 | 20.007 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Medium Off | Commercial EM-New-Medium Off-ElecHt | 15.4333 | 7 | 5.0191 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Small Off | Commercial EM-New-Small Off-ElecHt | 1.1501 | 7 | 1.0279 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Xlarge Ret | Commercial EM-New-Xlarge Ret-ElecHt | 15.7506 | 7 | 5.1222 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Large Ret | Commercial EM-New-Large Ret-ElecHt | 140.305 | 7 | 92.1387 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Medium Ret | Commercial EM-New-Medium Ret-ElecHt | 18.2971 | 7 | 8.6363 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Small Ret | Commercial EM-New-Small Ret-ElecHt | 25.0413 | 7 | 5.0807 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-School K-12 | Commercial EM-New-School K-12-ElecHt | 37.646 | 7 | 18.3423 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-University | Commercial EM-New-University-ElecHt | 116.3004 | 7 | 34.4435 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Warehouse | Commercial EM-New-Warehouse-ElecHt | 13.8461 | 7 | 7.6049 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Supermarket | Commercial EM-New-Supermarket-ElecHt | 1.5416 | 7 | 0.36764 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-MiniMart | Commercial EM-New-MiniMart-ElecHt | 0 | 7 | 0 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Restaurant | Commercial EM-New-Restaurant-ElecHt | 2.422 | 7 | 0.7244 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Lodging | Commercial EM-New-Lodging-ElecHt | 45.2759 | 7 | 6.8385 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Hospital | Commercial EM-New-Hospital-ElecHt | 149.4605 | 7 | 24.5378 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Residential Care | Commercial EM-New-Residential Care-ElecHt | 0.61562 | 7 | 0.11921 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Assembly | Commercial EM-New-Assembly-ElecHt | 0.80273 | 7 | 0.23722 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Other | Commercial EM-New-Other-ElecHt | 40.9213 | 7 | 12.0929 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Large Off | Commercial EM-New-Large Off-HtPmpHt | 93.0069 | 7 | 20.7946 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Medium Off | Commercial EM-New-Medium Off-HtPmpHt | 3.1799 | 7 | 1.0341 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Small Off | Commercial EM-New-Small Off-HtPmpHt | 5.0258 | 7 | 4.4917 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Xlarge Ret | Commercial EM-New-Xlarge Ret-HtPmpHt | 5.2953 | 7 | 1.7221 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Large Ret | Commercial EM-New-Large Ret-HtPmpHt | 32.672 | 7 | 21.4558 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Medium Ret | Commercial EM-New-Medium Ret-HtPmpHt | 0.46185 | 7 | 0.21799 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Small Ret | Commercial EM-New-Small Ret-HtPmpHt | 44.3031 | 7 | 8.9887 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-School K-12 | Commercial EM-New-School K-12-HtPmpHt | 41.5928 | 7 | 20.2653 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-University | Commercial EM-New-University-HtPmpHt | 81.0874 | 7 | 24.0149 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Warehouse | Commercial EM-New-Warehouse-HtPmpHt | 4.655 | 7 | 2.5567 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Supermarket | Commercial EM-New-Supermarket-HtPmpHt | 10.031 | 7 | 2.3923 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-MiniMart | Commercial EM-New-MiniMart-HtPmpHt | 0 | 7 | 0 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Restaurant | Commercial EM-New-Restaurant-HtPmpHt | 2.6811 | 7 | 0.80189 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Lodging | Commercial EM-New-Lodging-HtPmpHt | 12.3465 | 7 | 2.3976 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Hospital | Commercial EM-New-Hospital-HtPmpHt | 224.6076 | 7 | 36.8751 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Residential Care | Commercial EM-New-Residential Care-HtPmpHt | 0.94779 | 7 | 0.18353 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Assembly | Commercial EM-New-Assembly-HtPmpHt | 1.2359 | 7 | 0.36522 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
Commercial EM-New-Other | Commercial EM-New-Other-HtPmpHt | 13.8485 | 7 | 4.0925 |  | C-All-HVAC-Vent-All-All-E | [7 empty] | 0 | R-All-HVAC-CAC-All-All-E | R
ProCost Results
Version: | ProCost 3.0 - Beta04
Run Time: | Thursday, 19 March , 2015 at 9:18 AM
Regurgitation of ProData input parameters which were used for this run
| Run Parameters |  | Run Parameters |  |  | Marginal Cost & Conservation Load Shape Parameters | [9 empty] | Sponsor Parameters | [5 empty] | Program Parameters |  |  | Utility System Parameters
| Run Type | Electric | Run Type | Electric |  | Marginal Costs and Savings Shape File | Q:\SeventhPlan\Conservation Analysis\Global EE Inputs\MC Files\MC_AND_LOADSHAPE_v3.0_24segment-7P-D9 - NewSegValues.xlsx |  |  | 6P MidC Final (with carbon) | [6 empty] | Customer | Wholesale Elec | Retail Elec | Nat Gas |  | Program Life (yrs) | 20 |  |  | Electric | Gas
| Negative B/C Ratios | Off | Negative B/C Ratios | Off |  | Marginal Elec Avoided Cost Input Worksheet | 7P Mid |  |  | Conservation Load Shapes | [5 empty] | Real After-Tax Cost of Capital | 0.068013 | 0.043878 | 0.053289 | 0.054479 |  | Program Start Date | 2016 |  | Bulk System T&D Loss Factor | 0.0040389 | 0.01
| Admin Cost @ Category Level | On | Admin Cost @ Category Level | On |  | Elec Savings Shape Input Worksheet | GLSShapes |  |  | 6P_Gas_Final | [5 empty] | Financial Life (years) | 12 | 12 | 1 | 1 |  | Present Value Time Zero | 2016 |  | Bulk System T&D Credit ($/kw-yr)($/dailytherm-yr) | 26 | 0
| Repeat Periodic Replacement | On | Repeat Periodic Replacement | On |  | Marginal Gas Avoided Cost Input Worksheet | 7P Gas |  |  | Conservation Load Shapes | [6 empty] | Customer | Wholesale Elec | Retail Elec | Nat Gas |  | Input Cost Reference Year | 2012 |  | Bulk System T&D I2R Loss Component (%) | 0.9 | N/A
[6 empty] | Gas Savings Shape Input Worksheet | GLSShapes | [8 empty] | Sponsor Share of Initial Capital Cost | 0.35 | 0.195 | 0.455 | 0 |  | Real Discount Rate | 0.04 |  | Local System Dist Loss Factor | 0.047399 | 0
| Run Type: | Electric |  |  |  | Marginal Elec CO2 per kWh Input Worksheet | CO2 lbs per kWh .95 |  |  | CO2 lbs per therm | [5 empty] | Sponsor Share of Annual O&M | 1 | 0 | 0 | 0 |  | Capital Real Escalation Rate | 0 |  | Local System Dist Credit ($/kw-yr)($/dailytherm-yr) | 31 | 0
| Negative B/C Ratios: | False: (Converts Negative B/C Ratios) |  |  |  | Marginal Gas CO2 per therm Input Worksheet | CO2 lbs per therm |  |  | Zero Dollars per ton CO2 | [5 empty] | Sponsor Share of Periodic Replacement Cost | 1 | 0 | 0 | 0 |  | Admin Cost (as % of Initial Capital Cost) | 0.2 |  | Local System Dist I2R Loss Component (%) | 0.7 | N/A
| Admin Cost / Category Level: | True: Admin Costs added at Category Results |  |  |  | Marginal Avoided Cost CO2 Input Worksheet | Zero Dollars per ton CO2 |  |  | LineLossShapes | [5 empty] | Sponsor Share of Admin Cost |  | 0.3 | 0.7 | 0 |  | Regional Act Conservation Credit (%) | 0 |  | Risk-Mitigation Credit (mills/kWh)(mills/therm) - Retro. | 0 | 0
| Periodic O&M Treatment: | True: (Periodic O&M Repeats over measure life) |  |  |  | Line Loss Shape Input Worksheet | LineLossShapes | [8 empty] | Last Year of Non-Customer O&M & Period Replacement |  | 20 |  |  |  | Report Annual Carbon Saved for Year | 2018 |  | Risk-Mitigation Credit (mills/kWh)(mills/therm) - Lost Op. | 0 | 0
Measure Results; Sorted in same order as input
Total Results |  | Measure Input Data | [8 empty] | Savings | [5 empty] | PV Capital |  |  |  | PV Admin |  |  |  | PV O&M |  |  |  | PV Periodic Repl. |  |  |  | Total PV Capital, O&M and Periodic Repl Costs |  |  |  |  | PV Wholesale Electric Utility Costs & Benefits | [6 empty] | PV Retail Electric Utility Costs & Benefits | [6 empty] | PV Electric Utility System Costs & Benefits | [5 empty] | Electric Utility System Economics |  | Sponsor Levelized Cost (mills/kwh) |  |  |  |  | PV Regional Costs & Benefits | [15 empty] | TRC Economics |  | Physical CO2 | [5 empty] | Gas Inputs |  |  |  | PV Gas Utility System Costs & Benefits |  |  |  |  | Gas Utility System Economics
Category | Measure | Measure Life | Site Savings (kWh) | Site Savings (therms) | Capital Cost ($/unit) | Annual O&M Cost ($/unit) | PV Per. Repl. Cost ($/unit) | Load Shape (electric) | Diversified Load Factor (electric) | Wholesale Power Coincidence Factor (electric) | Wholesale Electric Energy (kWh) | Wholesale Electric Demand (kw) | Retail Electric Demand (kW) | Wholesale Gas Energy (therms/yr) | Wholesale Gas Demand (therms/day) | Retail Gas Demand (therms/day) | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Total | Wholesale Utility System Energy | Wholesale Utility System T&D Def. Cap. | Wholesale Utility System Act C-E Credit | Wholesale Utility System Risk Mitigation Benefit | Wholesale Utility System Total System Benefit | Wholesale Utility System Total Non-Consumer Cost | Wholesale Utility System B/C Ratio | Retail Utility System Energy | Retail Utility System T&D Def. Cap. | Retail Utility System Act C-E Credit | Retail Utility System Risk Mitigation Benefit | Retail Utility System Total System Benefit | Retail Utility System Total Non-Consumer Cost | Retail Utility System System B/C Ratio | Utility System Energy | Utility System T&D Def. Cap. | Utility System Act C-E Credit | Utility System Total Risk Mitigation Benefit | Utility System Total System Benefit | Utility System Total Non-Consumer Cost | Utility System Net Levelized Cost (Net of Elec T&D Capacity Benefits, Act Credit & Risk-Mitigation Benefit) in mills/kwh | Utility System System B/C Ratio | Wholesale Electric Levelized Cost | Retail Electric Levelized Cost | Natural Gas Levelized Cost | Customer Levelized Cost | Total Levelized Cost | PV Regional Electric Energy | PV Regional Gas Energy | PV Regional Electric T&D Def. Cap. | PV Regional Gas T&D Def. Cap. | PV Regional Electric System CO2 | PV Regional Gas System CO2 | PV Regional Electric System Risk-Mitigation Benefit | PV Regional Gas System Risk-Mitigation Benefit | PV Regional Non-E Value | PV Regional Act Credit | PV Regional Capital Cost | PV Regional Admin Cost | PV Regional Annual O&M Cost | PV Regional Periodic Replacement Cost | PV Total Regional Benefit | PV Total Regional Cost | TRC B/C Ratio | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | Electric System CO2 Avoided (Lifetime Tons) | Gas System CO2 Avoided (Lifetime Tons) | Total System CO2 Avoided (Lifetime Tons) | Electric System CO2 Avoided (Annual Tons in 2018) | Gas System CO2 Avoided (Annual Tons in 2018) | Total System CO2 Avoided (Annual Tons in 2018) | Gas Site Savings (therms) | Load Shape (gas) | Diversitfied Load Factor (gas) | Wholesale Coincidence Factor (gas) | Total Gas Utility System Energy | Gas Utility System T&D Def. Cap. | Gas Utility System Risk Mitigation Benefit | Gas Utility System Total System Benefit | Gas Utility System Total Non-Consumer Cost | Gas Utility System Net Levelized Cost (Net of Gas T&D Capacity Benefits & Risk-Mitigation Benefits) in cents/therm | Gas Utility System System B/C Ratio
Commercial EM-New-Large Off | Commercial EM-New-Large Off-GasHt | 7 | 657.3838 | 27.3249 | 172.5156 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 706.553 | 0.13282 | 0.13186 | 27.5981 | 0 | 0 | 34.4019 | 79.4976 | 0 | 325.5856 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.4019 | 79.4976 | 0 | 325.5856 | 439.4851 | 367.7315 | 46.9326 | 0 | 0 | 414.6641 | 34.4019 | 12.0535 | 367.7315 | 55.5542 | 0 | 0 | 423.2857 | 79.4976 | 5.3245 | 367.7315 | 102.4868 | 0 | 0 | 470.2182 | 113.8995 | 1.1885 | 4.1284 | 3.5827 | 8.279 | 0 | 33.9071 | 45.7688 | 367.7315 | 179.3558 | 102.4868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 439.4851 |  | 0 | 0 | 649.574 | 439.4851 | 1.478 | 16.4172 | 6.7123 | 3.229 | 9.9413 | 0.33561 | 0.16145 | 0.49706 | 27.3249 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 179.3558 | 0 | 0 | 179.3558 | 0 | 0 | 9999
Commercial EM-New-Medium Off | Commercial EM-New-Medium Off-GasHt | 7 | 251.4791 | 12.9537 | 81.7833 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 270.2885 | 0.050811 | 0.050444 | 13.0833 | 0 | 0 | 16.3087 | 37.6869 | 0 | 154.3482 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.3087 | 37.6869 | 0 | 154.3482 | 208.3438 | 140.6739 | 17.9538 | 0 | 0 | 158.6278 | 16.3087 | 9.7266 | 140.6739 | 21.252 | 0 | 0 | 161.9259 | 37.6869 | 4.2966 | 140.6739 | 39.2058 | 0 | 0 | 179.8798 | 53.9956 | 4.0263 | 3.3314 | 4.4398 | 10.2597 | 0 | 42.0188 | 56.7183 | 140.6739 | 85.026 | 39.2058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208.3438 |  | 0 | 0 | 264.9058 | 208.3438 | 1.2715 | 22.8981 | 2.5678 | 1.5307 | 4.0985 | 0.12839 | 0.076537 | 0.20492 | 12.9537 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 85.026 | 0 | 0 | 85.026 | 0 | 0 | 9999
Commercial EM-New-Small Off | Commercial EM-New-Small Off-GasHt | 7 | 11.9241 | 0.75959 | 10.657 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 12.816 | 0.0024092 | 0.0023918 | 0.76718 | 0 | 0 | 2.1252 | 4.9109 | 0 | 20.1128 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1252 | 4.9109 | 0 | 20.1128 | 27.1488 | 6.6702 | 0.8513 | 0 | 0 | 7.5215 | 2.1252 | 3.5393 | 6.6702 | 1.0077 | 0 | 0 | 7.6779 | 4.9109 | 1.5634 | 6.6702 | 1.859 | 0 | 0 | 8.5292 | 7.0361 | 29.7237 | 1.2122 | 12.2014 | 28.1955 | 0 | 115.4758 | 155.8727 | 6.6702 | 4.9858 | 1.859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.1488 |  | 0 | 0 | 13.515 | 27.1488 | 0.49781 | 116.574 | 0.12175 | 0.089761 | 0.21151 | 0.0060876 | 0.004488 | 0.010576 | 0.75959 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 4.9858 | 0 | 0 | 4.9858 | 0 | 0 | 9999
Commercial EM-New-Xlarge Ret | Commercial EM-New-Xlarge Ret-GasHt | 7 | 9.177 | 0.50772 | 2.9844 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 9.8634 | 0.0018542 | 0.0018408 | 0.5128 | 0 | 0 | 0.59514 | 1.3753 | 0 | 5.6325 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59514 | 1.3753 | 0 | 5.6325 | 7.6029 | 5.1335 | 0.65517 | 0 | 0 | 5.7887 | 0.59514 | 9.7266 | 5.1335 | 0.77553 | 0 | 0 | 5.909 | 1.3753 | 4.2966 | 5.1335 | 1.4307 | 0 | 0 | 6.5642 | 1.9704 | 4.0263 | 3.3314 | 4.4398 | 10.2597 | 0 | 42.0188 | 56.7183 | 5.1335 | 3.3326 | 1.4307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6029 |  | 0 | 0 | 9.8968 | 7.6029 | 1.3017 | 21.1835 | 0.093703 | 0.059998 | 0.1537 | 0.0046851 | 0.0029999 | 0.007685 | 0.50772 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 3.3326 | 0 | 0 | 3.3326 | 0 | 0 | 9999
Commercial EM-New-Large Ret | Commercial EM-New-Large Ret-GasHt | 7 | 45.9264 | 2.3089 | 30.16 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 49.3615 | 0.0092793 | 0.0092123 | 2.332 | 0 | 0 | 6.0143 | 13.8981 | 0 | 56.9204 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0143 | 13.8981 | 0 | 56.9204 | 76.8328 | 25.6906 | 3.2788 | 0 | 0 | 28.9694 | 6.0143 | 4.8168 | 25.6906 | 3.8811 | 0 | 0 | 29.5717 | 13.8981 | 2.1277 | 25.6906 | 7.16 | 0 | 0 | 32.8506 | 19.9124 | 19.0098 | 1.6497 | 8.9654 | 20.7176 | 0 | 84.8496 | 114.5326 | 25.6906 | 15.1553 | 7.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.8328 |  | 0 | 0 | 48.0059 | 76.8328 | 0.62481 | 81.2678 | 0.46894 | 0.27284 | 0.74178 | 0.023447 | 0.013642 | 0.037089 | 2.3089 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 15.1553 | 0 | 0 | 15.1553 | 0 | 0 | 9999
Commercial EM-New-Medium Ret | Commercial EM-New-Medium Ret-GasHt | 7 | 13.8216 | 0.49944 | 6.5238 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 14.8553 | 0.0027926 | 0.0027724 | 0.50443 | 0 | 0 | 1.3009 | 3.0063 | 0 | 12.3123 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3009 | 3.0063 | 0 | 12.3123 | 16.6196 | 7.7316 | 0.98676 | 0 | 0 | 8.7183 | 1.3009 | 6.7016 | 7.7316 | 1.168 | 0 | 0 | 8.8996 | 3.0063 | 2.9603 | 7.7316 | 2.1548 | 0 | 0 | 9.8864 | 4.3072 | 10.6614 | 2.2953 | 6.4438 | 14.8908 | 0 | 60.9857 | 82.3203 | 7.7316 | 3.2782 | 2.1548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6196 |  | 0 | 0 | 13.1646 | 16.6196 | 0.79211 | 55.4094 | 0.14113 | 0.059018 | 0.20015 | 0.0070563 | 0.0029509 | 0.010007 | 0.49944 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 3.2782 | 0 | 0 | 3.2782 | 0 | 0 | 9999
Commercial EM-New-Small Ret | Commercial EM-New-Small Ret-GasHt | 7 | 56.16 | 1.9385 | 11.3944 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 60.3605 | 0.011347 | 0.011265 | 1.9578 | 0 | 0 | 2.2722 | 5.2507 | 0 | 21.5045 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2722 | 5.2507 | 0 | 21.5045 | 29.0274 | 31.4151 | 4.0094 | 0 | 0 | 35.4246 | 2.2722 | 15.5905 | 31.4151 | 4.746 | 0 | 0 | 36.1611 | 5.2507 | 6.8869 | 31.4151 | 8.7554 | 0 | 0 | 40.1706 | 7.5229 | -1.5025 | 5.3398 | 2.7699 | 6.4008 | 0 | 26.2147 | 35.3854 | 31.4151 | 12.7237 | 8.7554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.0274 |  | 0 | 0 | 52.8942 | 29.0274 | 1.8222 | 9.2016 | 0.57343 | 0.22907 | 0.8025 | 0.028671 | 0.011453 | 0.040125 | 1.9385 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 12.7237 | 0 | 0 | 12.7237 | 0 | 0 | 9999
Commercial EM-New-School K-12 | Commercial EM-New-School K-12-GasHt | 7 | 89.6797 | 6.6902 | 43.6948 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 96.3874 | 0.01812 | 0.017989 | 6.7571 | 0 | 0 | 8.7133 | 20.1352 | 0 | 82.4643 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7133 | 20.1352 | 0 | 82.4643 | 111.3128 | 50.1656 | 6.4025 | 0 | 0 | 56.5681 | 8.7133 | 6.4921 | 50.1656 | 7.5787 | 0 | 0 | 57.7443 | 20.1352 | 2.8678 | 50.1656 | 13.9812 | 0 | 0 | 64.1468 | 28.8485 | 11.3497 | 2.2236 | 6.6517 | 15.3711 | 0 | 62.953 | 84.9758 | 50.1656 | 43.913 | 13.9812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.3128 |  | 0 | 0 | 108.0598 | 111.3128 | 0.97078 | 40.7796 | 0.91569 | 0.79058 | 1.7063 | 0.045784 | 0.039529 | 0.085313 | 6.6902 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 43.913 | 0 | 0 | 43.913 | 0 | 0 | 9999
Commercial EM-New-University | Commercial EM-New-University-GasHt | 7 | 534.7222 | 24.2472 | 158.3634 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 574.7169 | 0.10804 | 0.10726 | 24.4897 | 0 | 0 | 31.5798 | 72.9761 | 0 | 298.8763 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.5798 | 72.9761 | 0 | 298.8763 | 403.4321 | 299.1163 | 38.1754 | 0 | 0 | 337.2917 | 31.5798 | 10.6806 | 299.1163 | 45.1883 | 0 | 0 | 344.3046 | 72.9761 | 4.718 | 299.1163 | 83.3637 | 0 | 0 | 382.48 | 104.5558 | 2.7133 | 3.6581 | 4.0432 | 9.3432 | 0 | 38.2655 | 51.6519 | 299.1163 | 159.1543 | 83.3637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403.4321 |  | 0 | 0 | 541.6343 | 403.4321 | 1.3426 | 20.602 | 5.4599 | 2.8653 | 8.3252 | 0.27299 | 0.14326 | 0.41626 | 24.2472 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 159.1543 | 0 | 0 | 159.1543 | 0 | 0 | 9999
Commercial EM-New-Warehouse | Commercial EM-New-Warehouse-GasHt | 7 | 8.0674 | 0.99425 | 4.431 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 8.6708 | 0.00163 | 0.0016182 | 1.0042 | 0 | 0 | 0.88359 | 2.0418 | 0 | 8.3625 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88359 | 2.0418 | 0 | 8.3625 | 11.2879 | 4.5128 | 0.57595 | 0 | 0 | 5.0887 | 0.88359 | 5.7592 | 4.5128 | 0.68176 | 0 | 0 | 5.1945 | 2.0418 | 2.544 | 4.5128 | 1.2577 | 0 | 0 | 5.7705 | 2.9254 | 14.1526 | 1.9725 | 7.4983 | 17.3274 | 0 | 70.9651 | 95.7909 | 4.5128 | 6.5261 | 1.2577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.2879 |  | 0 | 0 | 12.2966 | 11.2879 | 1.0894 | 29.7364 | 0.082373 | 0.11749 | 0.19986 | 0.0041186 | 0.0058745 | 0.0099931 | 0.99425 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 6.5261 | 0 | 0 | 6.5261 | 0 | 0 | 9999
Commercial EM-New-Supermarket | Commercial EM-New-Supermarket-GasHt | 7 | 88.6733 | 4.6522 | 21.1474 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 95.3056 | 0.017916 | 0.017787 | 4.6987 | 0 | 0 | 4.2171 | 9.745 | 0 | 39.9111 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2171 | 9.745 | 0 | 39.9111 | 53.8732 | 49.6026 | 6.3306 | 0 | 0 | 55.9333 | 4.2171 | 13.2635 | 49.6026 | 7.4936 | 0 | 0 | 57.0962 | 9.745 | 5.859 | 49.6026 | 13.8243 | 0 | 0 | 63.4269 | 13.9621 | 0.10643 | 4.5428 | 3.2558 | 7.5238 | 0 | 30.8138 | 41.5934 | 49.6026 | 30.536 | 13.8243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.8732 |  | 0 | 0 | 93.9628 | 53.8732 | 1.7441 | 7.3446 | 0.90541 | 0.54975 | 1.4552 | 0.04527 | 0.027487 | 0.072757 | 4.6522 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 30.536 | 0 | 0 | 30.536 | 0 | 0 | 9999
Commercial EM-New-MiniMart | Commercial EM-New-MiniMart-GasHt | 7 | 0 | 0 | 0 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Restaurant | Commercial EM-New-Restaurant-GasHt | 7 | 38.7637 | 1.5303 | 11.5939 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 41.663 | 0.0078321 | 0.0077756 | 1.5456 | 0 | 0 | 2.312 | 5.3426 | 0 | 21.881 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.312 | 5.3426 | 0 | 21.881 | 29.5356 | 21.6839 | 2.7675 | 0 | 0 | 24.4513 | 2.312 | 10.5759 | 21.6839 | 3.2758 | 0 | 0 | 24.9597 | 5.3426 | 4.6718 | 21.6839 | 6.0433 | 0 | 0 | 27.7272 | 7.6546 | 2.8458 | 3.6223 | 4.0832 | 9.4357 | 0 | 38.6444 | 52.1633 | 21.6839 | 10.0447 | 6.0433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.5356 |  | 0 | 0 | 37.7719 | 29.5356 | 1.2789 | 23.7501 | 0.3958 | 0.18084 | 0.57664 | 0.01979 | 0.0090418 | 0.028832 | 1.5303 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 10.0447 | 0 | 0 | 10.0447 | 0 | 0 | 9999
Commercial EM-New-Lodging | Commercial EM-New-Lodging-GasHt | 7 | 40.0566 | 1.879 | 10.6768 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 43.0526 | 0.0080933 | 0.0080349 | 1.8978 | 0 | 0 | 2.1291 | 4.92 | 0 | 20.1502 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1291 | 4.92 | 0 | 20.1502 | 27.1994 | 22.4071 | 2.8598 | 0 | 0 | 25.2669 | 2.1291 | 11.8674 | 22.4071 | 3.3851 | 0 | 0 | 25.7922 | 4.92 | 5.2423 | 22.4071 | 6.2449 | 0 | 0 | 28.652 | 7.0491 | 1.3746 | 4.0646 | 3.6389 | 8.4089 | 0 | 34.439 | 46.4867 | 22.4071 | 12.3335 | 6.2449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.1994 |  | 0 | 0 | 40.9855 | 27.1994 | 1.5069 | 14.7342 | 0.409 | 0.22204 | 0.63105 | 0.02045 | 0.011102 | 0.031552 | 1.879 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 12.3335 | 0 | 0 | 12.3335 | 0 | 0 | 9999
Commercial EM-New-Hospital | Commercial EM-New-Hospital-GasHt | 7 | 1075.3938 | 46.6074 | 176.5536 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1155.8282 | 0.21728 | 0.21571 | 47.0735 | 0 | 0 | 35.2071 | 81.3583 | 0 | 333.2063 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.2071 | 81.3583 | 0 | 333.2063 | 449.7717 | 601.5606 | 76.7755 | 0 | 0 | 678.3361 | 35.2071 | 19.267 | 601.5606 | 90.8794 | 0 | 0 | 692.44 | 81.3583 | 8.511 | 601.5606 | 167.6549 | 0 | 0 | 769.2155 | 116.5655 | -3.2524 | 6.599 | 2.2413 | 5.1794 | 0 | 21.2124 | 28.6331 | 601.5606 | 305.923 | 167.6549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 449.7717 |  | 0 | 0 | 1075.1385 | 449.7717 | 2.3904 | -1.5155 | 10.9805 | 5.5076 | 16.4881 | 0.54902 | 0.27538 | 0.8244 | 46.6074 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 305.923 | 0 | 0 | 305.923 | 0 | 0 | 9999
Commercial EM-New-Residential Care | Commercial EM-New-Residential Care-GasHt | 7 | 108.2051 | 5.5313 | 20.9532 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 116.2983 | 0.021862 | 0.021705 | 5.5866 | 0 | 0 | 4.1783 | 9.6555 | 0 | 39.5445 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1783 | 9.6555 | 0 | 39.5445 | 53.3784 | 60.5284 | 7.7251 | 0 | 0 | 68.2535 | 4.1783 | 16.3351 | 60.5284 | 9.1442 | 0 | 0 | 69.6726 | 9.6555 | 7.2158 | 60.5284 | 16.8693 | 0 | 0 | 77.3977 | 13.8339 | -1.9205 | 5.5948 | 2.6436 | 6.109 | 0 | 25.0198 | 33.7724 | 60.5284 | 36.3066 | 16.8693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.3784 |  | 0 | 0 | 113.7043 | 53.3784 | 2.1302 | 0.12814 | 1.1048 | 0.65364 | 1.7585 | 0.055242 | 0.032682 | 0.087923 | 5.5313 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 36.3066 | 0 | 0 | 36.3066 | 0 | 0 | 9999
Commercial EM-New-Assembly | Commercial EM-New-Assembly-GasHt | 7 | 141.0921 | 9.7839 | 41.695 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 151.6451 | 0.028507 | 0.028301 | 9.8817 | 0 | 0 | 8.3145 | 19.2136 | 0 | 78.6902 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3145 | 19.2136 | 0 | 78.6902 | 106.2184 | 78.925 | 10.073 | 0 | 0 | 88.9979 | 8.3145 | 10.7039 | 78.925 | 11.9234 | 0 | 0 | 90.8484 | 19.2136 | 4.7283 | 78.925 | 21.9964 | 0 | 0 | 100.9214 | 27.5282 | 2.6842 | 3.6661 | 4.0344 | 9.3229 | 0 | 38.1823 | 51.5397 | 78.925 | 64.2195 | 21.9964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.2184 |  | 0 | 0 | 165.1409 | 106.2184 | 1.5547 | 9.7057 | 1.4406 | 1.1562 | 2.5968 | 0.072031 | 0.057808 | 0.12984 | 9.7839 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 64.2195 | 0 | 0 | 64.2195 | 0 | 0 | 9999
Commercial EM-New-Other | Commercial EM-New-Other-GasHt | 7 | 115.5154 | 12.0154 | 34.1367 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 124.1554 | 0.02334 | 0.023171 | 12.1356 | 0 | 0 | 6.8073 | 15.7307 | 0 | 64.4255 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8073 | 15.7307 | 0 | 64.4255 | 86.9635 | 64.6178 | 8.247 | 0 | 0 | 72.8647 | 6.8073 | 10.7039 | 64.6178 | 9.762 | 0 | 0 | 74.3797 | 15.7307 | 4.7283 | 64.6178 | 18.009 | 0 | 0 | 82.6267 | 22.538 | 2.6842 | 3.6661 | 4.0344 | 9.3229 | 0 | 38.1823 | 51.5397 | 64.6178 | 78.8671 | 18.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9635 |  | 0 | 0 | 161.4938 | 86.9635 | 1.857 | -5.8747 | 1.1795 | 1.4199 | 2.5993 | 0.058974 | 0.070993 | 0.12997 | 12.0154 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 78.8671 | 0 | 0 | 78.8671 | 0 | 0 | 9999
Commercial EM-New-Large Off | Commercial EM-New-Large Off-ElecHt | 7 | 104.2022 | 0 | 20.007 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 111.9961 | 0.021054 | 0.020902 | 0 | 0 | 0 | 3.9897 | 9.2195 | 0 | 37.7589 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9897 | 9.2195 | 0 | 37.7589 | 50.9681 | 58.2893 | 7.4393 | 0 | 0 | 65.7286 | 3.9897 | 16.4747 | 58.2893 | 8.8059 | 0 | 0 | 67.0952 | 9.2195 | 7.2775 | 58.2893 | 16.2452 | 0 | 0 | 74.5345 | 13.2092 | -1.9947 | 5.6426 | 2.6212 | 6.0573 | 0 | 24.8077 | 33.4862 | 58.2893 | 0 | 16.2452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.9681 |  | 0 | 0 | 74.5345 | 50.9681 | 1.4624 | 22.8131 | 1.064 | 0 | 1.064 | 0.053198 | 0 | 0.053198 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Medium Off | Commercial EM-New-Medium Off-ElecHt | 7 | 15.4333 | 0 | 5.0191 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 16.5877 | 0.0031183 | 0.0030958 | 0 | 0 | 0 | 1.0009 | 2.3129 | 0 | 9.4724 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0009 | 2.3129 | 0 | 9.4724 | 12.7861 | 8.6332 | 1.1018 | 0 | 0 | 9.735 | 1.0009 | 9.7266 | 8.6332 | 1.3042 | 0 | 0 | 9.9374 | 2.3129 | 4.2966 | 8.6332 | 2.4061 | 0 | 0 | 11.0393 | 3.3137 | 4.0263 | 3.3314 | 4.4398 | 10.2597 | 0 | 42.0188 | 56.7183 | 8.6332 | 0 | 2.4061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.7861 |  | 0 | 0 | 11.0393 | 12.7861 | 0.86338 | 46.0451 | 0.15758 | 0 | 0.15758 | 0.0078792 | 0 | 0.0078792 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Small Off | Commercial EM-New-Small Off-ElecHt | 7 | 1.1501 | 0 | 1.0279 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.2361 | 0.00023237 | 0.00023069 | 0 | 0 | 0 | 0.20497 | 0.47366 | 0 | 1.9399 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20497 | 0.47366 | 0 | 1.9399 | 2.6185 | 0.64334 | 0.082108 | 0 | 0 | 0.72545 | 0.20497 | 3.5393 | 0.64334 | 0.097192 | 0 | 0 | 0.74054 | 0.47366 | 1.5634 | 0.64334 | 0.1793 | 0 | 0 | 0.82264 | 0.67863 | 29.7237 | 1.2122 | 12.2014 | 28.1955 | 0 | 115.4758 | 155.8727 | 0.64334 | 0 | 0.1793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6185 |  | 0 | 0 | 0.82264 | 2.6185 | 0.31416 | 145.1996 | 0.011743 | 0 | 0.011743 | 0.00058715 | 0 | 0.00058715 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Xlarge Ret | Commercial EM-New-Xlarge Ret-ElecHt | 7 | 15.7506 | 0 | 5.1222 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 16.9286 | 0.0031823 | 0.0031594 | 0 | 0 | 0 | 1.0214 | 2.3604 | 0 | 9.6671 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0214 | 2.3604 | 0 | 9.6671 | 13.0489 | 8.8106 | 1.1245 | 0 | 0 | 9.9351 | 1.0214 | 9.7266 | 8.8106 | 1.331 | 0 | 0 | 10.1417 | 2.3604 | 4.2966 | 8.8106 | 2.4555 | 0 | 0 | 11.2662 | 3.3818 | 4.0263 | 3.3314 | 4.4398 | 10.2597 | 0 | 42.0188 | 56.7183 | 8.8106 | 0 | 2.4555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.0489 |  | 0 | 0 | 11.2662 | 13.0489 | 0.86338 | 46.0451 | 0.16082 | 0 | 0.16082 | 0.0080411 | 0 | 0.0080411 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Large Ret | Commercial EM-New-Large Ret-ElecHt | 7 | 140.305 | 0 | 92.1387 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 150.7992 | 0.028348 | 0.028144 | 0 | 0 | 0 | 18.3737 | 42.4588 | 0 | 173.8917 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.3737 | 42.4588 | 0 | 173.8917 | 234.7242 | 78.4847 | 10.0168 | 0 | 0 | 88.5015 | 18.3737 | 4.8168 | 78.4847 | 11.8569 | 0 | 0 | 90.3416 | 42.4588 | 2.1277 | 78.4847 | 21.8737 | 0 | 0 | 100.3584 | 60.8325 | 19.0098 | 1.6497 | 8.9654 | 20.7176 | 0 | 84.8496 | 114.5326 | 78.4847 | 0 | 21.8737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.7242 |  | 0 | 0 | 100.3584 | 234.7242 | 0.42756 | 103.8594 | 1.4326 | 0 | 1.4326 | 0.07163 | 0 | 0.07163 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Medium Ret | Commercial EM-New-Medium Ret-ElecHt | 7 | 18.2971 | 0 | 8.6363 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 19.6657 | 0.0036969 | 0.0036702 | 0 | 0 | 0 | 1.7222 | 3.9797 | 0 | 16.2992 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7222 | 3.9797 | 0 | 16.2992 | 22.0012 | 10.2352 | 1.3063 | 0 | 0 | 11.5415 | 1.7222 | 6.7016 | 10.2352 | 1.5463 | 0 | 0 | 11.7814 | 3.9797 | 2.9603 | 10.2352 | 2.8525 | 0 | 0 | 13.0877 | 5.7019 | 10.6614 | 2.2953 | 6.4438 | 14.8908 | 0 | 60.9857 | 82.3203 | 10.2352 | 0 | 2.8525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.0012 |  | 0 | 0 | 13.0877 | 22.0012 | 0.59486 | 71.6471 | 0.18683 | 0 | 0.18683 | 0.0093412 | 0 | 0.0093412 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Small Ret | Commercial EM-New-Small Ret-ElecHt | 7 | 25.0413 | 0 | 5.0807 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 26.9143 | 0.0050595 | 0.005023 | 0 | 0 | 0 | 1.0132 | 2.3412 | 0 | 9.5887 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0132 | 2.3412 | 0 | 9.5887 | 12.9431 | 14.0078 | 1.7878 | 0 | 0 | 15.7955 | 1.0132 | 15.5905 | 14.0078 | 2.1162 | 0 | 0 | 16.124 | 2.3412 | 6.8869 | 14.0078 | 3.904 | 0 | 0 | 17.9117 | 3.3544 | -1.5025 | 5.3398 | 2.7699 | 6.4008 | 0 | 26.2147 | 35.3854 | 14.0078 | 0 | 3.904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.9431 |  | 0 | 0 | 17.9117 | 12.9431 | 1.3839 | 24.7123 | 0.25569 | 0 | 0.25569 | 0.012784 | 0 | 0.012784 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-School K-12 | Commercial EM-New-School K-12-ElecHt | 7 | 37.646 | 0 | 18.3423 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 40.4617 | 0.0076062 | 0.0075514 | 0 | 0 | 0 | 3.6577 | 8.4524 | 0 | 34.6171 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6577 | 8.4524 | 0 | 34.6171 | 46.7271 | 21.0586 | 2.6877 | 0 | 0 | 23.7463 | 3.6577 | 6.4921 | 21.0586 | 3.1814 | 0 | 0 | 24.24 | 8.4524 | 2.8678 | 21.0586 | 5.869 | 0 | 0 | 26.9277 | 12.1101 | 11.3497 | 2.2236 | 6.6517 | 15.3711 | 0 | 62.953 | 84.9758 | 21.0586 | 0 | 5.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.7271 |  | 0 | 0 | 26.9277 | 46.7271 | 0.57627 | 74.3026 | 0.38439 | 0 | 0.38439 | 0.019219 | 0 | 0.019219 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-University | Commercial EM-New-University-ElecHt | 7 | 116.3004 | 0 | 34.4435 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 124.9991 | 0.023498 | 0.023329 | 0 | 0 | 0 | 6.8685 | 15.8721 | 0 | 65.0047 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8685 | 15.8721 | 0 | 65.0047 | 87.7452 | 65.0568 | 8.303 | 0 | 0 | 73.3599 | 6.8685 | 10.6806 | 65.0568 | 9.8283 | 0 | 0 | 74.8852 | 15.8721 | 4.718 | 65.0568 | 18.1313 | 0 | 0 | 83.1882 | 22.7406 | 2.7133 | 3.6581 | 4.0432 | 9.3432 | 0 | 38.2655 | 51.6519 | 65.0568 | 0 | 18.1313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7452 |  | 0 | 0 | 83.1882 | 87.7452 | 0.94807 | 40.9788 | 1.1875 | 0 | 1.1875 | 0.059375 | 0 | 0.059375 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Warehouse | Commercial EM-New-Warehouse-ElecHt | 7 | 13.8461 | 0 | 7.6049 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 14.8817 | 0.0027976 | 0.0027774 | 0 | 0 | 0 | 1.5165 | 3.5044 | 0 | 14.3525 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5165 | 3.5044 | 0 | 14.3525 | 19.3735 | 7.7453 | 0.98851 | 0 | 0 | 8.7338 | 1.5165 | 5.7592 | 7.7453 | 1.1701 | 0 | 0 | 8.9154 | 3.5044 | 2.544 | 7.7453 | 2.1586 | 0 | 0 | 9.9039 | 5.0209 | 14.1526 | 1.9725 | 7.4983 | 17.3274 | 0 | 70.9651 | 95.7909 | 7.7453 | 0 | 2.1586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.3735 |  | 0 | 0 | 9.9039 | 19.3735 | 0.51121 | 85.1177 | 0.14138 | 0 | 0.14138 | 0.0070688 | 0 | 0.0070688 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Supermarket | Commercial EM-New-Supermarket-ElecHt | 7 | 1.5416 | 0 | 0.36764 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.6569 | 0.00031147 | 0.00030922 | 0 | 0 | 0 | 0.073313 | 0.16941 | 0 | 0.69384 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073313 | 0.16941 | 0 | 0.69384 | 0.93657 | 0.86233 | 0.11006 | 0 | 0 | 0.97239 | 0.073313 | 13.2635 | 0.86233 | 0.13027 | 0 | 0 | 0.9926 | 0.16941 | 5.859 | 0.86233 | 0.24033 | 0 | 0 | 1.1027 | 0.24273 | 0.10643 | 4.5428 | 3.2558 | 7.5238 | 0 | 30.8138 | 41.5934 | 0.86233 | 0 | 0.24033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93657 |  | 0 | 0 | 1.1027 | 0.93657 | 1.1773 | 30.9202 | 0.01574 | 0 | 0.01574 | 0.00078701 | 0 | 0.00078701 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-MiniMart | Commercial EM-New-MiniMart-ElecHt | 7 | 0 | 0 | 0 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Restaurant | Commercial EM-New-Restaurant-ElecHt | 7 | 2.422 | 0 | 0.7244 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 2.6031 | 0.00048936 | 0.00048582 | 0 | 0 | 0 | 0.14445 | 0.33381 | 0 | 1.3671 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14445 | 0.33381 | 0 | 1.3671 | 1.8454 | 1.3548 | 0.17291 | 0 | 0 | 1.5277 | 0.14445 | 10.5759 | 1.3548 | 0.20468 | 0 | 0 | 1.5595 | 0.33381 | 4.6718 | 1.3548 | 0.37759 | 0 | 0 | 1.7324 | 0.47827 | 2.8458 | 3.6223 | 4.0832 | 9.4357 | 0 | 38.6444 | 52.1633 | 1.3548 | 0 | 0.37759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8454 |  | 0 | 0 | 1.7324 | 1.8454 | 0.93877 | 41.4902 | 0.02473 | 0 | 0.02473 | 0.0012365 | 0 | 0.0012365 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Lodging | Commercial EM-New-Lodging-ElecHt | 7 | 45.2759 | 0 | 6.8385 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 48.6623 | 0.0091479 | 0.0090818 | 0 | 0 | 0 | 1.3637 | 3.1513 | 0 | 12.9063 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3637 | 3.1513 | 0 | 12.9063 | 17.4213 | 25.3267 | 3.2324 | 0 | 0 | 28.5591 | 1.3637 | 20.9424 | 25.3267 | 3.8262 | 0 | 0 | 29.1529 | 3.1513 | 9.2511 | 25.3267 | 7.0586 | 0 | 0 | 32.3853 | 4.515 | -3.8461 | 7.1728 | 2.062 | 4.765 | 0 | 19.5154 | 26.3425 | 25.3267 | 0 | 7.0586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.4213 |  | 0 | 0 | 32.3853 | 17.4213 | 1.859 | 15.6693 | 0.4623 | 0 | 0.4623 | 0.023115 | 0 | 0.023115 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Hospital | Commercial EM-New-Hospital-ElecHt | 7 | 149.4605 | 0 | 24.5378 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 160.6395 | 0.030198 | 0.02998 | 0 | 0 | 0 | 4.8932 | 11.3074 | 0 | 46.3097 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8932 | 11.3074 | 0 | 46.3097 | 62.5102 | 83.6062 | 10.6704 | 0 | 0 | 94.2766 | 4.8932 | 19.267 | 83.6062 | 12.6306 | 0 | 0 | 96.2368 | 11.3074 | 8.511 | 83.6062 | 23.301 | 0 | 0 | 106.9072 | 16.2005 | -3.2524 | 6.599 | 2.2413 | 5.1794 | 0 | 21.2124 | 28.6331 | 83.6062 | 0 | 23.301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.5102 |  | 0 | 0 | 106.9072 | 62.5102 | 1.7102 | 17.96 | 1.5261 | 0 | 1.5261 | 0.076304 | 0 | 0.076304 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Residential Care | Commercial EM-New-Residential Care-ElecHt | 7 | 0.61562 | 0 | 0.11921 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.66167 | 0.00012438 | 0.00012349 | 0 | 0 | 0 | 0.023772 | 0.054934 | 0 | 0.22498 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023772 | 0.054934 | 0 | 0.22498 | 0.30369 | 0.34437 | 0.043951 | 0 | 0 | 0.38832 | 0.023772 | 16.3351 | 0.34437 | 0.052025 | 0 | 0 | 0.3964 | 0.054934 | 7.2158 | 0.34437 | 0.095976 | 0 | 0 | 0.44035 | 0.078706 | -1.9205 | 5.5948 | 2.6436 | 6.109 | 0 | 25.0198 | 33.7724 | 0.34437 | 0 | 0.095976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30369 |  | 0 | 0 | 0.44035 | 0.30369 | 1.45 | 23.0993 | 0.0062859 | 0 | 0.0062859 | 0.00031429 | 0 | 0.00031429 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Assembly | Commercial EM-New-Assembly-ElecHt | 7 | 0.80273 | 0 | 0.23722 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.86277 | 0.00016219 | 0.00016102 | 0 | 0 | 0 | 0.047305 | 0.10931 | 0 | 0.4477 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047305 | 0.10931 | 0 | 0.4477 | 0.60432 | 0.44904 | 0.057309 | 0 | 0 | 0.50634 | 0.047305 | 10.7039 | 0.44904 | 0.067837 | 0 | 0 | 0.51687 | 0.10931 | 4.7283 | 0.44904 | 0.12515 | 0 | 0 | 0.57418 | 0.15662 | 2.6842 | 3.6661 | 4.0344 | 9.3229 | 0 | 38.1823 | 51.5397 | 0.44904 | 0 | 0.12515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60432 |  | 0 | 0 | 0.57418 | 0.60432 | 0.95013 | 40.8665 | 0.0081964 | 0 | 0.0081964 | 0.00040982 | 0 | 0.00040982 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Other | Commercial EM-New-Other-ElecHt | 7 | 40.9213 | 0 | 12.0929 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 43.982 | 0.008268 | 0.0082083 | 0 | 0 | 0 | 2.4115 | 5.5726 | 0 | 22.8227 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4115 | 5.5726 | 0 | 22.8227 | 30.8068 | 22.8908 | 2.9215 | 0 | 0 | 25.8123 | 2.4115 | 10.7039 | 22.8908 | 3.4582 | 0 | 0 | 26.349 | 5.5726 | 4.7283 | 22.8908 | 6.3797 | 0 | 0 | 29.2705 | 7.9841 | 2.6842 | 3.6661 | 4.0344 | 9.3229 | 0 | 38.1823 | 51.5397 | 22.8908 | 0 | 6.3797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.8068 |  | 0 | 0 | 29.2705 | 30.8068 | 0.95013 | 40.8665 | 0.41783 | 0 | 0.41783 | 0.020891 | 0 | 0.020891 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Large Off | Commercial EM-New-Large Off-HtPmpHt | 7 | 93.0069 | 0 | 20.7946 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 99.9634 | 0.018792 | 0.018656 | 0 | 0 | 0 | 4.1467 | 9.5824 | 0 | 39.2453 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1467 | 9.5824 | 0 | 39.2453 | 52.9745 | 52.0268 | 6.64 | 0 | 0 | 58.6668 | 4.1467 | 14.1478 | 52.0268 | 7.8598 | 0 | 0 | 59.8866 | 9.5824 | 6.2496 | 52.0268 | 14.4999 | 0 | 0 | 66.5267 | 13.7292 | -0.5673 | 4.8456 | 3.0523 | 7.0535 | 0 | 28.8879 | 38.9938 | 52.0268 | 0 | 14.4999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.9745 |  | 0 | 0 | 66.5267 | 52.9745 | 1.2558 | 28.3207 | 0.94966 | 0 | 0.94966 | 0.047483 | 0 | 0.047483 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Medium Off | Commercial EM-New-Medium Off-HtPmpHt | 7 | 3.1799 | 0 | 1.0341 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 3.4177 | 0.00064249 | 0.00063785 | 0 | 0 | 0 | 0.20622 | 0.47654 | 0 | 1.9517 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20622 | 0.47654 | 0 | 1.9517 | 2.6345 | 1.7788 | 0.22702 | 0 | 0 | 2.0058 | 0.20622 | 9.7266 | 1.7788 | 0.26873 | 0 | 0 | 2.0475 | 0.47654 | 4.2966 | 1.7788 | 0.49575 | 0 | 0 | 2.2745 | 0.68276 | 4.0263 | 3.3314 | 4.4398 | 10.2597 | 0 | 42.0188 | 56.7183 | 1.7788 | 0 | 0.49575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6345 |  | 0 | 0 | 2.2745 | 2.6345 | 0.86338 | 46.0451 | 0.032469 | 0 | 0.032469 | 0.0016234 | 0 | 0.0016234 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Small Off | Commercial EM-New-Small Off-HtPmpHt | 7 | 5.0258 | 0 | 4.4917 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 5.4017 | 0.0010154 | 0.0010081 | 0 | 0 | 0 | 0.89571 | 2.0699 | 0 | 8.4772 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89571 | 2.0699 | 0 | 8.4772 | 11.4428 | 2.8114 | 0.35881 | 0 | 0 | 3.1702 | 0.89571 | 3.5393 | 2.8114 | 0.42472 | 0 | 0 | 3.2361 | 2.0699 | 1.5634 | 2.8114 | 0.78353 | 0 | 0 | 3.5949 | 2.9656 | 29.7237 | 1.2122 | 12.2014 | 28.1955 | 0 | 115.4758 | 155.8727 | 2.8114 | 0 | 0.78353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.4428 |  | 0 | 0 | 3.5949 | 11.4428 | 0.31416 | 145.1996 | 0.051317 | 0 | 0.051317 | 0.0025658 | 0 | 0.0025658 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Xlarge Ret | Commercial EM-New-Xlarge Ret-HtPmpHt | 7 | 5.2953 | 0 | 1.7221 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 5.6914 | 0.0010699 | 0.0010622 | 0 | 0 | 0 | 0.34341 | 0.79356 | 0 | 3.2501 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34341 | 0.79356 | 0 | 3.2501 | 4.387 | 2.9621 | 0.37805 | 0 | 0 | 3.3402 | 0.34341 | 9.7266 | 2.9621 | 0.4475 | 0 | 0 | 3.4096 | 0.79356 | 4.2966 | 2.9621 | 0.82554 | 0 | 0 | 3.7877 | 1.137 | 4.0263 | 3.3314 | 4.4398 | 10.2597 | 0 | 42.0188 | 56.7183 | 2.9621 | 0 | 0.82554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.387 |  | 0 | 0 | 3.7877 | 4.387 | 0.86338 | 46.0451 | 0.054068 | 0 | 0.054068 | 0.0027034 | 0 | 0.0027034 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Large Ret | Commercial EM-New-Large Ret-HtPmpHt | 7 | 32.672 | 0 | 21.4558 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 35.1157 | 0.0066013 | 0.0065536 | 0 | 0 | 0 | 4.2786 | 9.8871 | 0 | 40.4931 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2786 | 9.8871 | 0 | 40.4931 | 54.6589 | 18.2763 | 2.3326 | 0 | 0 | 20.6088 | 4.2786 | 4.8168 | 18.2763 | 2.761 | 0 | 0 | 21.0373 | 9.8871 | 2.1277 | 18.2763 | 5.0936 | 0 | 0 | 23.3699 | 14.1657 | 19.0098 | 1.6497 | 8.9654 | 20.7176 | 0 | 84.8496 | 114.5326 | 18.2763 | 0 | 5.0936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.6589 |  | 0 | 0 | 23.3699 | 54.6589 | 0.42756 | 103.8594 | 0.3336 | 0 | 0.3336 | 0.01668 | 0 | 0.01668 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Medium Ret | Commercial EM-New-Medium Ret-HtPmpHt | 7 | 0.46185 | 0 | 0.21799 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.49639 | 9.3315e-05 | 9.2642e-05 | 0 | 0 | 0 | 0.043471 | 0.10046 | 0 | 0.41142 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043471 | 0.10046 | 0 | 0.41142 | 0.55534 | 0.25835 | 0.032973 | 0 | 0 | 0.29132 | 0.043471 | 6.7016 | 0.25835 | 0.03903 | 0 | 0 | 0.29738 | 0.10046 | 2.9603 | 0.25835 | 0.072003 | 0 | 0 | 0.33035 | 0.14393 | 10.6614 | 2.2953 | 6.4438 | 14.8908 | 0 | 60.9857 | 82.3203 | 0.25835 | 0 | 0.072003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55534 |  | 0 | 0 | 0.33035 | 0.55534 | 0.59486 | 71.6471 | 0.0047158 | 0 | 0.0047158 | 0.00023579 | 0 | 0.00023579 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Small Ret | Commercial EM-New-Small Ret-HtPmpHt | 7 | 44.3031 | 0 | 8.9887 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 47.6168 | 0.0089513 | 0.0088867 | 0 | 0 | 0 | 1.7925 | 4.1421 | 0 | 16.9643 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7925 | 4.1421 | 0 | 16.9643 | 22.8989 | 24.7826 | 3.1629 | 0 | 0 | 27.9455 | 1.7925 | 15.5905 | 24.7826 | 3.744 | 0 | 0 | 28.5265 | 4.1421 | 6.8869 | 24.7826 | 6.9069 | 0 | 0 | 31.6895 | 5.9346 | -1.5025 | 5.3398 | 2.7699 | 6.4008 | 0 | 26.2147 | 35.3854 | 24.7826 | 0 | 6.9069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8989 |  | 0 | 0 | 31.6895 | 22.8989 | 1.3839 | 24.7123 | 0.45236 | 0 | 0.45236 | 0.022618 | 0 | 0.022618 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-School K-12 | Commercial EM-New-School K-12-HtPmpHt | 7 | 41.5928 | 0 | 20.2653 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 44.7037 | 0.0084037 | 0.008343 | 0 | 0 | 0 | 4.0412 | 9.3385 | 0 | 38.2463 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0412 | 9.3385 | 0 | 38.2463 | 51.626 | 23.2664 | 2.9694 | 0 | 0 | 26.2359 | 4.0412 | 6.4921 | 23.2664 | 3.5149 | 0 | 0 | 26.7813 | 9.3385 | 2.8678 | 23.2664 | 6.4844 | 0 | 0 | 29.7508 | 13.3797 | 11.3497 | 2.2236 | 6.6517 | 15.3711 | 0 | 62.953 | 84.9758 | 23.2664 | 0 | 6.4844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.626 |  | 0 | 0 | 29.7508 | 51.626 | 0.57627 | 74.3026 | 0.42469 | 0 | 0.42469 | 0.021234 | 0 | 0.021234 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-University | Commercial EM-New-University-HtPmpHt | 7 | 81.0874 | 0 | 24.0149 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 87.1524 | 0.016383 | 0.016265 | 0 | 0 | 0 | 4.7889 | 11.0664 | 0 | 45.3228 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7889 | 11.0664 | 0 | 45.3228 | 61.1781 | 45.3592 | 5.7891 | 0 | 0 | 51.1483 | 4.7889 | 10.6806 | 45.3592 | 6.8525 | 0 | 0 | 52.2117 | 11.0664 | 4.718 | 45.3592 | 12.6416 | 0 | 0 | 58.0008 | 15.8553 | 2.7133 | 3.6581 | 4.0432 | 9.3432 | 0 | 38.2655 | 51.6519 | 45.3592 | 0 | 12.6416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.1781 |  | 0 | 0 | 58.0008 | 61.1781 | 0.94807 | 40.9788 | 0.82796 | 0 | 0.82796 | 0.041397 | 0 | 0.041397 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Warehouse | Commercial EM-New-Warehouse-HtPmpHt | 7 | 4.655 | 0 | 2.5567 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 5.0032 | 0.00094053 | 0.00093375 | 0 | 0 | 0 | 0.50985 | 1.1782 | 0 | 4.8253 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50985 | 1.1782 | 0 | 4.8253 | 6.5133 | 2.604 | 0.33234 | 0 | 0 | 2.9363 | 0.50985 | 5.7592 | 2.604 | 0.39339 | 0 | 0 | 2.9973 | 1.1782 | 2.544 | 2.604 | 0.72572 | 0 | 0 | 3.3297 | 1.688 | 14.1526 | 1.9725 | 7.4983 | 17.3274 | 0 | 70.9651 | 95.7909 | 2.604 | 0 | 0.72572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5133 |  | 0 | 0 | 3.3297 | 6.5133 | 0.51121 | 85.1177 | 0.047531 | 0 | 0.047531 | 0.0023765 | 0 | 0.0023765 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Supermarket | Commercial EM-New-Supermarket-HtPmpHt | 7 | 10.031 | 0 | 2.3923 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 10.7812 | 0.0020267 | 0.0020121 | 0 | 0 | 0 | 0.47705 | 1.1024 | 0 | 4.5148 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47705 | 1.1024 | 0 | 4.5148 | 6.0943 | 5.6112 | 0.71614 | 0 | 0 | 6.3273 | 0.47705 | 13.2635 | 5.6112 | 0.8477 | 0 | 0 | 6.4589 | 1.1024 | 5.859 | 5.6112 | 1.5638 | 0 | 0 | 7.175 | 1.5794 | 0.10643 | 4.5428 | 3.2558 | 7.5238 | 0 | 30.8138 | 41.5934 | 5.6112 | 0 | 1.5638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0943 |  | 0 | 0 | 7.175 | 6.0943 | 1.1773 | 30.9202 | 0.10242 | 0 | 0.10242 | 0.0051211 | 0 | 0.0051211 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-MiniMart | Commercial EM-New-MiniMart-HtPmpHt | 7 | 0 | 0 | 0 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Restaurant | Commercial EM-New-Restaurant-HtPmpHt | 7 | 2.6811 | 0 | 0.80189 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 2.8816 | 0.0005417 | 0.00053779 | 0 | 0 | 0 | 0.15991 | 0.36952 | 0 | 1.5134 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15991 | 0.36952 | 0 | 1.5134 | 2.0428 | 1.4998 | 0.19141 | 0 | 0 | 1.6912 | 0.15991 | 10.5759 | 1.4998 | 0.22657 | 0 | 0 | 1.7263 | 0.36952 | 4.6718 | 1.4998 | 0.41798 | 0 | 0 | 1.9177 | 0.52943 | 2.8458 | 3.6223 | 4.0832 | 9.4357 | 0 | 38.6444 | 52.1633 | 1.4998 | 0 | 0.41798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0428 |  | 0 | 0 | 1.9177 | 2.0428 | 0.93877 | 41.4902 | 0.027376 | 0 | 0.027376 | 0.0013688 | 0 | 0.0013688 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Lodging | Commercial EM-New-Lodging-HtPmpHt | 7 | 12.3465 | 0 | 2.3976 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 13.2699 | 0.0024946 | 0.0024766 | 0 | 0 | 0 | 0.47812 | 1.1049 | 0 | 4.525 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47812 | 1.1049 | 0 | 4.525 | 6.108 | 6.9065 | 0.88145 | 0 | 0 | 7.7879 | 0.47812 | 16.2885 | 6.9065 | 1.0434 | 0 | 0 | 7.9498 | 1.1049 | 7.1953 | 6.9065 | 1.9248 | 0 | 0 | 8.8313 | 1.583 | -1.8955 | 5.5789 | 2.6512 | 6.1265 | 0 | 25.0912 | 33.8689 | 6.9065 | 0 | 1.9248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.108 |  | 0 | 0 | 8.8313 | 6.108 | 1.4459 | 23.1958 | 0.12607 | 0 | 0.12607 | 0.0063032 | 0 | 0.0063032 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Hospital | Commercial EM-New-Hospital-HtPmpHt | 7 | 224.6076 | 0 | 36.8751 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 241.4072 | 0.045381 | 0.045054 | 0 | 0 | 0 | 7.3534 | 16.9926 | 0 | 69.5937 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3534 | 16.9926 | 0 | 69.5937 | 93.9397 | 125.6424 | 16.0354 | 0 | 0 | 141.6778 | 7.3534 | 19.267 | 125.6424 | 18.9811 | 0 | 0 | 144.6236 | 16.9926 | 8.511 | 125.6424 | 35.0165 | 0 | 0 | 160.659 | 24.346 | -3.2524 | 6.599 | 2.2413 | 5.1794 | 0 | 21.2124 | 28.6331 | 125.6424 | 0 | 35.0165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.9397 |  | 0 | 0 | 160.659 | 93.9397 | 1.7102 | 17.96 | 2.2934 | 0 | 2.2934 | 0.11467 | 0 | 0.11467 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Residential Care | Commercial EM-New-Residential Care-HtPmpHt | 7 | 0.94779 | 0 | 0.18353 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.0187 | 0.0001915 | 0.00019012 | 0 | 0 | 0 | 0.036599 | 0.084575 | 0 | 0.34638 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036599 | 0.084575 | 0 | 0.34638 | 0.46755 | 0.53018 | 0.067666 | 0 | 0 | 0.59785 | 0.036599 | 16.3351 | 0.53018 | 0.080096 | 0 | 0 | 0.61028 | 0.084575 | 7.2158 | 0.53018 | 0.14776 | 0 | 0 | 0.67794 | 0.12117 | -1.9205 | 5.5948 | 2.6436 | 6.109 | 0 | 25.0198 | 33.7724 | 0.53018 | 0 | 0.14776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46755 |  | 0 | 0 | 0.67794 | 0.46755 | 1.45 | 23.0993 | 0.0096776 | 0 | 0.0096776 | 0.00048387 | 0 | 0.00048387 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Assembly | Commercial EM-New-Assembly-HtPmpHt | 7 | 1.2359 | 0 | 0.36522 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.3283 | 0.0002497 | 0.0002479 | 0 | 0 | 0 | 0.072829 | 0.1683 | 0 | 0.68927 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072829 | 0.1683 | 0 | 0.68927 | 0.93039 | 0.69132 | 0.088232 | 0 | 0 | 0.77955 | 0.072829 | 10.7039 | 0.69132 | 0.10444 | 0 | 0 | 0.79576 | 0.1683 | 4.7283 | 0.69132 | 0.19267 | 0 | 0 | 0.88399 | 0.24113 | 2.6842 | 3.6661 | 4.0344 | 9.3229 | 0 | 38.1823 | 51.5397 | 0.69132 | 0 | 0.19267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93039 |  | 0 | 0 | 0.88399 | 0.93039 | 0.95013 | 40.8665 | 0.012619 | 0 | 0.012619 | 0.00063094 | 0 | 0.00063094 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Other | Commercial EM-New-Other-HtPmpHt | 7 | 13.8485 | 0 | 4.0925 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 14.8843 | 0.002798 | 0.0027778 | 0 | 0 | 0 | 0.81609 | 1.8859 | 0 | 7.7236 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81609 | 1.8859 | 0 | 7.7236 | 10.4256 | 7.7466 | 0.98868 | 0 | 0 | 8.7353 | 0.81609 | 10.7039 | 7.7466 | 1.1703 | 0 | 0 | 8.917 | 1.8859 | 4.7283 | 7.7466 | 2.159 | 0 | 0 | 9.9056 | 2.7019 | 2.6842 | 3.6661 | 4.0344 | 9.3229 | 0 | 38.1823 | 51.5397 | 7.7466 | 0 | 2.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4256 |  | 0 | 0 | 9.9056 | 10.4256 | 0.95013 | 40.8665 | 0.1414 | 0 | 0.1414 | 0.00707 | 0 | 0.00707 | 0 | R-All-HVAC-CAC-All-All-E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Category Results; Sorted by TRC Levelized Cost
Total Results |  | Measure Input Data | [8 empty] | Savings | [5 empty] | PV Capital |  |  |  | PV Admin |  |  |  | PV O&M |  |  |  | PV Periodic Repl. |  |  |  | Total PV Capital, O&M and Periodic Repl Costs |  |  |  |  | PV Wholesale Electric Utility Costs & Benefits | [6 empty] | PV Retail Electric Utility Costs & Benefits | [6 empty] | PV Electric Utility System Costs & Benefits | [5 empty] | Electric Utility System Economics |  | Sponsor Levelized Cost (mills/kwh) |  |  |  |  | PV Regional Costs & Benefits | [15 empty] | TRC Economics |  | Physical CO2 | [5 empty] | Gas Inputs |  |  |  | PV Gas Utility System Costs & Benefits |  |  |  |  | Gas Utility System Economics
Category | Measure | Measure Life | Site Savings (kWh) | Site Savings (therms) | Capital Cost ($/unit) | Annual O&M Cost ($/unit) | PV Per. Repl. Cost ($/unit) | Load Shape (electric) | Diversified Load Factor (electric) | Wholesale Power Coincidence Factor (electric) | Wholesale Electric Energy (kWh) | Wholesale Electric Demand (kw) | Retail Electric Demand (kW) | Wholesale Gas Energy (therms/yr) | Wholesale Gas Demand (therms/day) | Retail Gas Demand (therms/day) | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Total | Wholesale Utility System Energy | Wholesale Utility System T&D Def. Cap. | Wholesale Utility System Act C-E Credit | Wholesale Utility System Risk Mitigation Benefit | Wholesale Utility System Total System Benefit | Wholesale Utility System Total Non-Consumer Cost | Wholesale Utility System B/C Ratio | Retail Utility System Energy | Retail Utility System T&D Def. Cap. | Retail Utility System Act C-E Credit | Retail Utility System Risk Mitigation Benefit | Retail Utility System Total System Benefit | Retail Utility System Total Non-Consumer Cost | Retail Utility System System B/C Ratio | Utility System Energy | Utility System T&D Def. Cap. | Utility System Act C-E Credit | Utility System Total Risk Mitigation Benefit | Utility System Total System Benefit | Utility System Total Non-Consumer Cost | Utility System Net Levelized Cost (Net of Elec T&D Capacity Benefits, Act Credit & Risk-Mitigation Benefit) in mills/kwh | Utility System System B/C Ratio | Wholesale Electric Levelized Cost | Retail Electric Levelized Cost | Natural Gas Levelized Cost | Customer Levelized Cost | Total Levelized Cost | PV Regional Electric Energy | PV Regional Gas Energy | PV Regional Electric T&D Def. Cap. | PV Regional Gas T&D Def. Cap. | PV Regional Electric System CO2 | PV Regional Gas System CO2 | PV Regional Electric System Risk-Mitigation Benefit | PV Regional Gas System Risk-Mitigation Benefit | PV Regional Non-E Value | PV Regional Act Credit | PV Regional Capital Cost | PV Regional Admin Cost | PV Regional Annual O&M Cost | PV Regional Periodic Replacement Cost | PV Total Regional Benefit | PV Total Regional Cost | TRC B/C Ratio | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | Electric System CO2 Avoided (Lifetime Tons) | Gas System CO2 Avoided (Lifetime Tons) | Total System CO2 Avoided (Lifetime Tons) | Electric System CO2 Avoided (Annual Tons in 2018) | Gas System CO2 Avoided (Annual Tons in 2018) | Total System CO2 Avoided (Annual Tons in 2018) | Gas Site Savings (therms) | Load Shape (gas) | Diversitfied Load Factor (gas) | Wholesale Coincidence Factor (gas) | Total Gas Utility System Energy | Gas Utility System T&D Def. Cap. | Gas Utility System Risk Mitigation Benefit | Gas Utility System Total System Benefit | Gas Utility System Total Non-Consumer Cost | Gas Utility System Net Levelized Cost (Net of Gas T&D Capacity Benefits & Risk-Mitigation Benefits) in cents/therm | Gas Utility System System B/C Ratio
Commercial EM-New-MiniMart |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Commercial EM-New-Hospital |  | 7 | 1449.4619 | 46.6074 | 237.9665 | 0 | 0 |  |  |  | 1557.8749 | 0.29286 | 0.29075 | 47.0735 | 0 | 0 | 47.4537 | 109.6583 | 0 | 449.1097 | 14.278 | 33.3153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.7317 | 142.9736 | 0 | 449.1097 | 653.8149 | 810.8092 | 103.4814 | 0 | 0 | 914.2905 | 61.7317 | 14.8107 | 810.8092 | 122.4911 | 0 | 0 | 933.3003 | 142.9736 | 6.5278 | 810.8092 | 225.9725 | 0 | 0 | 1036.7817 | 204.7052 | -1.0045 | 5.0648 | 2.9157 | 6.7529 | 0 | 21.2124 | 30.8811 | 810.8092 | 305.923 | 225.9725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606.2216 | 47.5933 | 0 | 0 | 1342.7047 | 653.8149 | 2.0536 | 5.7585 | 14.8 | 5.5076 | 20.3076 | 0.73999 | 0.27538 | 1.0154 | 47.0735 |  | 0 | 0 | 305.923 | 0 | 0 | 305.923 | 0 | 0 | 9999
Commercial EM-New-Residential Care |  | 7 | 109.7685 | 5.5313 | 21.2559 | 0 | 0 |  |  |  | 117.9787 | 0.022178 | 0.022018 | 5.5866 | 0 | 0 | 4.2387 | 9.795 | 0 | 40.1159 | 1.2754 | 2.9758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5141 | 12.7709 | 0 | 40.1159 | 58.4008 | 61.403 | 7.8367 | 0 | 0 | 69.2397 | 5.5141 | 12.5569 | 61.403 | 9.2763 | 0 | 0 | 70.6793 | 12.7709 | 5.5344 | 61.403 | 17.113 | 0 | 0 | 78.516 | 18.2849 | 0.7309 | 4.294 | 3.4391 | 7.965 | 0 | 25.0198 | 36.4238 | 61.403 | 36.3066 | 17.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.1496 | 4.2512 | 0 | 0 | 114.8226 | 58.4008 | 1.9661 | 3.1067 | 1.1208 | 0.65364 | 1.7744 | 0.05604 | 0.032682 | 0.088722 | 5.5866 |  | 0 | 0 | 36.3066 | 0 | 0 | 36.3066 | 0 | 0 | 9999
Commercial EM-New-Supermarket |  | 7 | 100.2458 | 4.6522 | 23.9073 | 0 | 0 |  |  |  | 107.7437 | 0.020254 | 0.020108 | 4.6987 | 0 | 0 | 4.7674 | 11.0168 | 0 | 45.1198 | 1.4344 | 3.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2019 | 14.3638 | 0 | 45.1198 | 65.6855 | 56.0761 | 7.1568 | 0 | 0 | 63.233 | 6.2019 | 10.1958 | 56.0761 | 8.4716 | 0 | 0 | 64.5477 | 14.3638 | 4.4938 | 56.0761 | 15.6284 | 0 | 0 | 71.7046 | 20.5657 | 3.3718 | 3.4866 | 4.2355 | 9.8095 | 0 | 30.8138 | 44.8588 | 56.0761 | 30.536 | 15.6284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.9041 | 4.7815 | 0 | 0 | 102.2405 | 65.6855 | 1.5565 | 13.3316 | 1.0236 | 0.54975 | 1.5733 | 0.051178 | 0.027487 | 0.078666 | 4.6987 |  | 0 | 0 | 30.536 | 0 | 0 | 30.536 | 0 | 0 | 9999
Commercial EM-New-Lodging |  | 7 | 97.6789 | 1.879 | 19.913 | 0 | 0 |  |  |  | 104.9849 | 0.019736 | 0.019593 | 1.8978 | 0 | 0 | 3.9709 | 9.1762 | 0 | 37.5815 | 1.1948 | 2.7878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1657 | 11.964 | 0 | 37.5815 | 54.7112 | 54.6403 | 6.9736 | 0 | 0 | 61.6138 | 5.1657 | 11.9275 | 54.6403 | 8.2547 | 0 | 0 | 62.8949 | 11.964 | 5.257 | 54.6403 | 15.2282 | 0 | 0 | 69.8685 | 17.1297 | 1.3327 | 4.0788 | 3.6205 | 8.3853 | 0 | 26.3401 | 38.346 | 54.6403 | 12.3335 | 15.2282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.7286 | 3.9826 | 0 | 0 | 82.202 | 54.7112 | 1.5025 | 19.0285 | 0.99737 | 0.22204 | 1.2194 | 0.049868 | 0.011102 | 0.06097 | 1.8978 |  | 0 | 0 | 12.3335 | 0 | 0 | 12.3335 | 0 | 0 | 9999
Commercial EM-New-Small Ret |  | 7 | 125.5044 | 1.9385 | 25.4638 | 0 | 0 |  |  |  | 134.8916 | 0.025358 | 0.025175 | 1.9578 | 0 | 0 | 5.0778 | 11.7341 | 0 | 48.0574 | 1.5278 | 3.5649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6057 | 15.299 | 0 | 48.0574 | 69.9621 | 70.2055 | 8.9601 | 0 | 0 | 79.1656 | 6.6057 | 11.9845 | 70.2055 | 10.6061 | 0 | 0 | 80.8116 | 15.299 | 5.2821 | 70.2055 | 19.5663 | 0 | 0 | 89.7717 | 21.9047 | 1.2756 | 4.0983 | 3.6033 | 8.3454 | 0 | 26.2147 | 38.1635 | 70.2055 | 12.7237 | 19.5663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.8693 | 5.0928 | 0 | 0 | 102.4954 | 69.9621 | 1.465 | 20.5497 | 1.2815 | 0.22907 | 1.5105 | 0.064074 | 0.011453 | 0.075527 | 1.9578 |  | 0 | 0 | 12.7237 | 0 | 0 | 12.7237 | 0 | 0 | 9999
Commercial EM-New-Other |  | 7 | 170.2852 | 12.0154 | 50.3221 | 0 | 0 |  |  |  | 183.0218 | 0.034406 | 0.034157 | 12.1356 | 0 | 0 | 10.0349 | 23.1891 | 0 | 94.9719 | 3.0193 | 7.0451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.0542 | 30.2342 | 0 | 94.9719 | 138.2603 | 95.2552 | 12.1572 | 0 | 0 | 107.4124 | 13.0542 | 8.2282 | 95.2552 | 14.3905 | 0 | 0 | 109.6457 | 30.2342 | 3.6265 | 95.2552 | 26.5476 | 0 | 0 | 121.8029 | 43.2884 | 6.7304 | 2.8138 | 5.2483 | 12.1553 | 0 | 38.1823 | 55.5859 | 95.2552 | 78.8671 | 26.5476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128.1959 | 10.0644 | 0 | 0 | 200.6699 | 138.2603 | 1.4514 | 13.2052 | 1.7387 | 1.4199 | 3.1586 | 0.086935 | 0.070993 | 0.15793 | 12.1356 |  | 0 | 0 | 78.8671 | 0 | 0 | 78.8671 | 0 | 0 | 9999
Commercial EM-New-Assembly |  | 7 | 143.1306 | 9.7839 | 42.2974 | 0 | 0 |  |  |  | 153.8362 | 0.028919 | 0.02871 | 9.8817 | 0 | 0 | 8.4347 | 19.4913 | 0 | 79.8272 | 2.5378 | 5.9216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.9725 | 25.4129 | 0 | 79.8272 | 116.2126 | 80.0653 | 10.2185 | 0 | 0 | 90.2838 | 10.9725 | 8.2282 | 80.0653 | 12.0957 | 0 | 0 | 92.161 | 25.4129 | 3.6265 | 80.0653 | 22.3142 | 0 | 0 | 102.3795 | 36.3854 | 6.7304 | 2.8138 | 5.2483 | 12.1553 | 0 | 38.1823 | 55.5859 | 80.0653 | 64.2195 | 22.3142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.7531 | 8.4595 | 0 | 0 | 166.5991 | 116.2126 | 1.4336 | 14.1958 | 1.4615 | 1.1562 | 2.6176 | 0.073072 | 0.057808 | 0.13088 | 9.8817 |  | 0 | 0 | 64.2195 | 0 | 0 | 64.2195 | 0 | 0 | 9999
Commercial EM-New-Large Off |  | 7 | 854.5929 | 27.3249 | 213.3173 | 0 | 0 |  |  |  | 918.5124 | 0.17267 | 0.17142 | 27.5981 | 0 | 0 | 42.5383 | 98.2996 | 0 | 402.5898 | 12.799 | 29.8644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.3374 | 128.164 | 0 | 402.5898 | 586.0912 | 478.0476 | 61.0119 | 0 | 0 | 539.0595 | 55.3374 | 9.7413 | 478.0476 | 72.2199 | 0 | 0 | 550.2675 | 128.164 | 4.2935 | 478.0476 | 133.2318 | 0 | 0 | 611.2794 | 183.5014 | 4.0271 | 3.3312 | 4.4331 | 10.2672 | 0 | 32.2513 | 46.9516 | 478.0476 | 179.3558 | 133.2318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 543.4277 | 42.6635 | 0 | 0 | 790.6352 | 586.0912 | 1.349 | 21.9103 | 8.726 | 3.229 | 11.9549 | 0.43629 | 0.16145 | 0.59774 | 27.5981 |  | 0 | 0 | 179.3558 | 0 | 0 | 179.3558 | 0 | 0 | 9999
Commercial EM-New-Medium Off |  | 7 | 270.0923 | 12.9537 | 87.8365 | 0 | 0 |  |  |  | 290.2939 | 0.054571 | 0.054177 | 13.0833 | 0 | 0 | 17.5158 | 40.4763 | 0 | 165.7723 | 5.2702 | 12.2971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.786 | 52.7734 | 0 | 165.7723 | 241.3317 | 151.0859 | 19.2827 | 0 | 0 | 170.3686 | 22.786 | 7.4769 | 151.0859 | 22.825 | 0 | 0 | 173.9109 | 52.7734 | 3.2954 | 151.0859 | 42.1076 | 0 | 0 | 193.1936 | 75.5594 | 8.4791 | 2.5568 | 5.7756 | 13.3766 | 0 | 42.0188 | 61.1711 | 151.0859 | 85.026 | 42.1076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223.7643 | 17.5673 | 0 | 0 | 278.2196 | 241.3317 | 1.1529 | 28.9461 | 2.7578 | 1.5307 | 4.2886 | 0.13789 | 0.076537 | 0.21443 | 13.0833 |  | 0 | 0 | 85.026 | 0 | 0 | 85.026 | 0 | 0 | 9999
Commercial EM-New-Restaurant |  | 7 | 43.8668 | 1.5303 | 13.1202 | 0 | 0 |  |  |  | 47.1478 | 0.0088631 | 0.0087992 | 1.5456 | 0 | 0 | 2.6163 | 6.046 | 0 | 24.7615 | 0.78721 | 1.8368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4036 | 7.8828 | 0 | 24.7615 | 36.0479 | 24.5385 | 3.1318 | 0 | 0 | 27.6702 | 3.4036 | 8.1298 | 24.5385 | 3.7071 | 0 | 0 | 28.2456 | 7.8828 | 3.5832 | 24.5385 | 6.8389 | 0 | 0 | 31.3773 | 11.2864 | 6.941 | 2.7801 | 5.3118 | 12.3024 | 0 | 38.6444 | 56.2586 | 24.5385 | 10.0447 | 6.8389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.4239 | 2.624 | 0 | 0 | 41.422 | 36.0479 | 1.1491 | 29.9091 | 0.44791 | 0.18084 | 0.62874 | 0.022395 | 0.0090418 | 0.031437 | 1.5456 |  | 0 | 0 | 10.0447 | 0 | 0 | 10.0447 | 0 | 0 | 9999
Commercial EM-New-University |  | 7 | 732.11 | 24.2472 | 216.8218 | 0 | 0 |  |  |  | 786.8684 | 0.14792 | 0.14685 | 24.4897 | 0 | 0 | 43.2372 | 99.9145 | 0 | 409.2038 | 13.0093 | 30.3551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.2465 | 130.2696 | 0 | 409.2038 | 595.7198 | 409.5323 | 52.2675 | 0 | 0 | 461.7998 | 56.2465 | 8.2103 | 409.5323 | 61.8692 | 0 | 0 | 471.4015 | 130.2696 | 3.6187 | 409.5323 | 114.1367 | 0 | 0 | 523.669 | 186.516 | 6.7684 | 2.8076 | 5.2597 | 12.1818 | 0 | 38.2655 | 55.707 | 409.5323 | 159.1543 | 114.1367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 552.3554 | 43.3644 | 0 | 0 | 682.8233 | 595.7198 | 1.1462 | 30.151 | 7.4753 | 2.8653 | 10.3406 | 0.37376 | 0.14326 | 0.51703 | 24.4897 |  | 0 | 0 | 159.1543 | 0 | 0 | 159.1543 | 0 | 0 | 9999
Commercial EM-New-Xlarge Ret |  | 7 | 30.2229 | 0.50772 | 9.8288 | 0 | 0 |  |  |  | 32.4834 | 0.0061064 | 0.0060624 | 0.5128 | 0 | 0 | 1.96 | 4.5292 | 0 | 18.5496 | 0.58973 | 1.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5497 | 5.9053 | 0 | 18.5496 | 27.0046 | 16.9063 | 2.1577 | 0 | 0 | 19.064 | 2.5497 | 7.4769 | 16.9063 | 2.5541 | 0 | 0 | 19.4603 | 5.9053 | 3.2954 | 16.9063 | 4.7118 | 0 | 0 | 21.618 | 8.455 | 8.4791 | 2.5568 | 5.7756 | 13.3766 | 0 | 42.0188 | 61.1711 | 16.9063 | 3.3326 | 4.7118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.0388 | 1.9658 | 0 | 0 | 24.9506 | 27.0046 | 0.92394 | 42.9489 | 0.3086 | 0.059998 | 0.36859 | 0.01543 | 0.0029999 | 0.01843 | 0.5128 |  | 0 | 0 | 3.3326 | 0 | 0 | 3.3326 | 0 | 0 | 9999
Commercial EM-New-School K-12 |  | 7 | 168.9185 | 6.6902 | 82.3023 | 0 | 0 |  |  |  | 181.5528 | 0.034129 | 0.033883 | 6.7571 | 0 | 0 | 16.4122 | 37.9261 | 0 | 155.3277 | 4.9381 | 11.5223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.3503 | 49.4484 | 0 | 155.3277 | 226.1264 | 94.4907 | 12.0596 | 0 | 0 | 106.5503 | 21.3503 | 4.9906 | 94.4907 | 14.275 | 0 | 0 | 108.7656 | 49.4484 | 2.1996 | 94.4907 | 26.3346 | 0 | 0 | 120.8252 | 70.7987 | 18.0209 | 1.7066 | 8.6531 | 20.041 | 0 | 62.953 | 91.6471 | 94.4907 | 43.913 | 26.3346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.666 | 16.4605 | 0 | 0 | 164.7382 | 226.1264 | 0.72852 | 63.1763 | 1.7248 | 0.79058 | 2.5153 | 0.086238 | 0.039529 | 0.12577 | 6.7571 |  | 0 | 0 | 43.913 | 0 | 0 | 43.913 | 0 | 0 | 9999
Commercial EM-New-Warehouse |  | 7 | 26.5685 | 0.99425 | 14.5926 | 0 | 0 |  |  |  | 28.5557 | 0.0053681 | 0.0053293 | 1.0042 | 0 | 0 | 2.91 | 6.7245 | 0 | 27.5403 | 0.87555 | 2.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7855 | 8.7674 | 0 | 27.5403 | 40.0932 | 14.8621 | 1.8968 | 0 | 0 | 16.7589 | 3.7855 | 4.4271 | 14.8621 | 2.2453 | 0 | 0 | 17.1073 | 8.7674 | 1.9512 | 14.8621 | 4.1421 | 0 | 0 | 19.0041 | 12.5529 | 21.6729 | 1.5139 | 9.7544 | 22.5917 | 0 | 70.9651 | 103.3112 | 14.8621 | 6.5261 | 4.1421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1747 | 2.9185 | 0 | 0 | 25.5302 | 40.0932 | 0.63677 | 75.8218 | 0.27128 | 0.11749 | 0.38877 | 0.013564 | 0.0058745 | 0.019438 | 1.0042 |  | 0 | 0 | 6.5261 | 0 | 0 | 6.5261 | 0 | 0 | 9999
Commercial EM-New-Medium Ret |  | 7 | 32.5805 | 0.49944 | 15.3782 | 0 | 0 |  |  |  | 35.0174 | 0.0065828 | 0.0065353 | 0.50443 | 0 | 0 | 3.0666 | 7.0865 | 0 | 29.023 | 0.92269 | 2.1529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9893 | 9.2394 | 0 | 29.023 | 42.2517 | 18.2251 | 2.326 | 0 | 0 | 20.5511 | 3.9893 | 5.1516 | 18.2251 | 2.7533 | 0 | 0 | 20.9784 | 9.2394 | 2.2705 | 18.2251 | 5.0793 | 0 | 0 | 23.3044 | 13.2287 | 17.1242 | 1.7617 | 8.3827 | 19.4147 | 0 | 60.9857 | 88.7831 | 18.2251 | 3.2782 | 5.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.1761 | 3.0756 | 0 | 0 | 26.5827 | 42.2517 | 0.62915 | 71.2214 | 0.33267 | 0.059018 | 0.39169 | 0.016633 | 0.0029509 | 0.019584 | 0.50443 |  | 0 | 0 | 3.2782 | 0 | 0 | 3.2782 | 0 | 0 | 9999
Commercial EM-New-Large Ret |  | 7 | 218.9034 | 2.3089 | 143.7545 | 0 | 0 |  |  |  | 235.2764 | 0.044229 | 0.04391 | 2.332 | 0 | 0 | 28.6666 | 66.2441 | 0 | 271.3052 | 8.6253 | 20.1256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.2918 | 86.3697 | 0 | 271.3052 | 394.9668 | 122.4516 | 15.6282 | 0 | 0 | 138.0798 | 37.2918 | 3.7027 | 122.4516 | 18.4991 | 0 | 0 | 140.9507 | 86.3697 | 1.6319 | 122.4516 | 34.1273 | 0 | 0 | 156.5788 | 123.6616 | 28.0015 | 1.2662 | 11.6629 | 27.0118 | 0 | 84.8496 | 123.5243 | 122.4516 | 15.1553 | 34.1273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366.2159 | 28.7509 | 0 | 0 | 171.7342 | 394.9668 | 0.43481 | 108.1114 | 2.2351 | 0.27284 | 2.508 | 0.11176 | 0.013642 | 0.1254 | 2.332 |  | 0 | 0 | 15.1553 | 0 | 0 | 15.1553 | 0 | 0 | 9999
Commercial EM-New-Small Off |  | 7 | 18.1 | 0.75959 | 16.1766 | 0 | 0 |  |  |  | 19.4538 | 0.003657 | 0.0036307 | 0.76718 | 0 | 0 | 3.2258 | 7.4544 | 0 | 30.5299 | 0.9706 | 2.2647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1964 | 9.7192 | 0 | 30.5299 | 44.4455 | 10.1249 | 1.2922 | 0 | 0 | 11.4171 | 4.1964 | 2.7207 | 10.1249 | 1.5296 | 0 | 0 | 11.6545 | 9.7192 | 1.1991 | 10.1249 | 2.8218 | 0 | 0 | 12.9467 | 13.9156 | 41.961 | 0.93037 | 15.8726 | 36.7616 | 0 | 115.4758 | 168.11 | 10.1249 | 4.9858 | 2.8218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.2101 | 3.2353 | 0 | 0 | 17.9325 | 44.4455 | 0.40347 | 138.5786 | 0.18481 | 0.089761 | 0.27457 | 0.0092405 | 0.004488 | 0.013729 | 0.76718 |  | 0 | 0 | 4.9858 | 0 | 0 | 4.9858 | 0 | 0 | 9999
Supply Curve Results; Categories sorted by TRC Net Levelized Cost
Totals for Categories with Benefits Exceeding Costs. Levelized cost is TRC Net Levelized Cost (Net of Benefits) | [12 empty] | Savings Allocation by Cost Bin and Month for Segments 1 | [12 empty] | Savings Allocation by Cost Bin and Month for Segments 2
| Totals Basis | Busbar Electric Savings in kWh | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Measures with B/C > 1.00 | 4122.9893 | 876.8116 | 0 | 876.8116 | 2233.6852 | 3728.2404 | 1862.9371 | -0.3418 | 11.6234 | 1.7609 | 56.8902 | 258.5326 | 232.4627 | 267.5049 | 248.8654 | 254.0768 | 251.5016 | 238.9309 | 248.9569 | 232.6053 | 265.2143 | 234.7002 | 255.5272 |  | 109.7625 | 94.3047 | 90.4581 | 94.4533 | 92.6714 | 81.3166 | 95.476 | 78.3 | 96.3958 | 86.5784 | 103.8763 | 110.5176
| Categories with B/C > 1.00 | 4403.1542 | 952.2219 | 190.4444 | 1142.6663 | 2616.238 | 3904.8343 | 2273.315 | 3.0154 | 16.7623 | 1.583 | 59.3743 | 29.6793 | 26.6865 | 30.7093 | 28.5695 | 29.1678 | 28.8722 | 27.4291 | 28.58 | 26.7029 | 30.4464 | 26.9434 | 29.3343 |  | 12.6006 | 10.8261 | 10.3845 | 10.8432 | 10.6386 | 9.3351 | 10.9606 | 8.9888 | 11.0662 | 9.9391 | 11.9249 | 12.6873
Supply Curve Results: By TRC Net Levelized Cost - Net of Benefits
| Block 1: <= 0 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 2: <= 10 mills/kWh | 1675.8535 | 259.2224 | 51.8445 | 311.0669 | 712.2158 | 1457.5272 | 1626.0047 | -0.88233 | 5.5718 | 2.0475 | 22.082 | 105.0846 | 94.4881 | 108.7315 | 101.1552 | 103.2735 | 102.2268 | 97.1172 | 101.1924 | 94.5461 | 107.8005 | 95.3976 | 103.863 |  | 44.6147 | 38.3316 | 36.7681 | 38.392 | 37.6677 | 33.0524 | 38.8077 | 31.8262 | 39.1816 | 35.1912 | 42.2222 | 44.9216
| Block 3: 10-20 mills/kWh | 549.5865 | 136.4398 | 27.288 | 163.7278 | 374.8696 | 551.7116 | 2609.6994 | 5.0409 | 14.6196 | 1.4768 | 8.5689 | 34.4619 | 30.9868 | 35.6579 | 33.1733 | 33.8679 | 33.5247 | 31.849 | 33.1855 | 31.0058 | 35.3525 | 31.2851 | 34.0613 |  | 14.6311 | 12.5706 | 12.0579 | 12.5904 | 12.3529 | 10.8393 | 12.7268 | 10.4372 | 12.8494 | 11.5407 | 13.8465 | 14.7318
| Block 4: 20-30 mills/kWh | 1390.8457 | 339.7379 | 67.9476 | 407.6855 | 933.4328 | 1212.7722 | 2567.736 | 4.7882 | 23.518 | 1.3125 | 18.3828 | 87.2132 | 78.4188 | 90.2399 | 83.952 | 85.7101 | 84.8414 | 80.6007 | 83.9829 | 78.4669 | 89.4672 | 79.1736 | 86.1993 |  | 37.0272 | 31.8127 | 30.5151 | 31.8628 | 31.2617 | 27.4313 | 32.2078 | 26.4136 | 32.5181 | 29.2063 | 35.0415 | 37.2819
| Block 5: 30-40 mills/kWh | 786.8684 | 216.8218 | 43.3644 | 260.1862 | 595.7198 | 682.8233 | 2896.5844 | 6.7684 | 30.151 | 1.1462 | 10.3406 | 49.3407 | 44.3653 | 51.053 | 47.4957 | 48.4903 | 47.9988 | 45.5997 | 47.5132 | 44.3925 | 50.6159 | 44.7923 | 48.7671 |  | 20.9481 | 17.998 | 17.2638 | 18.0263 | 17.6862 | 15.5192 | 18.2215 | 14.9435 | 18.397 | 16.5234 | 19.8247 | 21.0922
| Block 6: 40-50 mills/kWh | 32.4834 | 9.8288 | 1.9658 | 11.7945 | 27.0046 | 24.9506 | 3180.6991 | 8.4791 | 42.9489 | 0.92394 | 0.36859 | 2.0369 | 1.8315 | 2.1076 | 1.9607 | 2.0018 | 1.9815 | 1.8824 | 1.9614 | 1.8326 | 2.0895 | 1.8491 | 2.0132 |  | 0.86478 | 0.74299 | 0.71268 | 0.74416 | 0.73012 | 0.64066 | 0.75222 | 0.61689 | 0.75946 | 0.68212 | 0.8184 | 0.87072
| Block 7: 50-60 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 8: 60-70 mills/kWh | 181.5528 | 82.3023 | 16.4605 | 98.7628 | 226.1264 | 164.7382 | 4765.3485 | 18.0209 | 63.1763 | 0.72852 | 2.5153 | 11.3843 | 10.2363 | 11.7794 | 10.9586 | 11.1881 | 11.0747 | 10.5211 | 10.9626 | 10.2426 | 11.6785 | 10.3348 | 11.2519 |  | 4.8333 | 4.1526 | 3.9833 | 4.1592 | 4.0807 | 3.5807 | 4.2042 | 3.4479 | 4.2447 | 3.8124 | 4.5741 | 4.8666
| Block 9: 70-80 mills/kWh | 63.5731 | 29.9707 | 5.9941 | 35.9649 | 82.3449 | 52.1128 | 4955.7485 | 19.1674 | 73.2878 | 0.63257 | 0.78046 | 3.9864 | 3.5844 | 4.1247 | 3.8373 | 3.9177 | 3.8779 | 3.6841 | 3.8387 | 3.5866 | 4.0894 | 3.6189 | 3.94 |  | 1.6924 | 1.4541 | 1.3948 | 1.4564 | 1.4289 | 1.2538 | 1.4722 | 1.2073 | 1.4863 | 1.335 | 1.6017 | 1.7041
| Block 10: 80-90 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 11: 90-100 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 12: 100-110 mills/kWh | 235.2764 | 143.7545 | 28.7509 | 172.5054 | 394.9668 | 171.7342 | 6422.861 | 28.0015 | 108.1114 | 0.43481 | 2.508 | 14.753 | 13.2654 | 15.265 | 14.2014 | 14.4988 | 14.3518 | 13.6345 | 14.2066 | 13.2735 | 15.1343 | 13.3931 | 14.5815 |  | 6.2635 | 5.3815 | 5.1619 | 5.3899 | 5.2882 | 4.6403 | 5.4483 | 4.4681 | 5.5008 | 4.9406 | 5.9277 | 6.3066
| Block 13: 110-120 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 14: 120-130 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 15: 130-140 mills/kWh | 19.4538 | 16.1766 | 3.2353 | 19.412 | 44.4455 | 17.9325 | 8741.1718 | 41.961 | 138.5786 | 0.40347 | 0.27457 | 1.2199 | 1.0968 | 1.2622 | 1.1742 | 1.1988 | 1.1867 | 1.1274 | 1.1747 | 1.0975 | 1.2514 | 1.1074 | 1.2057 |  | 0.5179 | 0.44496 | 0.42681 | 0.44567 | 0.43726 | 0.38368 | 0.45049 | 0.36945 | 0.45483 | 0.40851 | 0.49013 | 0.52146
| Block 16: 140-150 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 17: 150-160 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 18: 160-170 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 19: 170-180 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 20: 180-190 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 21: 190-200 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 22: > 200 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Shaped Savings Results; By Category and sorted by TRC BC ratio
[13 empty] | Savings Allocation by Cost Bin and Month for Segments 1 Feb: Savings Allocation by Category and Month for Segments 1 |  |  | Savings Allocation by Category and Month for Segments 2
Category | Measure | Busbar Savings | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Wholesale KW | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Commercial EM-New-MiniMart |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commercial EM-New-Hospital |  | 1557.8749 | 237.9665 | 47.5933 | 285.5598 | 653.8149 | 1342.7047 | 1605.7152 | -1.0045 | 5.7585 | 2.0536 | 20.3076 | 0.29286 | 97.6868 | 87.8362 | 101.0769 | 94.034 | 96.0031 | 95.0301 | 90.2802 | 94.0686 | 87.8901 | 100.2114 | 88.6817 | 96.5511 |  | 41.4739 | 35.6331 | 34.1797 | 35.6893 | 35.016 | 30.7255 | 36.0757 | 29.5857 | 36.4232 | 32.7137 | 39.2498 | 41.7592
Commercial EM-New-Residential Care |  | 117.9787 | 21.2559 | 4.2512 | 25.5071 | 58.4008 | 114.8226 | 1893.9206 | 0.7309 | 3.1067 | 1.9661 | 1.7744 | 0.022178 | 7.3979 | 6.6519 | 7.6546 | 7.1212 | 7.2704 | 7.1967 | 6.837 | 7.1239 | 6.656 | 7.5891 | 6.7159 | 7.3119 |  | 3.1408 | 2.6985 | 2.5884 | 2.7028 | 2.6518 | 2.3269 | 2.732 | 2.2405 | 2.7583 | 2.4774 | 2.9724 | 3.1624
Commercial EM-New-Supermarket |  | 107.7437 | 23.9073 | 4.7815 | 28.6888 | 65.6855 | 102.2405 | 2332.5127 | 3.3718 | 13.3316 | 1.5565 | 1.5733 | 0.020254 | 6.7561 | 6.0748 | 6.9906 | 6.5035 | 6.6396 | 6.5723 | 6.2438 | 6.5058 | 6.0785 | 6.9307 | 6.1333 | 6.6775 |  | 2.8684 | 2.4644 | 2.3639 | 2.4683 | 2.4217 | 2.125 | 2.495 | 2.0462 | 2.5191 | 2.2625 | 2.7145 | 2.8881
Commercial EM-New-Lodging |  | 104.9849 | 19.913 | 3.9826 | 23.8956 | 54.7112 | 82.202 | 1993.8663 | 1.3327 | 19.0285 | 1.5025 | 1.2194 | 0.019736 | 6.5831 | 5.9193 | 6.8116 | 6.3369 | 6.4696 | 6.4041 | 6.084 | 6.3393 | 5.9229 | 6.7532 | 5.9762 | 6.5066 |  | 2.7949 | 2.4013 | 2.3034 | 2.4051 | 2.3597 | 2.0706 | 2.4311 | 1.9938 | 2.4546 | 2.2046 | 2.645 | 2.8141
Commercial EM-New-Small Ret |  | 134.8916 | 25.4638 | 5.0928 | 30.5566 | 69.9621 | 102.4954 | 1984.3765 | 1.2756 | 20.5497 | 1.465 | 1.5105 | 0.025358 | 8.4584 | 7.6055 | 8.7519 | 8.1421 | 8.3126 | 8.2284 | 7.8171 | 8.1451 | 7.6101 | 8.677 | 7.6787 | 8.3601 |  | 3.5911 | 3.0854 | 2.9595 | 3.0902 | 3.0319 | 2.6604 | 3.1237 | 2.5617 | 3.1538 | 2.8326 | 3.3985 | 3.6158
Commercial EM-New-Other |  | 183.0218 | 50.3221 | 10.0644 | 60.3865 | 138.2603 | 200.6699 | 2890.2874 | 6.7304 | 13.2052 | 1.4514 | 3.1586 | 0.034406 | 11.4764 | 10.3191 | 11.8747 | 11.0473 | 11.2786 | 11.1643 | 10.6063 | 11.0513 | 10.3255 | 11.773 | 10.4185 | 11.343 |  | 4.8724 | 4.1862 | 4.0155 | 4.1928 | 4.1137 | 3.6097 | 4.2382 | 3.4758 | 4.2791 | 3.8433 | 4.6111 | 4.9059
Commercial EM-New-Assembly |  | 153.8362 | 42.2974 | 8.4595 | 50.7569 | 116.2126 | 166.5991 | 2890.2874 | 6.7304 | 14.1958 | 1.4336 | 2.6176 | 0.028919 | 9.6463 | 8.6736 | 9.9811 | 9.2856 | 9.4801 | 9.384 | 8.9149 | 9.289 | 8.6789 | 9.8956 | 8.7571 | 9.5342 |  | 4.0954 | 3.5187 | 3.3752 | 3.5242 | 3.4577 | 3.0341 | 3.5624 | 2.9215 | 3.5967 | 3.2304 | 3.8758 | 4.1236
Commercial EM-New-Large Off |  | 918.5124 | 213.3173 | 42.6635 | 255.9808 | 586.0912 | 790.6352 | 2441.3296 | 4.0271 | 21.9103 | 1.349 | 11.9549 | 0.17267 | 57.5954 | 51.7876 | 59.5943 | 55.4418 | 56.6028 | 56.0291 | 53.2286 | 55.4622 | 51.8194 | 59.084 | 52.2861 | 56.9259 |  | 24.4527 | 21.009 | 20.1521 | 21.0421 | 20.6452 | 18.1156 | 21.27 | 17.4435 | 21.4749 | 19.2878 | 23.1414 | 24.6209
Commercial EM-New-Medium Off |  | 290.2939 | 87.8365 | 17.5673 | 105.4038 | 241.3317 | 278.2196 | 3180.6991 | 8.4791 | 28.9461 | 1.1529 | 4.2886 | 0.054571 | 18.2029 | 16.3674 | 18.8346 | 17.5223 | 17.8892 | 17.7079 | 16.8228 | 17.5287 | 16.3774 | 18.6734 | 16.5249 | 17.9913 |  | 7.7282 | 6.6399 | 6.369 | 6.6503 | 6.5249 | 5.7254 | 6.7223 | 5.513 | 6.7871 | 6.0959 | 7.3138 | 7.7814
Commercial EM-New-Restaurant |  | 47.1478 | 13.1202 | 2.624 | 15.7443 | 36.0479 | 41.422 | 2925.2634 | 6.941 | 29.9091 | 1.1491 | 0.62874 | 0.0088631 | 2.9564 | 2.6583 | 3.059 | 2.8459 | 2.9055 | 2.876 | 2.7323 | 2.8469 | 2.6599 | 3.0328 | 2.6839 | 2.922 |  | 1.2552 | 1.0784 | 1.0344 | 1.0801 | 1.0597 | 0.92988 | 1.0918 | 0.89539 | 1.1023 | 0.99005 | 1.1879 | 1.2638
Commercial EM-New-University |  | 786.8684 | 216.8218 | 43.3644 | 260.1862 | 595.7198 | 682.8233 | 2896.5844 | 6.7684 | 30.151 | 1.1462 | 10.3406 | 0.14792 | 49.3407 | 44.3653 | 51.053 | 47.4957 | 48.4903 | 47.9988 | 45.5997 | 47.5132 | 44.3925 | 50.6159 | 44.7923 | 48.7671 |  | 20.9481 | 17.998 | 17.2638 | 18.0263 | 17.6862 | 15.5192 | 18.2215 | 14.9435 | 18.397 | 16.5234 | 19.8247 | 21.0922
Commercial EM-New-Xlarge Ret |  | 32.4834 | 9.8288 | 1.9658 | 11.7945 | 27.0046 | 24.9506 | 3180.6991 | 8.4791 | 42.9489 | 0.92394 | 0.36859 | 0.0061064 | 2.0369 | 1.8315 | 2.1076 | 1.9607 | 2.0018 | 1.9815 | 1.8824 | 1.9614 | 1.8326 | 2.0895 | 1.8491 | 2.0132 |  | 0.86478 | 0.74299 | 0.71268 | 0.74416 | 0.73012 | 0.64066 | 0.75222 | 0.61689 | 0.75946 | 0.68212 | 0.8184 | 0.87072
Commercial EM-New-School K-12 |  | 181.5528 | 82.3023 | 16.4605 | 98.7628 | 226.1264 | 164.7382 | 4765.3485 | 18.0209 | 63.1763 | 0.72852 | 2.5153 | 0.034129 | 11.3843 | 10.2363 | 11.7794 | 10.9586 | 11.1881 | 11.0747 | 10.5211 | 10.9626 | 10.2426 | 11.6785 | 10.3348 | 11.2519 |  | 4.8333 | 4.1526 | 3.9833 | 4.1592 | 4.0807 | 3.5807 | 4.2042 | 3.4479 | 4.2447 | 3.8124 | 4.5741 | 4.8666
Commercial EM-New-Warehouse |  | 28.5557 | 14.5926 | 2.9185 | 17.5111 | 40.0932 | 25.5302 | 5371.8474 | 21.6729 | 75.8218 | 0.63677 | 0.38877 | 0.0053681 | 1.7906 | 1.61 | 1.8527 | 1.7236 | 1.7597 | 1.7419 | 1.6548 | 1.7243 | 1.611 | 1.8369 | 1.6255 | 1.7698 |  | 0.76021 | 0.65315 | 0.62651 | 0.65418 | 0.64184 | 0.5632 | 0.66126 | 0.5423 | 0.66763 | 0.59964 | 0.71944 | 0.76544
Commercial EM-New-Medium Ret |  | 35.0174 | 15.3782 | 3.0756 | 18.4538 | 42.2517 | 26.5827 | 4616.4313 | 17.1242 | 71.2214 | 0.62915 | 0.39169 | 0.0065828 | 2.1958 | 1.9744 | 2.272 | 2.1137 | 2.1579 | 2.1361 | 2.0293 | 2.1144 | 1.9756 | 2.2525 | 1.9934 | 2.1702 |  | 0.93224 | 0.80095 | 0.76828 | 0.80221 | 0.78708 | 0.69064 | 0.8109 | 0.66502 | 0.81871 | 0.73533 | 0.88224 | 0.93865
Commercial EM-New-Large Ret |  | 235.2764 | 143.7545 | 28.7509 | 172.5054 | 394.9668 | 171.7342 | 6422.861 | 28.0015 | 108.1114 | 0.43481 | 2.508 | 0.044229 | 14.753 | 13.2654 | 15.265 | 14.2014 | 14.4988 | 14.3518 | 13.6345 | 14.2066 | 13.2735 | 15.1343 | 13.3931 | 14.5815 |  | 6.2635 | 5.3815 | 5.1619 | 5.3899 | 5.2882 | 4.6403 | 5.4483 | 4.4681 | 5.5008 | 4.9406 | 5.9277 | 6.3066
Commercial EM-New-Small Off |  | 19.4538 | 16.1766 | 3.2353 | 19.412 | 44.4455 | 17.9325 | 8741.1718 | 41.961 | 138.5786 | 0.40347 | 0.27457 | 0.003657 | 1.2199 | 1.0968 | 1.2622 | 1.1742 | 1.1988 | 1.1867 | 1.1274 | 1.1747 | 1.0975 | 1.2514 | 1.1074 | 1.2057 |  | 0.5179 | 0.44496 | 0.42681 | 0.44567 | 0.43726 | 0.38368 | 0.45049 | 0.36945 | 0.45483 | 0.40851 | 0.49013 | 0.52146
Note on I6: :ProCost Perioodic replacement costs and savinsg of the measure. These are costs and savings that occur periodicially, but at different periods than annually. Can be positive or negative. Periodic replacement costs for both the measure and the baseline measure should be included if applicable. ProCost can analysze these costs in two ways dependent on the 'Repeat Periodic Replacemetn' switch in the ProData page. When set to 'On', ProCost repeats replacement costs for multiple times over the life of a measure depending on the input period and measure life. For example fluorescent lamps may have a 4-year replacement cycle that repeats 3 times in a 15-year measure life. When set to 'Off', ProCost reads the period as the year after installation that the replacement cost occurs and does not subsequently reinstall or repeat the replacement costs. For example a compressor may be replaced only once in the life of a heat-pump system. Example: A new fluorescent lighting systems may have a measure life of 15 years, and a lamp life of five years. Two lamps lamps per fixture must be replaced at years 6 and 11. Lamp and labor costs, expressed as positive costs, are entered as a cost and the period would be enetered as 5. The baseline measure may have a four year lamp life and would have required a three-lamp replacement at years 5, 9 and 13. Lamp and labor replacement costs would be entered as annual savings in dollars with a 4-year period. ProCost determines the net present value of the two cost streams.
Note on O6: :ProCost If the measure has gas savings for incfreases, enter the annual savings and shape of the savings here. Example: Clothes washer saves electric motor and dryer energy and gas water heat.
Note on A7: :Procost Category for the measure. Individual measures can be grouped into categories. Procost output is reported by measure and by category. All measures must belong to at least one category. Category name can be the same as measure name. Example: Measures can be combined into one category if they have components with different load shapes or measure lives. On wash machines there may be one load shape for the electric motor savings component, a second load shape for the electric water heat savings component and a third shape for electric dryer savings component.
Note on B7: :ProCost Name of Measure. User-defined. For PTR measures, defined naming conventions apply.
Note on C7: :ProCost Annual electric savings for the measure in kWh at the site. May be positive, negative or zero. Savings are incremental to the baseline alternative.
Note on D7: :ProCost Physical life of the measure in years. Must be >=1.
Note on E7: :ProCost Initial cost to install the measure in dollars. Costs are incremental to the baseline alternative. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on F7: :ProCost Annaul opperations and maintenace cost for the measure in dollars. Must be incremental cost over the baseline alternative. May be positive, negative or zero. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page. O&M costs are enetered as positive values. Negative values represent O&M savings compared to the baseline alternative. Example: Annualized maintenace cost for a heat pump heating system compared to a baseline electric resistance heating system.
Note on G7: :ProCost Name of the pointer to the shape of the savings. The shapes represent the daily and monthly shape of the savings in four time segments for each month of the year. Shape of the savings is relative to the baseline alternative. These shaps are in the MC_AND_Loadshape file.
Note on H7: :ProCost Annual value of any non-energy benefits of the measure, relative to the baseline alternative. Expressed in dollars per year and denominated in dollars of the 'Cost Reference Year'. Positive value represents dollar savings. Negative value represents dollar cost. Example: Water, detergent and sewer savings from efficient clothes washer.
Note on I7: : Cost in dollars that is incurred for Period 1. Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on J7: :ProCost Duration of Period1. The time at which Period 1 costs, or savings, occur. In years.
Note on K7: : Cost in dollars that is incurred for Period 2 Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on L7: :ProCost Duration of Period 2. The time at which Period 2 costs, or savings, occur. In years.
Note on M7: : Cost in dollars that is incurred for Period 3. Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on N7: :ProCost Duration of Period 3. The time at which Period 3 costs, or savings, occur. In years.
Note on O7: : Annual gas savings, or increases, in therms.
Note on P7: :ProCost Name of the pointer to the shape of the savings. The shapes represent the daily and monthly shape of the savings in four time segments for each month of the year. Shape of the savings is relative to the baseline alternative. These shaps are in the MC_AND_Loadshape file.
Note on BH88: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BM88: Direct and program administrative costs of the measure to sponsor. Separate costs for each sponsor. Depends on share of costs incurred by sponsor, sponsor cost of capital, and financing term which are user-defined inputs. Includes applicable Capital, O&M, Periodic Replacement and Program Administrative costs. Sponsor costs are levelized over program life. Does not include any adjustments for benefit. NOTE: Units are per kWh for 'Electric' runs and per therm for 'Gas' runs for all sponsors.
Note on CE88: All costs minus all benefits regardless of which sponsor incurs the cost or accrues the benefits. TRC Net Levelized Cost includes all applicable costs and all benefits. In addition to energy system costs and benefits, TRC Net Levelized Cost includes non-energy, other-fuel, O&M, periodic-replacement and risk-mitigation benefits and costs. TRC Net Levelized Cost corresponds to TRC B/C ratios with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure. The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the TRC B/C ratio and the TRC Net Levelized Cost. If Risk-Mitigation credit is non-zero, TRC Levelized Cost will be reduced by the risk-mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on CW88: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BH147: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BM147: Direct and program administrative costs of the measure to sponsor. Separate costs for each sponsor. Depends on share of costs incurred by sponsor, sponsor cost of capital, and financing term which are user-defined inputs. Includes applicable Capital, O&M, Periodic Replacement and Program Administrative costs. Sponsor costs are levelized over program life. Does not include any adjustments for benefit. NOTE: Units are per kWh for 'Electric' runs and per therm for 'Gas' runs for all sponsors.
Note on CE147: All costs minus all benefits regardless of which sponsor incurs the cost or accrues the benefits. TRC Net Levelized Cost includes all applicable costs and all benefits. In addition to energy system costs and benefits, TRC Net Levelized Cost includes non-energy, other-fuel, O&M, periodic-replacement and risk-mitigation benefits and costs. TRC Net Levelized Cost corresponds to TRC B/C ratios with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure. The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the TRC B/C ratio and the TRC Net Levelized Cost. If Risk-Mitigation credit is non-zero, TRC Levelized Cost will be reduced by the risk-mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on CW147: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.

## MMap
Measure Map
ElecHt%TYP
Maybe need to eliminate the Indirect functions | [8 empty] | GasHt%TYP
HtPmpHt%TYP
Commercial EM
[8 empty] | ElecHt | GasHt | HtPmpHt | [10 empty] | 1000 | 1000 | 1000
[8 empty] | ElecHt%TYP | GasHt%TYP | HtPmpHt%TYP | BuiltUp%TYP | raw | raw |  | CoolSat%TYP |  | FloorA%TYP | FloorA%REG |  |  | Per 1000 sf | Per 1000 sf | Per 1000 sf
Measure Index Name | Category Name | Measure Name | BType | MOPP | End Use | Heat Fuel | Life | ElecHt%TYP | GasHt%TYP | HtPmpHt%TYP | BuiltUp%TYP | RAW Savings (kWh/yr.) | RAW Capital Cost ($) | STOCK | COOLING SATURATION | Btype IDX | Activity Type WT for MOPP Cohort | Btype WT for Region for MOPP and Cohort | Weighted Savings Sytem and Heat Type | Gas Heat Savings | Weighted Savings for Region (kWh) | Weighted Cost for Region | Weighted Savings for Region (Therms)
Commercial EM-Retro | Commercial EM-Retro-Large Off | Commercial EM-Retro-Large Off-GasHt | Large Off | Retro | Cool | GasHt | 5 | 20.94% | 54.04% | 25.02% | 63.01% | 0.95631 | 0.25096 | _PRE2013 | 76.89% | 2 | 43.94% | 9.634% | 0.3256 | 0.03975 | 325.5954 | 85.4452 | 13.5337
Commercial EM-Retro | Commercial EM-Retro-Medium Off | Commercial EM-Retro-Medium Off-GasHt | Medium Off | Retro | Cool | GasHt | 5 | 22.13% | 51.43% | 26.44% | 9.396% | 0.77169 | 0.25096 | _PRE2013 | 91.57% | 3 | 43.06% | 9.442% | 0.037293 | 0.03975 | 37.2926 | 12.1279 | 1.9209
Commercial EM-Retro | Commercial EM-Retro-Small Off | Commercial EM-Retro-Small Off-GasHt | Small Off | Retro | Cool | GasHt | 5 | 30.64% | 32.75% | 36.6% | 2.901% | 0.624 | 0.55769 | _PRE2013 | 85.58% | 4 | 13% | 2.85% | 0.0059285 | 0.03975 | 5.9285 | 5.2985 | 0.37766
Commercial EM-Retro | Commercial EM-Retro-Xlarge Ret | Commercial EM-Retro-Xlarge Ret-GasHt | Xlarge Ret | Retro | Cool | GasHt | 5 | 5.3% | 91.61% | 3.094% | 3.916% | 0.77169 | 0.25096 | _PRE2013 | 95.16% | 5 | 23.46% | 3.999% | 0.027686 | 0.042694 | 27.6862 | 9.0038 | 1.5318
Commercial EM-Retro | Commercial EM-Retro-Large Ret | Commercial EM-Retro-Large Ret-GasHt | Large Ret | Retro | Cool | GasHt | 5 | 1.059% | 98.32% | 0.6184% | 25.78% | 0.84923 | 0.55769 | _PRE2013 | 98.53% | 6 | 5.526% | 0.942% | 0.21523 | 0.042694 | 215.2309 | 141.3428 | 10.8206
Commercial EM-Retro | Commercial EM-Retro-Medium Ret | Commercial EM-Retro-Medium Ret-GasHt | Medium Ret | Retro | Cool | GasHt | 5 | 12.01% | 80.99% | 7.009% | 2.757% | 1.1815 | 0.55769 | _PRE2013 | 65.23% | 7 | 60.64% | 10.34% | 0.026385 | 0.042694 | 26.3853 | 12.454 | 0.95342
Commercial EM-Retro | Commercial EM-Retro-Small Ret | Commercial EM-Retro-Small Ret-GasHt | Small Ret | Retro | Cool | GasHt | 5 | 27.33% | 56.72% | 15.95% | 10.15% | 1.2369 | 0.25096 | _PRE2013 | 66.01% | 8 | 10.37% | 1.768% | 0.071183 | 0.042694 | 71.1826 | 14.4424 | 2.457
Commercial EM-Retro | Commercial EM-Retro-School K-12 | Commercial EM-Retro-School K-12-GasHt | School K-12 | Retro | Cool | GasHt | 5 | 5.837% | 84.78% | 9.385% | 29.52% | 0.57231 | 0.27885 | _PRE2013 | 69.62% | 9 | 66.43% | 7.326% | 0.14321 | 0.042694 | 143.2053 | 69.7741 | 10.6832
Commercial EM-Retro | Commercial EM-Retro-University | Commercial EM-Retro-University-GasHt | University | Retro | Cool | GasHt | 5 | 10% | 80% | 10% | 77.76% | 0.94154 | 0.27885 | _PRE2013 | 75% | 10 | 33.57% | 3.702% | 0.58569 | 0.042694 | 585.688 | 173.4574 | 26.5583
Commercial EM-Retro | Commercial EM-Retro-Warehouse | Commercial EM-Retro-Warehouse-GasHt | Warehouse | Retro | Cool | GasHt | 5 | 0.6393% | 98.7% | 0.6603% | 13.08% | 0.20308 | 0.11154 | _PRE2013 | 23% | 11 | 100% | 13.2% | 0.026223 | 0.025028 | 26.2232 | 14.4029 | 3.2318
Commercial EM-Retro | Commercial EM-Retro-Supermarket | Commercial EM-Retro-Supermarket-GasHt | Supermarket | Retro | Cool | GasHt | 5 | 3.918% | 46.96% | 6.235% | 7.145% | 1.4031 | 0.33462 | _PRE2013 | 89.44% | 12 | 84.84% | 1.954% | 0.047073 | 0.073611 | 47.0726 | 11.2262 | 2.4696
Commercial EM-Retro | Commercial EM-Retro-MiniMart | Commercial EM-Retro-MiniMart-GasHt | MiniMart | Retro | Cool | GasHt | 5 | 0.9894% | 86.61% | 1.574% | 0% | 1.8646 | 0.55769 | _PRE2013 | 91.39% | 13 | 15.16% | 0.3491% | 0 | 0.073611 | 0 | 0 | 0
Commercial EM-Retro | Commercial EM-Retro-Restaurant | Commercial EM-Retro-Restaurant-GasHt | Restaurant | Retro | Cool | GasHt | 5 | 3.005% | 79.37% | 17.63% | 2.353% | 1.8646 | 0.55769 | _PRE2013 | 95.81% | 14 | 100% | 1.584% | 0.034815 | 0.073611 | 34.815 | 10.4129 | 1.3744
Commercial EM-Retro | Commercial EM-Retro-Lodging | Commercial EM-Retro-Lodging-GasHt | Lodging | Retro | Cool | GasHt | 5 | 44.68% | 24.94% | 30.38% | 7.935% | 0.94154 | 0.25096 | _PRE2013 | 82.64% | 15 | 100% | 5.107% | 0.018634 | 0.044167 | 18.6335 | 4.9667 | 0.87408
Commercial EM-Retro | Commercial EM-Retro-Hospital | Commercial EM-Retro-Hospital-GasHt | Hospital | Retro | Cool | GasHt | 5 | 8% | 91% | 1% | 85.34% | 1.6985 | 0.27885 | _PRE2013 | 95% | 16 | 100% | 3.098% | 1.319 | 0.073611 | 1319.0104 | 216.5495 | 57.1657
Commercial EM-Retro | Commercial EM-Retro-Residential Care | Commercial EM-Retro-Residential Care-GasHt | Residential Care | Retro | Cool | GasHt | 5 | 33.99% | 40.56% | 25.46% | 7.623% | 1.44 | 0.27885 | _PRE2013 | 82.65% | 17 | 100% | 3.737% | 0.044518 | 0.073611 | 44.5184 | 8.6207 | 2.2757
Commercial EM-Retro | Commercial EM-Retro-Assembly | Commercial EM-Retro-Assembly-GasHt | Assembly | Retro | Cool | GasHt | 5 | 10.64% | 77.82% | 11.54% | 16.85% | 0.84923 | 0.25096 | _PRE2013 | 77.18% | 18 | 100% | 11.01% | 0.11138 | 0.058889 | 111.3777 | 32.9139 | 7.7234
Commercial EM-Retro | Commercial EM-Retro-Other | Commercial EM-Retro-Other-GasHt | Other | Retro | Cool | GasHt | 5 | 16.94% | 72.57% | 10.49% | 20.05% | 0.84923 | 0.25096 | _PRE2013 | 71.31% | 19 | 100% | 9.955% | 0.12358 | 0.088333 | 123.5787 | 36.5195 | 12.8541
Commercial EM-Retro | Commercial EM-Retro-Large Off | Commercial EM-Retro-Large Off-ElecHt | Large Off | Retro | Cool | ElecHt | 5 | 20.94% | 54.04% | 25.02% | 63.01% | 1.3071 | 0.25096 | _PRE2013 | 76.89% | 2 | 43.94% | 9.634% | 0.17248 | 0 | 172.4784 | 33.1162 | 0
Commercial EM-Retro | Commercial EM-Retro-Medium Off | Commercial EM-Retro-Medium Off-ElecHt | Medium Off | Retro | Cool | ElecHt | 5 | 22.13% | 51.43% | 26.44% | 9.396% | 1.1225 | 0.25096 | _PRE2013 | 91.57% | 3 | 43.06% | 9.442% | 0.023342 | 0 | 23.3419 | 5.2188 | 0
Commercial EM-Retro | Commercial EM-Retro-Small Off | Commercial EM-Retro-Small Off-ElecHt | Small Off | Retro | Cool | ElecHt | 5 | 30.64% | 32.75% | 36.6% | 2.901% | 0.97477 | 0.55769 | _PRE2013 | 85.58% | 4 | 13% | 2.85% | 0.0086636 | 0 | 8.6636 | 4.9567 | 0
Commercial EM-Retro | Commercial EM-Retro-Xlarge Ret | Commercial EM-Retro-Xlarge Ret-ElecHt | Xlarge Ret | Retro | Cool | ElecHt | 5 | 5.3% | 91.61% | 3.094% | 3.916% | 1.1225 | 0.25096 | _PRE2013 | 95.16% | 5 | 23.46% | 3.999% | 0.0023297 | 0 | 2.3297 | 0.52088 | 0
Commercial EM-Retro | Commercial EM-Retro-Large Ret | Commercial EM-Retro-Large Ret-ElecHt | Large Ret | Retro | Cool | ElecHt | 5 | 1.059% | 98.32% | 0.6184% | 25.78% | 1.2369 | 0.55769 | _PRE2013 | 98.53% | 6 | 5.526% | 0.942% | 0.0033775 | 0 | 3.3775 | 1.5228 | 0
Commercial EM-Retro | Commercial EM-Retro-Medium Ret | Commercial EM-Retro-Medium Ret-ElecHt | Medium Ret | Retro | Cool | ElecHt | 5 | 12.01% | 80.99% | 7.009% | 2.757% | 1.7169 | 0.55769 | _PRE2013 | 65.23% | 7 | 60.64% | 10.34% | 0.0056842 | 0 | 5.6842 | 1.8463 | 0
Commercial EM-Retro | Commercial EM-Retro-Small Ret | Commercial EM-Retro-Small Ret-ElecHt | Small Ret | Retro | Cool | ElecHt | 5 | 27.33% | 56.72% | 15.95% | 10.15% | 1.7723 | 0.25096 | _PRE2013 | 66.01% | 8 | 10.37% | 1.768% | 0.049145 | 0 | 49.1453 | 6.9591 | 0
Commercial EM-Retro | Commercial EM-Retro-School K-12 | Commercial EM-Retro-School K-12-ElecHt | School K-12 | Retro | Cool | ElecHt | 5 | 5.837% | 84.78% | 9.385% | 29.52% | 1.1077 | 0.27885 | _PRE2013 | 69.62% | 9 | 66.43% | 7.326% | 0.019083 | 0 | 19.0832 | 4.8039 | 0
Commercial EM-Retro | Commercial EM-Retro-University | Commercial EM-Retro-University-ElecHt | University | Retro | Cool | ElecHt | 5 | 10% | 80% | 10% | 77.76% | 1.6615 | 0.27885 | _PRE2013 | 75% | 10 | 33.57% | 3.702% | 0.1292 | 0 | 129.1959 | 21.6822 | 0
Commercial EM-Retro | Commercial EM-Retro-Warehouse | Commercial EM-Retro-Warehouse-ElecHt | Warehouse | Retro | Cool | ElecHt | 5 | 0.6393% | 98.7% | 0.6603% | 13.08% | 0.55385 | 0.11154 | _PRE2013 | 23% | 11 | 100% | 13.2% | 0.00046323 | 0 | 0.46323 | 0.093289 | 0
Commercial EM-Retro | Commercial EM-Retro-Supermarket | Commercial EM-Retro-Supermarket-ElecHt | Supermarket | Retro | Cool | ElecHt | 5 | 3.918% | 46.96% | 6.235% | 7.145% | 2.3077 | 0.33462 | _PRE2013 | 89.44% | 12 | 84.84% | 1.954% | 0.0064604 | 0 | 6.4604 | 0.93675 | 0
Commercial EM-Retro | Commercial EM-Retro-MiniMart | Commercial EM-Retro-MiniMart-ElecHt | MiniMart | Retro | Cool | ElecHt | 5 | 0.9894% | 86.61% | 1.574% | 0% | 2.5846 | 0.55769 | _PRE2013 | 91.39% | 13 | 15.16% | 0.3491% | 0 | 0 | 0 | 0 | 0
Commercial EM-Retro | Commercial EM-Retro-Restaurant | Commercial EM-Retro-Restaurant-ElecHt | Restaurant | Retro | Cool | ElecHt | 5 | 3.005% | 79.37% | 17.63% | 2.353% | 2.5846 | 0.55769 | _PRE2013 | 95.81% | 14 | 100% | 1.584% | 0.0018272 | 0 | 1.8272 | 0.39427 | 0
Commercial EM-Retro | Commercial EM-Retro-Lodging | Commercial EM-Retro-Lodging-ElecHt | Lodging | Retro | Cool | ElecHt | 5 | 44.68% | 24.94% | 30.38% | 7.935% | 1.6615 | 0.25096 | _PRE2013 | 82.64% | 15 | 100% | 5.107% | 0.058904 | 0 | 58.9041 | 8.897 | 0
Commercial EM-Retro | Commercial EM-Retro-Hospital | Commercial EM-Retro-Hospital-ElecHt | Hospital | Retro | Cool | ElecHt | 5 | 8% | 91% | 1% | 85.34% | 2.7692 | 0.27885 | _PRE2013 | 95% | 16 | 100% | 3.098% | 0.18906 | 0 | 189.0603 | 19.0373 | 0
Commercial EM-Retro | Commercial EM-Retro-Residential Care | Commercial EM-Retro-Residential Care-ElecHt | Residential Care | Retro | Cool | ElecHt | 5 | 33.99% | 40.56% | 25.46% | 7.623% | 2.3446 | 0.27885 | _PRE2013 | 82.65% | 17 | 100% | 3.737% | 0.060741 | 0 | 60.7411 | 7.224 | 0
Commercial EM-Retro | Commercial EM-Retro-Assembly | Commercial EM-Retro-Assembly-ElecHt | Assembly | Retro | Cool | ElecHt | 5 | 10.64% | 77.82% | 11.54% | 16.85% | 1.5692 | 0.25096 | _PRE2013 | 77.18% | 18 | 100% | 11.01% | 0.028141 | 0 | 28.1412 | 4.5005 | 0
Commercial EM-Retro | Commercial EM-Retro-Other | Commercial EM-Retro-Other-ElecHt | Other | Retro | Cool | ElecHt | 5 | 16.94% | 72.57% | 10.49% | 20.05% | 1.5692 | 0.25096 | _PRE2013 | 71.31% | 19 | 100% | 9.955% | 0.053301 | 0 | 53.3014 | 8.5243 | 0
Commercial EM-Retro | Commercial EM-Retro-Large Off | Commercial EM-Retro-Large Off-HtPmpHt | Large Off | Retro | Cool | HtPmpHt | 5 | 20.94% | 54.04% | 25.02% | 63.01% | 1.1225 | 0.25096 | _PRE2013 | 76.89% | 2 | 43.94% | 9.634% | 0.17695 | 0 | 176.9464 | 39.5619 | 0
Commercial EM-Retro | Commercial EM-Retro-Medium Off | Commercial EM-Retro-Medium Off-HtPmpHt | Medium Off | Retro | Cool | HtPmpHt | 5 | 22.13% | 51.43% | 26.44% | 9.396% | 0.93785 | 0.25096 | _PRE2013 | 91.57% | 3 | 43.06% | 9.442% | 0.023299 | 0 | 23.2988 | 6.2346 | 0
Commercial EM-Retro | Commercial EM-Retro-Small Off | Commercial EM-Retro-Small Off-HtPmpHt | Small Off | Retro | Cool | HtPmpHt | 5 | 30.64% | 32.75% | 36.6% | 2.901% | 0.79015 | 0.55769 | _PRE2013 | 85.58% | 4 | 13% | 2.85% | 0.0083897 | 0 | 8.3897 | 5.9214 | 0
Commercial EM-Retro | Commercial EM-Retro-Xlarge Ret | Commercial EM-Retro-Xlarge Ret-HtPmpHt | Xlarge Ret | Retro | Cool | HtPmpHt | 5 | 5.3% | 91.61% | 3.094% | 3.916% | 0.93785 | 0.25096 | _PRE2013 | 95.16% | 5 | 23.46% | 3.999% | 0.0011363 | 0 | 1.1363 | 0.30407 | 0
Commercial EM-Retro | Commercial EM-Retro-Large Ret | Commercial EM-Retro-Large Ret-HtPmpHt | Large Ret | Retro | Cool | HtPmpHt | 5 | 1.059% | 98.32% | 0.6184% | 25.78% | 1.0338 | 0.55769 | _PRE2013 | 98.53% | 6 | 5.526% | 0.942% | 0.0016479 | 0 | 1.6479 | 0.88895 | 0
Commercial EM-Retro | Commercial EM-Retro-Medium Ret | Commercial EM-Retro-Medium Ret-HtPmpHt | Medium Ret | Retro | Cool | HtPmpHt | 5 | 12.01% | 80.99% | 7.009% | 2.757% | 1.44 | 0.55769 | _PRE2013 | 65.23% | 7 | 60.64% | 10.34% | 0.002783 | 0 | 2.783 | 1.0778 | 0
Commercial EM-Retro | Commercial EM-Retro-Small Ret | Commercial EM-Retro-Small Ret-HtPmpHt | Small Ret | Retro | Cool | HtPmpHt | 5 | 27.33% | 56.72% | 15.95% | 10.15% | 1.4954 | 0.25096 | _PRE2013 | 66.01% | 8 | 10.37% | 1.768% | 0.024206 | 0 | 24.2064 | 4.0624 | 0
Commercial EM-Retro | Commercial EM-Retro-School K-12 | Commercial EM-Retro-School K-12-HtPmpHt | School K-12 | Retro | Cool | HtPmpHt | 5 | 5.837% | 84.78% | 9.385% | 29.52% | 0.83077 | 0.27885 | _PRE2013 | 69.62% | 9 | 66.43% | 7.326% | 0.023013 | 0 | 23.0131 | 7.7243 | 0
Commercial EM-Retro | Commercial EM-Retro-University | Commercial EM-Retro-University-HtPmpHt | University | Retro | Cool | HtPmpHt | 5 | 10% | 80% | 10% | 77.76% | 1.2923 | 0.27885 | _PRE2013 | 75% | 10 | 33.57% | 3.702% | 0.10049 | 0 | 100.4857 | 21.6822 | 0
Commercial EM-Retro | Commercial EM-Retro-Warehouse | Commercial EM-Retro-Warehouse-HtPmpHt | Warehouse | Retro | Cool | HtPmpHt | 5 | 0.6393% | 98.7% | 0.6603% | 13.08% | 0.36923 | 0.11154 | _PRE2013 | 23% | 11 | 100% | 13.2% | 0.00031898 | 0 | 0.31898 | 0.096359 | 0
Commercial EM-Retro | Commercial EM-Retro-Supermarket | Commercial EM-Retro-Supermarket-HtPmpHt | Supermarket | Retro | Cool | HtPmpHt | 5 | 3.918% | 46.96% | 6.235% | 7.145% | 1.8462 | 0.33462 | _PRE2013 | 89.44% | 12 | 84.84% | 1.954% | 0.0082238 | 0 | 8.2238 | 1.4906 | 0
Commercial EM-Retro | Commercial EM-Retro-MiniMart | Commercial EM-Retro-MiniMart-HtPmpHt | MiniMart | Retro | Cool | HtPmpHt | 5 | 0.9894% | 86.61% | 1.574% | 0% | 2.2154 | 0.55769 | _PRE2013 | 91.39% | 13 | 15.16% | 0.3491% | 0 | 0 | 0 | 0 | 0
Commercial EM-Retro | Commercial EM-Retro-Restaurant | Commercial EM-Retro-Restaurant-HtPmpHt | Restaurant | Retro | Cool | HtPmpHt | 5 | 3.005% | 79.37% | 17.63% | 2.353% | 2.2154 | 0.55769 | _PRE2013 | 95.81% | 14 | 100% | 1.584% | 0.0091884 | 0 | 9.1884 | 2.313 | 0
Commercial EM-Retro | Commercial EM-Retro-Lodging | Commercial EM-Retro-Lodging-HtPmpHt | Lodging | Retro | Cool | HtPmpHt | 5 | 44.68% | 24.94% | 30.38% | 7.935% | 1.2923 | 0.25096 | _PRE2013 | 82.64% | 15 | 100% | 5.107% | 0.031151 | 0 | 31.1509 | 6.0494 | 0
Commercial EM-Retro | Commercial EM-Retro-Hospital | Commercial EM-Retro-Hospital-HtPmpHt | Hospital | Retro | Cool | HtPmpHt | 5 | 8% | 91% | 1% | 85.34% | 2.2154 | 0.27885 | _PRE2013 | 95% | 16 | 100% | 3.098% | 0.018906 | 0 | 18.906 | 2.3797 | 0
Commercial EM-Retro | Commercial EM-Retro-Residential Care | Commercial EM-Retro-Residential Care-HtPmpHt | Residential Care | Retro | Cool | HtPmpHt | 5 | 33.99% | 40.56% | 25.46% | 7.623% | 1.8831 | 0.27885 | _PRE2013 | 82.65% | 17 | 100% | 3.737% | 0.036543 | 0 | 36.5428 | 5.4113 | 0
Commercial EM-Retro | Commercial EM-Retro-Assembly | Commercial EM-Retro-Assembly-HtPmpHt | Assembly | Retro | Cool | HtPmpHt | 5 | 10.64% | 77.82% | 11.54% | 16.85% | 1.2 | 0.25096 | _PRE2013 | 77.18% | 18 | 100% | 11.01% | 0.023349 | 0 | 23.3486 | 4.883 | 0
Commercial EM-Retro | Commercial EM-Retro-Other | Commercial EM-Retro-Other-HtPmpHt | Other | Retro | Cool | HtPmpHt | 5 | 16.94% | 72.57% | 10.49% | 20.05% | 1.2 | 0.25096 | _PRE2013 | 71.31% | 19 | 100% | 9.955% | 0.025238 | 0 | 25.2384 | 5.2782 | 0
Commercial EM-New | Commercial EM-New-Large Off | Commercial EM-New-Large Off-GasHt | Large Off | New | Cool | GasHt | 5 | 9.379% | 80.87% | 9.748% | 85% | 0.95631 | 0.25096 | POST2013 | 95.13% | 2 | 49.84% | 15.07% | 0.65738 | 0.03975 | 657.3838 | 172.5156 | 27.3249
Commercial EM-New | Commercial EM-New-Medium Off | Commercial EM-New-Medium Off-GasHt | Medium Off | New | Cool | GasHt | 5 | 5.714% | 93.11% | 1.177% | 35% | 0.77169 | 0.25096 | POST2013 | 97.67% | 3 | 39.73% | 12.01% | 0.25148 | 0.03975 | 251.4791 | 81.7833 | 12.9537
Commercial EM-New | Commercial EM-New-Small Off | Commercial EM-New-Small Off-GasHt | Small Off | New | Cool | GasHt | 5 | 6.354% | 65.88% | 27.77% | 2.901% | 0.624 | 0.55769 | POST2013 | 91.12% | 4 | 10.43% | 3.154% | 0.011924 | 0.03975 | 11.9241 | 10.657 | 0.75959
Commercial EM-New | Commercial EM-New-Xlarge Ret | Commercial EM-New-Xlarge Ret-GasHt | Xlarge Ret | New | Cool | GasHt | 5 | 52.11% | 30.36% | 17.52% | 3.916% | 0.77169 | 0.25096 | POST2013 | 98.61% | 5 | 29.29% | 2.682% | 0.009177 | 0.042694 | 9.177 | 2.9844 | 0.50772
Commercial EM-New | Commercial EM-New-Large Ret | Commercial EM-New-Large Ret-GasHt | Large Ret | New | Cool | GasHt | 5 | 64.09% | 20.98% | 14.93% | 25.78% | 0.84923 | 0.55769 | POST2013 | 77.18% | 6 | 11.84% | 1.084% | 0.045926 | 0.042694 | 45.9264 | 30.16 | 2.3089
Commercial EM-New | Commercial EM-New-Medium Ret | Commercial EM-New-Medium Ret-GasHt | Medium Ret | New | Cool | GasHt | 5 | 56.16% | 42.42% | 1.418% | 2.757% | 1.1815 | 0.55769 | POST2013 | 90.53% | 7 | 44.66% | 4.089% | 0.013822 | 0.042694 | 13.8216 | 6.5238 | 0.49944
Commercial EM-New | Commercial EM-New-Small Ret | Commercial EM-New-Small Ret-GasHt | Small Ret | New | Cool | GasHt | 5 | 19.95% | 44.75% | 35.3% | 10.15% | 1.2369 | 0.25096 | POST2013 | 53.67% | 8 | 14.21% | 1.302% | 0.05616 | 0.042694 | 56.16 | 11.3944 | 1.9385
Commercial EM-New | Commercial EM-New-School K-12 | Commercial EM-New-School K-12-GasHt | School K-12 | New | Cool | GasHt | 5 | 22.29% | 53.09% | 24.62% | 29.52% | 0.57231 | 0.27885 | POST2013 | 96.13% | 9 | 58.04% | 3.089% | 0.08968 | 0.042694 | 89.6797 | 43.6948 | 6.6902
Commercial EM-New | Commercial EM-New-University | Commercial EM-New-University-GasHt | University | New | Cool | GasHt | 5 | 15.89% | 73.04% | 11.08% | 77.76% | 0.94154 | 0.27885 | POST2013 | 75% | 10 | 41.96% | 2.233% | 0.53472 | 0.042694 | 534.7222 | 158.3634 | 24.2472
Commercial EM-New | Commercial EM-New-Warehouse | Commercial EM-New-Warehouse-GasHt | Warehouse | New | Cool | GasHt | 5 | 52.11% | 30.36% | 17.52% | 13.08% | 0.20308 | 0.11154 | POST2013 | 18.16% | 11 | 100% | 10.09% | 0.0080674 | 0.025028 | 8.0674 | 4.431 | 0.99425
Commercial EM-New | Commercial EM-New-Supermarket | Commercial EM-New-Supermarket-GasHt | Supermarket | New | Cool | GasHt | 5 | 1.538% | 88.46% | 10.01% | 7.145% | 1.4031 | 0.33462 | POST2013 | 92.15% | 12 | 70.77% | 0.6168% | 0.088673 | 0.073611 | 88.6733 | 21.1474 | 4.6522
Commercial EM-New | Commercial EM-New-MiniMart | Commercial EM-New-MiniMart-GasHt | MiniMart | New | Cool | GasHt | 5 | 0% | 99.62% | 0.3792% | 0% | 1.8646 | 0.55769 | POST2013 | 83.87% | 13 | 29.23% | 0.2548% | 0 | 0.073611 | 0 | 0 | 0
Commercial EM-New | Commercial EM-New-Restaurant | Commercial EM-New-Restaurant-GasHt | Restaurant | New | Cool | GasHt | 5 | 5.521% | 88.37% | 6.112% | 2.353% | 1.8646 | 0.55769 | POST2013 | 100% | 14 | 100% | 1.169% | 0.038764 | 0.073611 | 38.7637 | 11.5939 | 1.5303
Commercial EM-New | Commercial EM-New-Lodging | Commercial EM-New-Lodging-GasHt | Lodging | New | Cool | GasHt | 5 | 34.34% | 53.62% | 12.04% | 7.935% | 0.94154 | 0.25096 | POST2013 | 94.44% | 15 | 100% | 2.396% | 0.040057 | 0.044167 | 40.0566 | 10.6768 | 1.879
Commercial EM-New | Commercial EM-New-Hospital | Commercial EM-New-Hospital-GasHt | Hospital | New | Cool | GasHt | 5 | 10.31% | 74.19% | 15.5% | 85.34% | 1.6985 | 0.27885 | POST2013 | 95% | 16 | 100% | 4.497% | 1.0754 | 0.073611 | 1075.3938 | 176.5536 | 46.6074
Commercial EM-New | Commercial EM-New-Residential Care | Commercial EM-New-Residential Care-GasHt | Residential Care | New | Cool | GasHt | 5 | 0.5608% | 98.58% | 0.8634% | 7.623% | 1.44 | 0.27885 | POST2013 | 84.23% | 17 | 100% | 5.828% | 0.10821 | 0.073611 | 108.2051 | 20.9532 | 5.5313
Commercial EM-New | Commercial EM-New-Assembly | Commercial EM-New-Assembly-GasHt | Assembly | New | Cool | GasHt | 5 | 0.5608% | 98.58% | 0.8634% | 16.85% | 0.84923 | 0.25096 | POST2013 | 91.18% | 18 | 100% | 9.098% | 0.14109 | 0.058889 | 141.0921 | 41.695 | 9.7839
Commercial EM-New | Commercial EM-New-Other | Commercial EM-New-Other-GasHt | Other | New | Cool | GasHt | 5 | 24.03% | 67.84% | 8.133% | 20.05% | 0.84923 | 0.25096 | POST2013 | 87.72% | 19 | 100% | 21.33% | 0.11552 | 0.088333 | 115.5154 | 34.1367 | 12.0154
Commercial EM-New | Commercial EM-New-Large Off | Commercial EM-New-Large Off-ElecHt | Large Off | New | Cool | ElecHt | 5 | 9.379% | 80.87% | 9.748% | 85% | 1.3071 | 0.25096 | POST2013 | 95.13% | 2 | 49.84% | 15.07% | 0.1042 | 0 | 104.2022 | 20.007 | 0
Commercial EM-New | Commercial EM-New-Medium Off | Commercial EM-New-Medium Off-ElecHt | Medium Off | New | Cool | ElecHt | 5 | 5.714% | 93.11% | 1.177% | 35% | 0.77169 | 0.25096 | POST2013 | 97.67% | 3 | 39.73% | 12.01% | 0.015433 | 0 | 15.4333 | 5.0191 | 0
Commercial EM-New | Commercial EM-New-Small Off | Commercial EM-New-Small Off-ElecHt | Small Off | New | Cool | ElecHt | 5 | 6.354% | 65.88% | 27.77% | 2.901% | 0.624 | 0.55769 | POST2013 | 91.12% | 4 | 10.43% | 3.154% | 0.0011501 | 0 | 1.1501 | 1.0279 | 0
Commercial EM-New | Commercial EM-New-Xlarge Ret | Commercial EM-New-Xlarge Ret-ElecHt | Xlarge Ret | New | Cool | ElecHt | 5 | 52.11% | 30.36% | 17.52% | 3.916% | 0.77169 | 0.25096 | POST2013 | 98.61% | 5 | 29.29% | 2.682% | 0.015751 | 0 | 15.7506 | 5.1222 | 0
Commercial EM-New | Commercial EM-New-Large Ret | Commercial EM-New-Large Ret-ElecHt | Large Ret | New | Cool | ElecHt | 5 | 64.09% | 20.98% | 14.93% | 25.78% | 0.84923 | 0.55769 | POST2013 | 77.18% | 6 | 11.84% | 1.084% | 0.14031 | 0 | 140.305 | 92.1387 | 0
Commercial EM-New | Commercial EM-New-Medium Ret | Commercial EM-New-Medium Ret-ElecHt | Medium Ret | New | Cool | ElecHt | 5 | 56.16% | 42.42% | 1.418% | 2.757% | 1.1815 | 0.55769 | POST2013 | 90.53% | 7 | 44.66% | 4.089% | 0.018297 | 0 | 18.2971 | 8.6363 | 0
Commercial EM-New | Commercial EM-New-Small Ret | Commercial EM-New-Small Ret-ElecHt | Small Ret | New | Cool | ElecHt | 5 | 19.95% | 44.75% | 35.3% | 10.15% | 1.2369 | 0.25096 | POST2013 | 53.67% | 8 | 14.21% | 1.302% | 0.025041 | 0 | 25.0413 | 5.0807 | 0
Commercial EM-New | Commercial EM-New-School K-12 | Commercial EM-New-School K-12-ElecHt | School K-12 | New | Cool | ElecHt | 5 | 22.29% | 53.09% | 24.62% | 29.52% | 0.57231 | 0.27885 | POST2013 | 96.13% | 9 | 58.04% | 3.089% | 0.037646 | 0 | 37.646 | 18.3423 | 0
Commercial EM-New | Commercial EM-New-University | Commercial EM-New-University-ElecHt | University | New | Cool | ElecHt | 5 | 15.89% | 73.04% | 11.08% | 77.76% | 0.94154 | 0.27885 | POST2013 | 75% | 10 | 41.96% | 2.233% | 0.1163 | 0 | 116.3004 | 34.4435 | 0
Commercial EM-New | Commercial EM-New-Warehouse | Commercial EM-New-Warehouse-ElecHt | Warehouse | New | Cool | ElecHt | 5 | 52.11% | 30.36% | 17.52% | 13.08% | 0.20308 | 0.11154 | POST2013 | 18.16% | 11 | 100% | 10.09% | 0.013846 | 0 | 13.8461 | 7.6049 | 0
Commercial EM-New | Commercial EM-New-Supermarket | Commercial EM-New-Supermarket-ElecHt | Supermarket | New | Cool | ElecHt | 5 | 1.538% | 88.46% | 10.01% | 7.145% | 1.4031 | 0.33462 | POST2013 | 92.15% | 12 | 70.77% | 0.6168% | 0.0015416 | 0 | 1.5416 | 0.36764 | 0
Commercial EM-New | Commercial EM-New-MiniMart | Commercial EM-New-MiniMart-ElecHt | MiniMart | New | Cool | ElecHt | 5 | 0% | 99.62% | 0.3792% | 0% | 1.8646 | 0.55769 | POST2013 | 83.87% | 13 | 29.23% | 0.2548% | 0 | 0 | 0 | 0 | 0
Commercial EM-New | Commercial EM-New-Restaurant | Commercial EM-New-Restaurant-ElecHt | Restaurant | New | Cool | ElecHt | 5 | 5.521% | 88.37% | 6.112% | 2.353% | 1.8646 | 0.55769 | POST2013 | 100% | 14 | 100% | 1.169% | 0.002422 | 0 | 2.422 | 0.7244 | 0
Commercial EM-New | Commercial EM-New-Lodging | Commercial EM-New-Lodging-ElecHt | Lodging | New | Cool | ElecHt | 5 | 34.34% | 53.62% | 12.04% | 7.935% | 1.6615 | 0.25096 | POST2013 | 94.44% | 15 | 100% | 2.396% | 0.045276 | 0 | 45.2759 | 6.8385 | 0
Commercial EM-New | Commercial EM-New-Hospital | Commercial EM-New-Hospital-ElecHt | Hospital | New | Cool | ElecHt | 5 | 10.31% | 74.19% | 15.5% | 85.34% | 1.6985 | 0.27885 | POST2013 | 95% | 16 | 100% | 4.497% | 0.14946 | 0 | 149.4605 | 24.5378 | 0
Commercial EM-New | Commercial EM-New-Residential Care | Commercial EM-New-Residential Care-ElecHt | Residential Care | New | Cool | ElecHt | 5 | 0.5608% | 98.58% | 0.8634% | 7.623% | 1.44 | 0.27885 | POST2013 | 84.23% | 17 | 100% | 5.828% | 0.00061562 | 0 | 0.61562 | 0.11921 | 0
Commercial EM-New | Commercial EM-New-Assembly | Commercial EM-New-Assembly-ElecHt | Assembly | New | Cool | ElecHt | 5 | 0.5608% | 98.58% | 0.8634% | 16.85% | 0.84923 | 0.25096 | POST2013 | 91.18% | 18 | 100% | 9.098% | 0.00080273 | 0 | 0.80273 | 0.23722 | 0
Commercial EM-New | Commercial EM-New-Other | Commercial EM-New-Other-ElecHt | Other | New | Cool | ElecHt | 5 | 24.03% | 67.84% | 8.133% | 20.05% | 0.84923 | 0.25096 | POST2013 | 87.72% | 19 | 100% | 21.33% | 0.040921 | 0 | 40.9213 | 12.0929 | 0
Commercial EM-New | Commercial EM-New-Large Off | Commercial EM-New-Large Off-HtPmpHt | Large Off | New | Cool | HtPmpHt | 5 | 9.379% | 80.87% | 9.748% | 85% | 1.1225 | 0.25096 | POST2013 | 95.13% | 2 | 49.84% | 15.07% | 0.093007 | 0 | 93.0069 | 20.7946 | 0
Commercial EM-New | Commercial EM-New-Medium Off | Commercial EM-New-Medium Off-HtPmpHt | Medium Off | New | Cool | HtPmpHt | 5 | 5.714% | 93.11% | 1.177% | 35% | 0.77169 | 0.25096 | POST2013 | 97.67% | 3 | 39.73% | 12.01% | 0.0031799 | 0 | 3.1799 | 1.0341 | 0
Commercial EM-New | Commercial EM-New-Small Off | Commercial EM-New-Small Off-HtPmpHt | Small Off | New | Cool | HtPmpHt | 5 | 6.354% | 65.88% | 27.77% | 2.901% | 0.624 | 0.55769 | POST2013 | 91.12% | 4 | 10.43% | 3.154% | 0.0050258 | 0 | 5.0258 | 4.4917 | 0
Commercial EM-New | Commercial EM-New-Xlarge Ret | Commercial EM-New-Xlarge Ret-HtPmpHt | Xlarge Ret | New | Cool | HtPmpHt | 5 | 52.11% | 30.36% | 17.52% | 3.916% | 0.77169 | 0.25096 | POST2013 | 98.61% | 5 | 29.29% | 2.682% | 0.0052953 | 0 | 5.2953 | 1.7221 | 0
Commercial EM-New | Commercial EM-New-Large Ret | Commercial EM-New-Large Ret-HtPmpHt | Large Ret | New | Cool | HtPmpHt | 5 | 64.09% | 20.98% | 14.93% | 25.78% | 0.84923 | 0.55769 | POST2013 | 77.18% | 6 | 11.84% | 1.084% | 0.032672 | 0 | 32.672 | 21.4558 | 0
Commercial EM-New | Commercial EM-New-Medium Ret | Commercial EM-New-Medium Ret-HtPmpHt | Medium Ret | New | Cool | HtPmpHt | 5 | 56.16% | 42.42% | 1.418% | 2.757% | 1.1815 | 0.55769 | POST2013 | 90.53% | 7 | 44.66% | 4.089% | 0.00046185 | 0 | 0.46185 | 0.21799 | 0
Commercial EM-New | Commercial EM-New-Small Ret | Commercial EM-New-Small Ret-HtPmpHt | Small Ret | New | Cool | HtPmpHt | 5 | 19.95% | 44.75% | 35.3% | 10.15% | 1.2369 | 0.25096 | POST2013 | 53.67% | 8 | 14.21% | 1.302% | 0.044303 | 0 | 44.3031 | 8.9887 | 0
Commercial EM-New | Commercial EM-New-School K-12 | Commercial EM-New-School K-12-HtPmpHt | School K-12 | New | Cool | HtPmpHt | 5 | 22.29% | 53.09% | 24.62% | 29.52% | 0.57231 | 0.27885 | POST2013 | 96.13% | 9 | 58.04% | 3.089% | 0.041593 | 0 | 41.5928 | 20.2653 | 0
Commercial EM-New | Commercial EM-New-University | Commercial EM-New-University-HtPmpHt | University | New | Cool | HtPmpHt | 5 | 15.89% | 73.04% | 11.08% | 77.76% | 0.94154 | 0.27885 | POST2013 | 75% | 10 | 41.96% | 2.233% | 0.081087 | 0 | 81.0874 | 24.0149 | 0
Commercial EM-New | Commercial EM-New-Warehouse | Commercial EM-New-Warehouse-HtPmpHt | Warehouse | New | Cool | HtPmpHt | 5 | 52.11% | 30.36% | 17.52% | 13.08% | 0.20308 | 0.11154 | POST2013 | 18.16% | 11 | 100% | 10.09% | 0.004655 | 0 | 4.655 | 2.5567 | 0
Commercial EM-New | Commercial EM-New-Supermarket | Commercial EM-New-Supermarket-HtPmpHt | Supermarket | New | Cool | HtPmpHt | 5 | 1.538% | 88.46% | 10.01% | 7.145% | 1.4031 | 0.33462 | POST2013 | 92.15% | 12 | 70.77% | 0.6168% | 0.010031 | 0 | 10.031 | 2.3923 | 0
Commercial EM-New | Commercial EM-New-MiniMart | Commercial EM-New-MiniMart-HtPmpHt | MiniMart | New | Cool | HtPmpHt | 5 | 0% | 99.62% | 0.3792% | 0% | 1.8646 | 0.55769 | POST2013 | 83.87% | 13 | 29.23% | 0.2548% | 0 | 0 | 0 | 0 | 0
Commercial EM-New | Commercial EM-New-Restaurant | Commercial EM-New-Restaurant-HtPmpHt | Restaurant | New | Cool | HtPmpHt | 5 | 5.521% | 88.37% | 6.112% | 2.353% | 1.8646 | 0.55769 | POST2013 | 100% | 14 | 100% | 1.169% | 0.0026811 | 0 | 2.6811 | 0.80189 | 0
Commercial EM-New | Commercial EM-New-Lodging | Commercial EM-New-Lodging-HtPmpHt | Lodging | New | Cool | HtPmpHt | 5 | 34.34% | 53.62% | 12.04% | 7.935% | 1.2923 | 0.25096 | POST2013 | 94.44% | 15 | 100% | 2.396% | 0.012346 | 0 | 12.3465 | 2.3976 | 0
Commercial EM-New | Commercial EM-New-Hospital | Commercial EM-New-Hospital-HtPmpHt | Hospital | New | Cool | HtPmpHt | 5 | 10.31% | 74.19% | 15.5% | 85.34% | 1.6985 | 0.27885 | POST2013 | 95% | 16 | 100% | 4.497% | 0.22461 | 0 | 224.6076 | 36.8751 | 0
Commercial EM-New | Commercial EM-New-Residential Care | Commercial EM-New-Residential Care-HtPmpHt | Residential Care | New | Cool | HtPmpHt | 5 | 0.5608% | 98.58% | 0.8634% | 7.623% | 1.44 | 0.27885 | POST2013 | 84.23% | 17 | 100% | 5.828% | 0.00094779 | 0 | 0.94779 | 0.18353 | 0
Commercial EM-New | Commercial EM-New-Assembly | Commercial EM-New-Assembly-HtPmpHt | Assembly | New | Cool | HtPmpHt | 5 | 0.5608% | 98.58% | 0.8634% | 16.85% | 0.84923 | 0.25096 | POST2013 | 91.18% | 18 | 100% | 9.098% | 0.0012359 | 0 | 1.2359 | 0.36522 | 0
Commercial EM-New | Commercial EM-New-Other | Commercial EM-New-Other-HtPmpHt | Other | New | Cool | HtPmpHt | 5 | 24.03% | 67.84% | 8.133% | 20.05% | 0.84923 | 0.25096 | POST2013 | 87.72% | 19 | 100% | 21.33% | 0.013848 | 0 | 13.8485 | 4.0925 | 0

## Savings
Existing Buildings
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
[6 empty] | ElecHt | GasHt | HtPmpHt |  |  | 2
|  | HVACElecHt | HVACGasHt | HVACHtPmpHt |  | SaveElecHt | SaveGasHt | SaveHtPmpHt | ElecHtEUITYPHeat | ThermsTYPHeat | Gas Save | Cost $/sf
| BType | HVAC Electric EUI - Electric Heat | HVAC Electric EUI - Gas Heat | HVAC Electric EUI - HP Heat | Controls Savings Fraction | ElecHt Savings kWh/sf | GasHt Savings kWh/sf | Heat Pump Savings kWh/sf | Gas Heating EUI (kWh/sf) | Gas Heating therms/sf | Gas Savings Therms | Cost $/sf | Gas heat Savings Fraction |  | See 6P Savings Tab
| Large Off | 7.08 | 5.18 | 6.08 | 18.46% | 1.3071 | 0.95631 | 1.1225 | 2 | 0.27 | 0.03975 | 0.25096 | 14.72% |  | 6% | Relative savings (PECI) - Notes & Sources 2008
| Medium Off | 6.08 | 4.18 | 5.08 | 18.46% | 1.1225 | 0.77169 | 0.93785 | 2 | 0.27 | 0.03975 | 0.25096 | 14.72% |  | 32.5% | Based upon CEUS data HVAC is 32.5% of total electric EUI and 36% of gas EUI
| Small Off | 5.28 | 3.38 | 4.28 | 18.46% | 0.97477 | 0.624 | 0.79015 | 2 | 0.27 | 0.03975 | 0.55769 | 14.72% |  | 18.46% | 6P Savings
| Xlarge Ret | 6.08 | 4.18 | 5.08 | 18.46% | 1.1225 | 0.77169 | 0.93785 | 2 | 0.29 | 0.042694 | 0.25096 | 14.72%
| Large Ret | 6.7 | 4.6 | 5.6 | 18.46% | 1.2369 | 0.84923 | 1.0338 | 2.2 | 0.29 | 0.042694 | 0.55769 | 14.72% |  | 5.3% | Relative savings (PECI) - Notes & Sources 2008
| Medium Ret | 9.3 | 6.4 | 7.8 | 18.46% | 1.7169 | 1.1815 | 1.44 | 3 | 0.29 | 0.042694 | 0.55769 | 14.72% |  | 36% | Based upon CEUS data HVAC is 32.5% of total electric EUI and 36% of gas EUI (very weird).
| Small Ret | 9.6 | 6.7 | 8.1 | 18.46% | 1.7723 | 1.2369 | 1.4954 | 3 | 0.29 | 0.042694 | 0.25096 | 14.72% |  | 14.72% | 6P Savings
| School K-12 | 6 | 3.1 | 4.5 | 18.46% | 1.1077 | 0.57231 | 0.83077 | 3 | 0.29 | 0.042694 | 0.27885 | 14.72%
| University | 9 | 5.1 | 7 | 18.46% | 1.6615 | 0.94154 | 1.2923 | 4 | 0.29 | 0.042694 | 0.27885 | 14.72%
| Warehouse | 3 | 1.1 | 2 | 18.46% | 0.55385 | 0.20308 | 0.36923 | 2 | 0.17 | 0.025028 | 0.11154 | 14.72%
| Supermarket | 12.5 | 7.6 | 10 | 18.46% | 2.3077 | 1.4031 | 1.8462 | 5 | 0.5 | 0.073611 | 0.33462 | 14.72%
| MiniMart | 14 | 10.1 | 12 | 18.46% | 2.5846 | 1.8646 | 2.2154 | 4 | 0.5 | 0.073611 | 0.55769 | 14.72%
| Restaurant | 14 | 10.1 | 12 | 18.46% | 2.5846 | 1.8646 | 2.2154 | 4 | 0.5 | 0.073611 | 0.55769 | 14.72%
| Lodging | 9 | 5.1 | 7 | 18.46% | 1.6615 | 0.94154 | 1.2923 | 4 | 0.3 | 0.044167 | 0.25096 | 14.72%
| Hospital | 15 | 9.2 | 12 | 18.46% | 2.7692 | 1.6985 | 2.2154 | 6 | 0.5 | 0.073611 | 0.27885 | 14.72%
| Residential Care | 12.7 | 7.8 | 10.2 | 18.46% | 2.3446 | 1.44 | 1.8831 | 5 | 0.5 | 0.073611 | 0.27885 | 14.72%
| Assembly | 8.5 | 4.6 | 6.5 | 18.46% | 1.5692 | 0.84923 | 1.2 | 4 | 0.4 | 0.058889 | 0.25096 | 14.72%
| Other | 8.5 | 4.6 | 6.5 | 18.46% | 1.5692 | 0.84923 | 1.2 | 4 | 0.6 | 0.088333 | 0.25096 | 14.72%
Not using these for 7P. Roll new sf into retro after 4 years
New
| BType | [7 empty] | Electric Savings (kWh/sf) |  | Gas Savings Therms | Cost $/sf |  | Cost $/sf |  | 88.53% | Overall EUI reduction from 6P to 7P; apply to heating EUI's in base case.
| Large Off |  |  |  |  | 1.3071 | 0.95631 | 1.1225 | 0.95631 |  | 0.021 | 0.25096 |  | 1 | All | 100% | Originally thought of using a baseline adjustment here, but used measure saturation instead. Avoid the double-counting.
| Medium Off |  |  |  |  | 0.77169 | 0.77169 | 0.77169 | 0.77169 |  | 0.021 | 0.25096 |  | 1 | Dry Goods Retail | 79.1%
| Small Off |  |  |  |  | 0.624 | 0.624 | 0.624 | 0.624 |  | 0.021 | 0.55769 |  | 1 | Grocery | 134.4%
| Xlarge Ret |  |  |  |  | 0.77169 | 0.77169 | 0.77169 | 0.77169 |  | 0.021 | 0.25096 |  | 1 | Hotel/Motel | 82.22%
| Large Ret |  |  |  |  | 0.84923 | 0.84923 | 0.84923 | 0.84923 |  | 0.021 | 0.55769 |  | 1 | Office | 91.01%
| Medium Ret |  |  |  |  | 1.1815 | 1.1815 | 1.1815 | 1.1815 |  | 0.021 | 0.55769 |  | 1 | Other Health | 98.6%
| Small Ret |  |  |  |  | 1.2369 | 1.2369 | 1.2369 | 1.2369 |  | 0.021 | 0.25096 |  | 1 | Restaurant | 107.7%
| School K-12 |  |  |  |  | 0.57231 | 0.57231 | 0.57231 | 0.57231 |  | 0.021 | 0.27885 |  | 1 | School | 100%
| University |  |  |  |  | 0.94154 | 0.94154 | 0.94154 | 0.94154 |  | 0.021 | 0.27885 |  | 1 | Warehouse | 64.34%
| Warehouse |  |  |  |  | 0.20308 | 0.20308 | 0.20308 | 0.20308 |  | 0.021 | 0.11154 |  | 0.25 | Other | 106.8%
| Supermarket |  |  |  |  | 1.4031 | 1.4031 | 1.4031 | 1.4031 |  | 0.021 | 0.33462 |  | 1
| MiniMart |  |  |  |  | 1.8646 | 1.8646 | 1.8646 | 1.8646 |  | 0.021 | 0.55769 |  | 1
| Restaurant |  |  |  |  | 1.8646 | 1.8646 | 1.8646 | 1.8646 |  | 0.021 | 0.55769 |  | 1
| Lodging |  |  |  |  | 1.6615 | 0.94154 | 1.2923 | 0.94154 |  | 0.021 | 0.25096 |  | 1
| Hospital |  |  |  |  | 1.6985 | 1.6985 | 1.6985 | 1.6985 |  | 0.021 | 0.27885 |  | 1
| Residential Care |  |  |  |  | 1.44 | 1.44 | 1.44 | 1.44 |  | 0.021 | 0.27885 |  | 1
| Assembly |  |  |  |  | 0.84923 | 0.84923 | 0.84923 | 0.84923 |  | 0.021 | 0.25096 |  | 1
| Other |  |  |  |  | 0.84923 | 0.84923 | 0.84923 | 0.84923 |  | 0.021 | 0.25096 |  | 1
0.021
Note on J29: MDK: currently new and existing eui are the same data so savings taken directly for existing above.
Note on L29: MDK: See savings discussion on Notes & Sources 2008. currently new and existing eui are the same data so savings taken directly for existing above.

## Cost
Cost Data
[10 empty] | Sources | Median | Average | ($/kWh)
6P cost Data | [9 empty] | 6P | 0.44 | 0.52
| Savings - kWh/sf | [7 empty] | See Savings Tab | SEM | 0.06 | 0.05
| Elect EUI | Gas EUI | HP Eui | $/sf | $/kWh |  |  |  | Revised Cost | California |  | 0.29
| 1.3071 | 0.95631 | 1.1225 | 0.45 | 0.34428 | 0.47056 | 0.4009 |  | 0.25096 | LBL |  | 0.41
| 1.1225 | 0.77169 | 0.93785 | 0.45 | 0.4009 | 0.58313 | 0.47982 |  | 0.25096
| 0.97477 | 0.624 | 0.79015 | 1 | 1.0259 | 1.6026 | 1.2656 |  | 0.55769
| 1.1225 | 0.77169 | 0.93785 | 0.45 | 0.4009 | 0.58313 | 0.47982 |  | 0.25096 |  | New/Old Cost ratio | 55.77%
| 1.2369 | 0.84923 | 1.0338 | 1 | 0.80846 | 1.1775 | 0.96726 |  | 0.55769
| 1.7169 | 1.1815 | 1.44 | 1 | 0.58244 | 0.84635 | 0.69444 |  | 0.55769
| 1.7723 | 1.2369 | 1.4954 | 0.45 | 0.25391 | 0.36381 | 0.30093 |  | 0.25096
| 1.1077 | 0.57231 | 0.83077 | 0.5 | 0.45139 | 0.87366 | 0.60185 |  | 0.27885
| 1.6615 | 0.94154 | 1.2923 | 0.5 | 0.30093 | 0.53105 | 0.3869 |  | 0.27885
| 0.55385 | 0.20308 | 0.36923 | 0.2 | 0.36111 | 0.98485 | 0.54167 |  | 0.11154
| 2.3077 | 1.4031 | 1.8462 | 0.6 | 0.26 | 0.42763 | 0.325 |  | 0.33462
| 2.5846 | 1.8646 | 2.2154 | 1 | 0.3869 | 0.5363 | 0.45139 |  | 0.55769
| 2.5846 | 1.8646 | 2.2154 | 1 | 0.3869 | 0.5363 | 0.45139 |  | 0.55769
| 1.6615 | 0.94154 | 1.2923 | 0.45 | 0.27083 | 0.47794 | 0.34821 |  | 0.25096
| 2.7692 | 1.6985 | 2.2154 | 0.5 | 0.18056 | 0.29438 | 0.22569 |  | 0.27885
| 2.3446 | 1.44 | 1.8831 | 0.5 | 0.21325 | 0.34722 | 0.26552 |  | 0.27885
| 1.5692 | 0.84923 | 1.2 | 0.45 | 0.28676 | 0.52989 | 0.375 |  | 0.25096
| 1.5692 | 0.84923 | 1.2 | 0.45 | 0.28676 | 0.52989 | 0.375 |  | 0.25096
|  |  |  | 0.5 |  |  |  | 0.51546
SEM Program Data (from Energy Trust) |  |  |  | 0.60833 |  |  |  | 0.43951
Data
Project ID | Sum of Electric Energy (kWh) | Sum of Gas Energy (thm) | Sum of Electric Incentive | Sum of Gas Incentive | First-Year Cost
1 | 689582 | 77646 | 41448.02 | 38483.29 | 0.060106
2 | 2542543 | 52540 | 72435.22 | 24551.82 | 0.028489
3 | 708922 | 23996 | 33674.35 | 17113.46 | 0.047501
4 | 681289 | 0 | 68007.65 | 513.83 | 0.099822
5 | 2135966 | 58902 | 77838.32 | 18642.61 | 0.036442
6 | 796239 | 0 | 50051.58 | 0 | 0.06286
7 | 666284 | 33376 | 38815.54 | 17961.9 | 0.058257
8 | 204234 | 14580 | 17770.19 | 19061.49 | 0.087009
9 | 235734 | 0 | 31491.58 | 0 | 0.13359
10 | 2207190 | 10511 | 40130.7 | 2102.2 | 0.018182
11 | 2589157 | 39507 | 125638.07 | 26049.9 | 0.048525
12 | 1168917 | 13007 | 78208.62 | 8692.8 | 0.066907
13 | 496473 | 41448 | 43929.62 | 30741.77 | 0.088483
14 | 158824 | 51929 | 13821.65 | 94648.29 | 0.087025
15 | 238091 | 82051 | 27102.68 | 31262.44 | 0.11383
16 | 273169 | 118 | 19280.17 | 5356.83 | 0.07058
Grand Total | 15792614 | 499611 | 779643.96 | 335182.63 | 0.049368
0.064883
California Retro Commissioning Fact Sheet
How much does retro-commissioning cost?
The cost of a retro-commissioning process is often difficult to estimate. The scope of work, the size and age of the building, and the complexity of the building systems are some factors that can affect the project costs. Table 1 shows average costs in a national study of retro-commissioning projects. The data is approximately three years old and includes 14 California projects. A project is underway to update the study with recent data and we expect the California costs to be in the range of $0.50/sq ft. Costs may vary depending on market conditions.
Table 1: Actual RCx costs, as reported in a study of 106 projects2
Description | Value or Ranges | Min | Max | Average
Total RCx Cost | $0.13 to $0.45/sqft | 0.13 | 0.45 | 0.29
Provider Fee as % of Total RCx Cost | 35 - 71%
Average RCx Cost Allocation
Planning and Investigation | 69%
Implementation | 27%
Verification, Tracking and Reporting | 4%
Simple Payback Time | 0.2 to 2.1 years
Note on N11: Kevin Smit: SEM and newer data seem to show much lower costs. Using the ratio of the average California retro CX cost to the average 6P Cx cost. This ratio will be used to adjust the 6P cost data. Need better, more current cost data.

## Market Data
From CBSA
Site_ID | (All)
Fan_Ctr | (All)
DistSys | (All)
Equip_Type | (All)
Sum of Heat_Frac_Sf_PNW_Heated | Column Labels | [15 empty] | Use this for the Com-EM measure
Row Labels | Baseboard/Zonal w/ Minimal Fan | DOAS/ERV | MAU/Swamp | MZ Air/Dual Duct | MZ Air/Single Duct | MZ MZ Sys | Radiant | SZ Ducted | SZ Unducted w/Fan | Unknown | VVT | Grand Total |  | Built up Total | Share of total | SZ Ducted | All Systems EXCEPT SZ Ducted
Assembly | 22971944.552 | 110296.3226 | 1609022.1432 |  | 46828389.0953 | 1939668.3953 | 3353745.3063 | 255153180.0937 | 10647216.6166 | 8729987.7035 | 8322.6732 | 351351772.9018 |  | 48878353.8133 | 13.91% | 72.62% | 27.38%
Grocery | 810727.2913 |  | 4082000.653 |  |  |  | 111367.5052 | 56843601.825 | 9487574.9054 | 307150.5718 |  | 71642422.7518 |  | 0 | 0% | 79.34% | 20.66%
Lodging | 13879312.8083 | 1839209.8812 | 2481450.963 |  | 4710251.9136 | 2579402.8017 | 2970958.6303 | 50545012.0401 | 80248763.1069 | 1114460.3856 |  | 160368822.5308 |  | 9128864.5966 | 5.692% | 31.52% | 68.48%
Office | 21238526.6711 | 4054634.8374 | 2716222.9632 | 21643220.5315 | 138999592.434 |  | 4496283.939 | 401438366.2434 | 27714804.7756 | 23409578.1158 |  | 645711230.5108 |  | 164697447.8029 | 25.51% | 62.17% | 37.83%
Other | 9183281.1046 |  | 3462429.3938 |  | 42979952.565 | 4127993.2605 | 15402687.5021 | 151837504.6621 | 48877202.3722 | 5936919.2702 |  | 281807970.1306 |  | 47107945.8255 | 16.72% | 53.88% | 46.12%
Residential Care | 16644374.2855 |  | 1326200.3739 |  | 3376953.3324 |  | 2310781.1781 | 56863387.2892 | 34224603.0977 | 4377423.0245 |  | 119123722.5813 |  | 3376953.3324 | 2.835% | 47.73% | 52.27%
Restaurant | 86725.7573 |  | 1142611.3328 |  |  |  |  | 45721618.8059 | 1617263.8577 |  |  | 48568219.7538 |  | 0 | 0% | 94.14% | 5.861%
Retail/Service | 7327146.6901 |  | 2369059.3651 |  | 3427772.9848 | 6421010.8571 | 10938155.9832 | 386316240.999 | 85786869.0141 | 14634957.7319 |  | 517221213.6254 |  | 9848783.8419 | 1.904% | 74.69% | 25.31%
School K-12 | 18295150.3977 | 12265167.8751 | 636451.6013 |  | 21508206.1077 | 17721004.3445 | 1828679.2082 | 131215315.1752 | 18327903.2251 | 18916928.7271 |  | 240714806.6619 |  | 51494378.3273 | 21.39% | 54.51% | 45.49%
Warehouse | 974433.402 |  | 19638934.0753 |  |  |  | 23392071.3262 | 65114466.8189 | 89419148.7987 | 7289595.478 |  | 205828649.8992 |  | 0 | 0% | 31.64% | 68.36%
Grand Total | 111411622.96 | 18269308.9164 | 39464382.8647 | 21643220.5315 | 261831118.4329 | 32789079.6591 | 64804730.5786 | 1601048693.9526 | 406351349.77 | 84717001.0084 | 8322.6732 | 2642338831.3474 |  | 0 | 0% | 60.59% | 39.41%
Site_ID | (All)
Fan_Ctr | (All)
DistSys | (All)
Equip_Type | (All)
Sum of Heat_Frac_Sf_PNW_Heated | Column Labels
Row Labels | DOAS/ERV | MZ Air/Dual Duct | MZ Air/Single Duct | MZ MZ Sys | Grand Total
Assembly | 110296.3226 |  | 46828389.0953 | 1939668.3953 | 48878353.8133
Lodging | 1839209.8812 |  | 4710251.9136 | 2579402.8017 | 9128864.5966
Office | 4054634.8374 | 21643220.5315 | 138999592.434 |  | 164697447.8029
Other |  |  | 42979952.565 | 4127993.2605 | 47107945.8255
Residential Care |  |  | 3376953.3324 |  | 3376953.3324
Retail/Service |  |  | 3427772.9848 | 6421010.8571 | 9848783.8419
School K-12 | 12265167.8751 |  | 21508206.1077 | 17721004.3445 | 51494378.3273
Grand Total | 18269308.9164 | 21643220.5315 | 261831118.4329 | 32789079.6591 | 334532727.5399
Assembly | 13.91% | 27.38% | Assumes Only Multizone Systems
Grocery | 0% | 20.66%
Lodging | 5.692% | 68.48%
Office | 25.51% | 37.83%
Other | 16.72% | 46.12%
Residential Care | 2.835% | 52.27%
Restaurant | 0% | 5.861%
Retail/Service | 1.904% | 25.31%
School K-12 | 21.39% | 45.49%
Warehouse | 0% | 68.36% |  |  | These Shares were moved into Com_master
Built-up share - for Com_Master -CHAR
Assembly | 13.91% |  | 27.38% |  | Could EXPAND THIS BY RETAIL AND OFFICE SIZES
Grocery | 0% |  | 20.66% |  | See Com_Master_7P
Hospital | 53% | From 6P | 53%
Lodging | 5.692% |  | 68.48%
Office | 25.51% |  | 37.83%
Other | 16.72% |  | 46.12%
Residential Care | 2.835% |  | 52.27%
Restaurant | 0% |  | 5.861%
Retail/Service | 1.904% |  | 25.31%
School K-12 | 21.39% |  | 45.49%
University | 72% | From 6P | 72%
Warehouse | 0% |  | 68.36%
Achievements Since 6th Plan.
Sector and End Use | 2010 | 2011 | 2012 | 2013 | 2014 | 2015
HVAC Controls | 11.2481 | 13.4996 | 14.7802 | 12.8142 | 13.0855 | 13.0855 | 52.3421
78.5132
[6 empty] | 6P Achievalble | 130
[6 empty] | 6P Technical | 152.9412
[6 empty] | Share of 6P potential achieved | 40.26%
[6 empty] | Share of 6P potential achieved | 51.34%
Site_ID | (All)
Fan_Ctr | (All)
DistSys | (All)
Equip_Type | (All)
Sum of Heat_Frac_Sf_PNW_Heated |  | Column Labels
Row Labels | Size_Group | Baseboard/Zonal w/ Minimal Fan | DOAS/ERV | MAU/Swamp | MZ Air/Dual Duct | MZ Air/Single Duct | MZ MZ Sys | Radiant | SZ Ducted | SZ Unducted w/Fan | Unknown | VVT | Grand Total
Assembly |  | 22971944.552 | 110296.3226 | 1609022.1432 |  | 46828389.0953 | 1939668.3953 | 3353745.3063 | 255153180.0937 | 10647216.6166 | 8729987.7035 | 8322.6732 | 351351772.9018
MiniMart | <5,001 |  |  | 0 |  |  |  |  | 9149727.9779 | 1060534.9147 |  |  | 10210262.8926
Supermarket | 5,001-20,000 | 810727.2913 |  | 896075.4109 |  |  |  | 111367.5052 | 11274900.5418 | 3340903.3052 | 307150.5718 |  | 16741124.6262
Supermarket | 20,001-50,000 |  |  | 2758491.2437 |  |  |  |  | 19156078.1831 | 4201325.6912 |  |  | 26115895.1181
Supermarket | 50,001-100,000 |  |  | 427433.9985 |  |  |  |  | 17262895.1222 | 884810.9943 |  |  | 18575140.1149
Lodging |  | 13879312.8083 | 1839209.8812 | 2481450.963 |  | 4710251.9136 | 2579402.8017 | 2970958.6303 | 50545012.0401 | 80248763.1069 | 1114460.3856 |  | 160368822.5308
Small Off | <5,001 | 3975987.6053 |  | 0 |  | 2768901.5594 |  | 1847806.5173 | 82803511.5767 | 4062104.2682 |  |  | 95458311.5269
Medium off | 5,001-20,000 | 7978933.8309 | 3774530.5711 |  |  | 2940094.0663 |  |  | 152685296.7702 | 3627752.9032 | 3822848.12 |  | 174829456.2617
Medium off | 20,001-50,000 | 994647.3586 | 0 | 2532830.1517 |  | 12016976.0647 |  | 2229342.136 | 95946354.5473 | 4650266.649 | 2718361.744 |  | 121088778.6513
Large Off | 50,001-100,000 | 8261247.6782 |  | 0 | 11602618.0403 | 17933298.8351 |  |  | 37210149.2752 | 9927847.3332 | 7998554.8115 |  | 92933715.9736
Large Off | 100,001+ | 27710.1981 | 280104.2663 | 183392.8115 | 10040602.4913 | 103340321.9084 |  | 419135.2857 | 32793054.0739 | 5446833.6219 | 8869813.4403 |  | 161400968.0973
Other |  | 9183281.1046 |  | 3462429.3938 |  | 42979952.565 | 4127993.2605 | 15402687.5021 | 151837504.6621 | 48877202.3722 | 5936919.2702 |  | 281807970.1306
Residential Care |  | 16644374.2855 |  | 1326200.3739 |  | 3376953.3324 |  | 2310781.1781 | 56863387.2892 | 34224603.0977 | 4377423.0245 |  | 119123722.5813
Restaurant |  | 86725.7573 |  | 1142611.3328 |  |  |  |  | 45721618.8059 | 1617263.8577 |  |  | 48568219.7538
Small Ret | <5,001 | 5926391.6462 |  | 0 |  |  |  | 2281713.0951 | 23556098.0089 | 15976597.4262 | 5391022.1178 |  | 53131822.2942
Medium ret | 5,001-20,000 | 633940.6109 | [6 empty] | 116593250.1718 | 28646683.4961 | 1119956.6546 |  | 146993830.9334
Medium ret | 20,001-50,000 | 766814.4331 |  | 1935913.9817 |  |  |  | 5611595.7707 | 110232929.8136 | 32922313.3791 | 5320880.8804 |  | 156790448.2585
Large Ret | 50,001-100,000 | [5 empty] | 6421010.8571 | 495463.7985 | 21292717.933 | 1323256.7135 | 1605252.7143 |  | 31137702.0163
xlarge ret | 100,001+ |  |  | 433145.3834 |  | 3427772.9848 |  | 2549383.319 | 114641245.0717 | 6918017.9992 | 1197845.3648 |  | 129167410.123
School K-12 |  | 18295150.3977 | 12265167.8751 | 636451.6013 |  | 21508206.1077 | 17721004.3445 | 1828679.2082 | 131215315.1752 | 18327903.2251 | 18916928.7271 |  | 240714806.6619
Warehouse |  | 974433.402 |  | 19638934.0753 |  |  |  | 23392071.3262 | 65114466.8189 | 89419148.7987 | 7289595.478 |  | 205828649.8992
Grand Total |  | 111411622.96 | 18269308.9164 | 39464382.8647 | 21643220.5315 | 261831118.4329 | 32789079.6591 | 64804730.5786 | 1601048693.9526 | 406351349.77 | 84717001.0084 | 8322.6732 | 2642338831.3474
These data to Com_Master_7P
|  | Baseboard/Zonal w/ Minimal Fan | DOAS/ERV | MAU/Swamp | MZ Air/Dual Duct | MZ Air/Single Duct | MZ MZ Sys | Radiant | SZ Ducted | SZ Unducted w/Fan | Unknown | VVT |  | Built-Up | Share of Heated SF | From 6P |  | Difference
Large Off |  | 8288957.8763 | 280104.2663 | 183392.8115 | 21643220.5315 | 121273620.7435 | 0 | 419135.2857 | 70003203.3491 | 15374680.9551 | 16868368.2518 | 0 | 254334684.0709 | 160248706.6046 | 63.01% | 92.25% |  | 29.24%
Medium Off |  | 8973581.1895 | 3774530.5711 | 2532830.1517 | 0 | 14957070.1311 | 0 | 2229342.136 | 248631651.3176 | 8278019.5522 | 6541209.864 | 0 | 295918234.913 | 27805640.7179 | 9.396% | 38.37% |  | 28.97%
Small Off |  | 3975987.6053 | 0 | 0 | 0 | 2768901.5594 | 0 | 1847806.5173 | 82803511.5767 | 4062104.2682 | 0 | 0 | 95458311.5269 | 2768901.5594 | 2.901% | 8.57% |  | 5.669%
XLarge Ret |  | 0 | 0 | 433145.3834 | 0 | 3427772.9848 | 0 | 2549383.319 | 114641245.0717 | 6918017.9992 | 1197845.3648 | 0 | 129167410.123 | 5058763.7331 | 3.916% | 4.532% |  | 0.6151%
Large Ret |  | 0 | 0 | 0 | 0 | 0 | 6421010.8571 | 495463.7985 | 21292717.933 | 1323256.7135 | 1605252.7143 | 0 | 31137702.0163 | 8026263.5713 | 25.78% | 7.475% |  | -18.3%
Medium Ret |  | 1400755.044 | 0 | 1935913.9817 | 0 | 0 | 0 | 5611595.7707 | 226826179.9854 | 61568996.8751 | 6440837.535 | 0 | 303784279.1919 | 8376751.5167 | 2.757% | 2.908% |  | 0.1501%
Small Ret |  | 5926391.6462 | 0 | 0 | 0 | 0 | 0 | 2281713.0951 | 23556098.0089 | 15976597.4262 | 5391022.1178 | 0 | 53131822.2942 | 5391022.1178 | 10.15% | 40.04% |  | 29.9%
School K-12 |  | 18295150.3977 | 12265167.8751 | 636451.6013 | 0 | 21508206.1077 | 17721004.3445 | 1828679.2082 | 131215315.1752 | 18327903.2251 | 18916928.7271 | 0 | 240714806.6619 | 71047758.6557 | 29.52% | 75.73% |  | 46.21%
University |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.76% | 77.76% | Use 6P value | 0%
Warehouse |  | 974433.402 | 0 | 19638934.0753 | 0 | 0 | 0 | 23392071.3262 | 65114466.8189 | 89419148.7987 | 7289595.478 | 0 | 205828649.8992 | 26928529.5534 | 13.08% | 7.223% |  | -5.86%
Supermarket |  | 810727.2913 | 0 | 4082000.653 | 0 | 0 | 0 | 111367.5052 | 47693873.8471 | 8427039.9907 | 307150.5718 | 0 | 61432159.8592 | 4389151.2249 | 7.145% | 10.42% |  | 3.271%
MiniMart |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9149727.9779 | 1060534.9147 | 0 | 0 | 10210262.8926 | 0 | 0% | 4.911% |  | 4.911%
Restaurant |  | 86725.7573 | 0 | 1142611.3328 | 0 | 0 | 0 | 0 | 45721618.8059 | 1617263.8577 | 0 | 0 | 48568219.7538 | 1142611.3328 | 2.353% | 6.127% |  | 3.775%
Lodging |  | 13879312.8083 | 1839209.8812 | 2481450.963 | 0 | 4710251.9136 | 2579402.8017 | 2970958.6303 | 50545012.0401 | 80248763.1069 | 1114460.3856 | 0 | 160368822.5308 | 12724775.9452 | 7.935% | 45.41% |  | 37.47%
Hospital |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.34% | 85.34% | Use 6P value | 0%
Residential Care |  | 16644374.2855 | 0 | 1326200.3739 | 0 | 3376953.3324 | 0 | 2310781.1781 | 56863387.2892 | 34224603.0977 | 4377423.0245 | 0 | 119123722.5813 | 9080576.7308 | 7.623% | 51.17% |  | 43.55%
Assembly |  | 22971944.552 | 110296.3226 | 1609022.1432 | 0 | 46828389.0953 | 1939668.3953 | 3353745.3063 | 255153180.0937 | 10647216.6166 | 8729987.7035 | 8322.6732 | 351351772.9018 | 59217363.66 | 16.85% | 30% |  | 13.15%
Other |  | 9183281.1046 | 0 | 3462429.3938 | 0 | 42979952.565 | 4127993.2605 | 15402687.5021 | 151837504.6621 | 48877202.3722 | 5936919.2702 | 0 | 281807970.1306 | 56507294.4895 | 20.05% | 35.65% |  | 15.6%
Total |  | 111411622.96 | 18269308.9164 | 39464382.8647 | 21643220.5315 | 261831118.4329 | 32789079.6591 | 64804730.5786 | 1601048693.9526 | 406351349.77 | 84717001.0084 | 8322.6732 | 2642338831.3474 | 458714111.413 | 17.36% |  |  | -17.36%

## 6P Applic
COHORT | (All)
Sum of WGT2 | bld_typ | [12 empty] | hvac_cd
PRI_HVAC | 1 DGR | 10 UNI | 11 OTH | 12 VAC | 2 GRO | 3 OFF | 4 RES | 5 WAR | 6 HOS | 7 OHE | 8 HTM | 9 SCH | Grand Total | 11 | BOILER/CHILLER | Summaries from NEEA 2005 New Construction Baseline | [15 empty] | NEEA 2005 New Construction Characteristics
11 | 8.717% | 50.35% | 12.44% | 0% | 0.6835% | 22.66% | 0% | 0% | 0% | 23.73% | 33.43% | 10.43% | 13.2% | 12 | DUCT HT/CHILLER
12 | 0.681% | 7.805% | 0.4327% | 0% | 6.534% | 9.148% | 0% | 2.49% | 0% | 4.532% | 0% | 3.379% | 3.36% | 13 | H2O LOOP HT PUMP | ACTIVITY TYPE |  | Office |  |  | Retail |  |  |  | School |  | Warehouse | Grocery |  | Restaurant | Lodging | Health |  | Assembly | Other
13 | 4.134% | 0% | 1.11% | 0% | 0% | 7.813% | 0% | 0% | 0% | 2.609% | 0% | 6.381% | 3.576% | 14 | BOILER ONLY | Pre2002 | FloorA%ACT
14 | 0.8404% | 14.02% | 7.755% | 0% | 0% | 4.751% | 0% | 0.6754% | 0% | 3.95% | 9.108% | 53.55% | 9.861% | 15 | CHILLER ONLY | BLDGTYPE | 0 | Large Off | Medium Off | Small Off | Big Box | Small Box | High End | Anchor | K-12 | University | Warehouse | Supermarket | MIniMart | Restaurant | Lodging | Hospital | OtherHealth | Assembly | Other | Total
21 | 46.89% | 0.7845% | 22.18% | 67.75% | 58.9% | 27.53% | 61.23% | 25.04% | 57.72% | 48.1% | 7.601% | 16.55% | 30.55% | 21 | PKG:HEAT/DX COOL | Simple%ACT |  | 48.29 |  |  | 96.33 | 94.2 |  |  | 22.35 | 28.06 | 89.69 | 88.44 |  | 100 | 67.62 | 2.68 | 22.18 |  | 52.87 | 61.61
22 | 2.781% | 21.95% | 7.899% | 0% | 1.156% | 12.17% | 0% | 1.236% | 24% | 4.701% | 0% | 2.337% | 5.548% | 22 | DUCT HT/DX COOL | Complex%ACT |  | 51.71 |  |  | 3.67 | 5.8 |  |  | 77.65 | 71.94 | 10.31 | 11.56 |  | 0 | 32.38 | 97.32 | 77.82 | 30 | 47.13 | 38.39
23 | 5.099% | 5.084% | 6.482% | 0% | 10.3% | 9.612% | 14.41% | 3.843% | 3.759% | 5.067% | 19.84% | 3.325% | 7.044% | 23 | AIR-AIR HT PUMP | MZVAV%ACT |  | 31.22 |  |  | 1.82 | 0.1 |  |  | 22.44 | 40.95 | 0.39 | 0.54 |  | 0 | 0.82 | 48.45 | 38.6 |  | 28.43 | 15.89
24 | 7.593% | 0% | 14.42% | 0% | 5.193% | 1.058% | 2.799% | 5.415% | 0% | 0% | 5.592% | 1.524% | 5.855% | 24 | PKG HEAT ONLY | VavElec%ACT |  | 87.09 |  |  | 70.34 | 0 |  |  | 2.1 | 31.48 | 100 | 100 |  | 0 | 29.96 | 13.43 | 64.52 |  | 49.19 | 41.81
25 | 0.6337% | 0% | 0% | 0% | 0.9004% | 1.253% | 0% | 0% | 0% | 0.1843% | 0% | 0% | 0.4346% | 25 | DX COOL ONLY | VavGas%ACT |  | 12.91 |  |  | 29.66 | 100 |  |  | 97.9 | 68.52 | 0 | 0 |  | 0 | 70.04 | 86.56 | 35.48 |  | 50.81 | 58.19
26 | 0% | 0% | 0% | 0% | 0.1587% | 0% | 2.233% | 0% | 0% | 0% | 0% | 0% | 0.04348% | 26 | EVAP COOL ONLY | SimpElec%ACT |  | 3.06 |  |  | 2.53 | 2.47 |  |  | 2.41 | 18.96 | 10.13 | 1.03 |  | 0 | 37.49 | 18.15 | 0.57 | 10 | 8.34 | 8.4
27 | 0.4262% | 0% | 0.3177% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.1446% | 27 | PKG:HT/EVAP CL | SimpGas%ACT |  | 61.61 |  |  | 87.83 | 80.07 |  |  | 61.24 | 70.62 | 81.47 | 95.04 |  | 92.12 | 32.41 | 4.6 | 97.98 | 75 | 72.88 | 76.05
28 | 0% | 0% | 0% | 0% | 7.017% | 0% | 2.224% | 0% | 0% | 0% | 0% | 0% | 0.3092% | 28 | HT REC/DX COOL | SimpHP%ACT |  | 29.1 |  |  | 0.78 | 14.27 |  |  | 4.62 | 7.42 | 3.81 | 0.25 |  | 7.88 | 24.66 | 3.54 | 0 | 10 | 6.32 | 7.87
31 | 0% | 0% | 2.384% | 31.76% | 0% | 0% | 0% | 1.103% | 0% | 5.178% | 24.13% | 0% | 2.17% | 29 | HT REC ONLY | SimpOther%ACT |  | 6.23 |  |  | 8.86 | 3.19 |  |  | 31.73 | 3 | 4.59 | 3.68 |  | 0 | 5.45 | 73.7 | 1.45 | 5 | 12.45 | 7.68
33 | 21.08% | 0% | 22.12% | 0.491% | 9.166% | 2.038% | 16.95% | 46.52% | 0% | 1.946% | 0.3012% | 2.244% | 15.15% | 31 | UNIT HEAT/AC | CompElec%ACT |  | 61.68 |  |  | 84.28 | 3.79 |  |  | 0.61 | 17.94 | 37.84 | 5.34 |  |  | 0.77 | 8.11 | 35.41 | 5 | 31.14 | 21.16
34 | 0% | 0% | 0% | 0% | 0% | 0% | 0.148% | 0% | 0% | 0% | 0% | 0% | 0.002475% | 32 | COMBO HT/AC UNIT | CompGas%ACT |  | 12.29 |  |  | 15.72 | 31.93 |  |  | 82.72 | 62.77 | 62.16 | 94.66 |  |  | 56.86 | 88.87 | 24.46 | 50 | 49.88 | 58.21
41 | 0.2576% | 0% | 1.152% | 0% | 0% | 1.967% | 0% | 0% | 14.52% | 0% | 0% | 0.2835% | 0.7825% | 33 | UNIT HT ONLY | CompHP%ACT |  | 13.01 |  |  | 0 | 64.28 |  |  | 16.05 | 0 | 0 | 0 |  |  | 42.38 | 0 | 7.27 | 40 | 1.42 | 10.28
42 | 0% | 0% | 0.6462% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.1279% | 34 | UNIT CL ONLY | CompOther%ACT |  | 13.03 |  |  | 0 | 0 |  |  | 0.61 | 19.3 | 0 | 0 |  |  | 0 | 3.02 | 32.87 | 5 | 17.55 | 10.35
61 | 0.8649% | 0% | 0.6605% | 0% | 0% | 0% | 0% | 13.67% | 0% | 0% | 0% | 0% | 1.846% | 41 | BOILER/DX COOL
Grand Total | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 42 | BOILER/UNIT AC
[14 empty] | 47 | PKG HT/UNIT COOL
Built-Up | 17.41% | 94.13% | 30.79% | 0% | 15.39% | 58.51% | 2.224% | 4.401% | 38.52% | 39.53% | 42.54% | 76.35% | 36.64% | 51 | AIR HTPMP/BOILER
ComplexElecHt | 31.75% | 31.61% | 28.86% | #DIV/0! | 49.96% | 43.12% | 0% | 84.66% | 62.31% | 26.66% | 0% | 11.66% | 29.2% | 61 | NO HVAC | CompElec%TYP |  | 31.89% | 31.89% | 31.89% | 3.093% | 0.2198% | 0.2198% | 0.2198% | 0.4737% | 12.91% | 3.901% | 0.6173% | 0.6173% | 0% | 0.2493% | 7.893% | 27.56% | 1.5% | 14.68%
ComplexGas | 27.09% | 62.99% | 48.29% | #DIV/0! | -16.87% | 33.78% | -547.9% | -71.97% | 27.94% | 57.22% | 53.36% | 79.8% | 46.7%
Complex HtPmp | 41.15% | 5.4% | 22.85% | #DIV/0! | 66.9% | 23.1% | 647.9% | 87.31% | 9.756% | 16.12% | 46.64% | 8.533% | 24.11%
[16 empty] | CompHP%TYP |  | 6.727% | 6.727% | 6.727% | 0% | 3.728% | 3.728% | 3.728% | 12.46% | 0% | 0% | 0% | 0% | 0% | 13.72% | 0% | 5.658% | 12% | 0.6692%
[16 empty] | CompGas%TYP |  | 13.09% | 13.09% | 13.09% | 0.5769% | 1.852% | 1.852% | 1.852% | 64.23% | 45.16% | 6.409% | 10.94% | 10.94% | 0% | 18.41% | 89.43% | 44.61% | 16.5% | 31.78%
COHORT | 1987 or earlier | [14 empty] | CompOther%TYP |  | 6.738% | 6.738% | 6.738% | 0% | 0% | 0% | 0% | 0.4737% | 13.88% | 0% | 0% | 0% | 0% | 0% | 2.939% | 25.58% | 1.5% | 8.271%
Sum of WGT2 | bld_typ
PRI_HVAC | 1 DGR | 10 UNI | 11 OTH | 12 VAC | 2 GRO | 3 OFF | 4 RES | 5 WAR | 6 HOS | 7 OHE | 8 HTM | 9 SCH | Grand Total |  |  | ElecHtComplex%TYP |  | 61.68% | 61.68% | 61.68% | 84.28% | 3.79% | 3.79% | 3.79% | 0.61% | 17.94% | 37.84% | 5.34% | 5.34% | 5.34% | 0.77% | 8.11% | 35.41% | 5% | 31.14%
11 | 11.73% | 0% | 3.343% | 0% | 0% | 26.71% | 0% | 0% | 0% | 19.61% | 36.14% | 6.412% | 13% |  |  | GasHtComplex%TYP |  | 25.32% | 25.32% | 25.32% | 15.72% | 31.93% | 31.93% | 31.93% | 83.33% | 82.07% | 62.16% | 94.66% | 94.66% | 94.66% | 56.86% | 91.89% | 57.33% | 55% | 67.43%
12 | 0% | 0% | 0% | 0% | 0% | 10.54% | 0% | 0% | 0% | 8.428% | 0% | 4.832% | 3.4% |  |  | HtPmpHtComplex%TYP |  | 13.01% | 13.01% | 13.01% | 0% | 64.28% | 64.28% | 64.28% | 16.05% | 0% | 0% | 0% | 0% | 0% | 42.38% | 0% | 7.27% | 40% | 1.42%
13 | 5.565% | 0% | 2.049% | 0% | 0% | 8.916% | 0% | 0% | 0% | 0% | 0% | 0% | 3.63% |  |  | ElecHtSimple%TYP |  | 3.06% | 3.06% | 3.06% | 2.53% | 2.47% | 2.47% | 2.47% | 2.41% | 18.96% | 10.13% | 1.03% | 1.03% | 1.03% | 37.49% | 18.15% | 0.57% | 10% | 8.34%
14 | 1.131% | 0% | 13.18% | 0% | 0% | 6.611% | 0% | 0% | 0% | 0% | 11.97% | 65.71% | 13.05% |  |  | GasHtSimple%TYP |  | 67.84% | 67.84% | 67.84% | 96.69% | 83.26% | 83.26% | 83.26% | 92.97% | 73.62% | 86.06% | 98.72% | 98.72% | 98.72% | 37.86% | 78.3% | 99.43% | 80% | 85.33%
21 | 37.89% | 100% | 17.27% | 67.04% | 57.65% | 25.31% | 54.64% | 19.08% | 100% | 50.18% | 6.341% | 19.81% | 27.45% |  |  | HtPmpHtSimple%TYP |  | 29.1% | 29.1% | 29.1% | 0.78% | 14.27% | 14.27% | 14.27% | 4.62% | 7.42% | 3.81% | 0.25% | 0.25% | 0.25% | 24.66% | 3.54% | 0% | 10% | 6.32%
22 | 0% | 0% | 9.516% | 0% | 0% | 4.68% | 0% | 0% | 0% | 0% | 0% | 0% | 2.655%
23 | 6.654% | 0% | 7.597% | 0% | 14.76% | 12.09% | 17.03% | 4.559% | 0% | 8.534% | 18.49% | 1.791% | 8.417% |  |  | BuiltUp%TYP |  | 51.71% | 51.71% | 51.71% | 3.67% | 5.8% | 5.8% | 5.8% | 77.65% | 71.94% | 10.31% | 11.56% | 11.56% | 11.56% | 32.38% | 97.32% | 77.82% | 30% | 47.13%
24 | 10.04% | 0% | 23.39% | 0% | 4.053% | 1.362% | 3.09% | 7.792% | 0% | 0% | 7.349% | 0% | 7.734% |  |  | SimpleHVAC%TYP |  | 48.29% | 48.29% | 48.29% | 96.33% | 94.2% | 94.2% | 94.2% | 22.35% | 28.06% | 89.69% | 88.44% | 88.44% | 100% | 67.62% | 2.68% | 22.18% | 0% | 52.87%
25 | 0% | 0% | 0% | 0% | 1.639% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.05356%
26 | 0% | 0% | 0% | 0% | 0% | 0% | 1.113% | 0% | 0% | 0% | 0% | 0% | 0.02269%
28 | 0% | 0% | 0% | 0% | 9.917% | 0% | 2.798% | 0% | 0% | 0% | 0% | 0% | 0.3811%
31 | 0% | 0% | 2.854% | 32.96% | 0% | 0% | 0% | 1.976% | 0% | 9.629% | 19.31% | 0% | 2.363%
33 | 25.82% | 0% | 19.58% | 0% | 11.98% | 2.602% | 21.33% | 43.44% | 0% | 3.619% | 0.3958% | 1.454% | 14.86%
41 | 0% | 0% | 0% | 0% | 0% | 1.176% | 0% | 0% | 0% | 0% | 0% | 0% | 0.2739%
61 | 1.164% | 0% | 1.219% | 0% | 0% | 0% | 0% | 23.15% | 0% | 0% | 0% | 0% | 2.702%
Grand Total | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Built-Up | 18.43% | 0% | 28.09% | 0% | 9.917% | 58.63% | 2.798% | 0% | 0% | 28.04% | 48.11% | 76.95% | 36.39%
COHORT | 1988-1994
Sum of WGT2 | bld_typ
PRI_HVAC | 1 DGR | 10 UNI | 11 OTH | 12 VAC | 2 GRO | 3 OFF | 4 RES | 5 WAR | 7 OHE | 8 HTM | 9 SCH | Grand Total
11 | 0% | 0% | 20.4% | 0% | 3.635% | 21.66% | 0% | 0% | 28.43% | 39.69% | 3.165% | 11.81%
12 | 6.582% | 0% | 0% | 0% | 34.75% | 10.14% | 0% | 16.5% | 0% | 0% | 0% | 7.03%
13 | 0% | 0% | 0% | 0% | 0% | 0.9743% | 0% | 0% | 6.506% | 0% | 31.64% | 4.838%
14 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 24% | 0% | 21.69% | 4.462%
21 | 70.84% | 0% | 19.34% | 86.53% | 35.4% | 42.89% | 68.43% | 29.4% | 37.04% | 0% | 11.88% | 33.75%
22 | 3.804% | 100% | 14.07% | 0% | 0% | 7.147% | 0% | 8.186% | 0% | 0% | 0% | 6.702%
23 | 1.5% | 0% | 3.733% | 0% | 5.225% | 8.568% | 10.17% | 0% | 2.903% | 10.14% | 12.43% | 5.05%
24 | 1.274% | 0% | 8.818% | 0% | 15.78% | 1.132% | 3.995% | 7.062% | 0% | 0% | 8.965% | 5.632%
25 | 6.125% | 0% | 0% | 0% | 0% | 4.854% | 0% | 0% | 1.12% | 0% | 0% | 1.808%
26 | 0% | 0% | 0% | 0% | 0.844% | 0% | 15.68% | 0% | 0% | 0% | 0% | 0.2368%
27 | 0% | 0% | 0.6491% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.1507%
31 | 0% | 0% | 5.897% | 0% | 0% | 0% | 0% | 0% | 0% | 50.17% | 0% | 3.063%
33 | 7.383% | 0% | 21.87% | 13.47% | 4.372% | 1.207% | 0% | 38.86% | 0% | 0% | 8.166% | 13.34%
34 | 0% | 0% | 0% | 0% | 0% | 0% | 1.721% | 0% | 0% | 0% | 0% | 0.02042%
41 | 2.49% | 0% | 5.223% | 0% | 0% | 1.433% | 0% | 0% | 0% | 0% | 2.065% | 2.116%
Grand Total | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Built-Up | 12.88% | 100% | 39.69% | 0% | 38.38% | 41.35% | 0% | 24.69% | 58.94% | 39.69% | 58.56% | 36.95%
COHORT | 1995-2001
Sum of WGT2 | bld_typ
PRI_HVAC | 1 DGR | 10 UNI | 11 OTH | 2 GRO | 3 OFF | 4 RES | 5 WAR | 6 HOS | 7 OHE | 8 HTM | 9 SCH | Grand Total
11 | 0% | 65.17% | 24.45% | 0% | 9.381% | 0% | 0% | 0% | 28.59% | 16.87% | 33.71% | 14.52%
12 | 0% | 10.1% | 1.368% | 0% | 4.049% | 0% | 0% | 0% | 0% | 0% | 0% | 1.288%
13 | 0% | 0% | 0% | 0% | 6.873% | 0% | 0% | 0% | 5.167% | 0% | 12.46% | 2.748%
14 | 0% | 18.15% | 1.954% | 0% | 0.4031% | 0% | 2.322% | 0% | 0% | 0% | 28.29% | 3.58%
21 | 74.31% | 0% | 31.86% | 78.33% | 28.76% | 100% | 34.21% | 0% | 50.45% | 17.8% | 6.566% | 37.73%
22 | 15.54% | 0% | 2.353% | 4.402% | 39.54% | 0% | 0% | 56.77% | 15.79% | 0% | 14.3% | 13.23%
23 | 0% | 6.579% | 5.807% | 4.595% | 1.652% | 0% | 4.464% | 8.889% | 0% | 31.58% | 2.236% | 4.167%
24 | 0% | 0% | 1.556% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.792% | 0.5825%
25 | 0% | 0% | 0% | 0% | 4.019% | 0% | 0% | 0% | 0% | 0% | 0% | 0.7951%
27 | 2.774% | 0% | 0.713% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.5562%
28 | 0% | 0% | 0% | 5.976% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.2679%
31 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 33.76% | 0% | 1.142%
33 | 7.375% | 0% | 26.6% | 6.701% | 0.4698% | 0% | 56.42% | 0% | 0% | 0% | 0.6496% | 16.92%
41 | 0% | 0% | 1.296% | 0% | 4.856% | 0% | 0% | 34.34% | 0% | 0% | 0% | 1.531%
42 | 0% | 0% | 2.043% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.5629%
61 | 0% | 0% | 0% | 0% | 0% | 0% | 2.582% | 0% | 0% | 0% | 0% | 0.3749%
Grand Total | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Built-Up | 15.54% | 93.42% | 30.13% | 4.402% | 60.25% | 0% | 4.904% | 56.77% | 49.55% | 50.63% | 88.76% | 36.89% | 0%
COHORT | (All) | [5 empty] | COHORT | (All)
Sum of WGT2 | sizegroup | [5 empty] | Sum of WGT2 | sizegroup
PRI_HVAC | 1 DGR-1: Big Box Retail | 1 DGR-2: Anchor Retail | 1 DGR-3: Small Box | 1 DGR-4: Boutique | Grand Total |  | PRI_HVAC | 3 OFF-1: Large | 3 OFF-2: Med | 3 OFF-3: Small | Grand Total
11 | 0% | 28.68% | 0% | 0% | 8.717% |  | 11 | 47.74% | 4.917% | 0.3499% | 22.66%
12 | 3.152% | 0.5804% | 0% | 0% | 0.681% |  | 12 | 18.72% | 2.995% | 0% | 9.148%
13 | 0% | 13.6% | 0% | 0% | 4.134% |  | 13 | 9.457% | 11.67% | 1.175% | 7.813%
14 | 0% | 0.6641% | 5.332% | 0% | 0.8404% |  | 14 | 3.649% | 8% | 3.185% | 4.751%
21 | 85.8% | 29.22% | 55.53% | 42.35% | 46.89% |  | 21 | 3.209% | 40.01% | 54.02% | 27.53%
22 | 1.24% | 6.884% | 2.461% | 0.4688% | 2.781% |  | 22 | 15.33% | 17.36% | 1.734% | 12.17%
23 | 0% | 0% | 12.58% | 8.63% | 5.099% |  | 23 | 0% | 6.359% | 28.52% | 9.612%
24 | 0% | 0% | 6.271% | 16.44% | 7.593% |  | 24 | 0% | 0% | 3.859% | 1.058%
25 | 1.771% | 0.9652% | 0% | 0.1366% | 0.6337% |  | 25 | 1.894% | 1.463% | 0% | 1.253%
27 | 2.662% | 0% | 0% | 0% | 0.4262% |  | 33 | 0% | 4.384% | 2.916% | 2.038%
33 | 5.377% | 18.55% | 17.82% | 29.9% | 21.08% |  | 41 | 0% | 2.842% | 4.247% | 1.967%
41 | 0% | 0.8476% | 0% | 0% | 0.2576% |  | Grand Total | 100% | 100% | 100% | 100%
61 | 0% | 0% | 0% | 2.078% | 0.8649%
Grand Total | 100% | 100% | 100% | 100% | 100% |  | Built-Up | 94.9% | 47.78% | 10.69% | 58.51% | 0%
Built-Up | 4.392% | 51.26% | 7.793% | 0.4688% | 17.41%
[7 empty] | COHORT | 1987 or earlier
[7 empty] | Sum of WGT2 | sizegroup
[7 empty] | PRI_HVAC | 3 OFF-1: Large | 3 OFF-2: Med | 3 OFF-3: Small | Grand Total
[7 empty] | 11 | 54.57% | 2.61% | 0.4849% | 26.71%
[7 empty] | 12 | 22.17% | 0% | 0% | 10.54%
[7 empty] | 13 | 10.32% | 16.4% | 0% | 8.916%
[7 empty] | 14 | 4.823% | 13.09% | 3.988% | 6.611%
[7 empty] | 21 | 2.076% | 44% | 48.41% | 25.31%
[7 empty] | 22 | 6.038% | 7.402% | 0% | 4.68%
[7 empty] | 23 | 0% | 9.913% | 34.51% | 12.09%
[7 empty] | 24 | 0% | 0% | 4.86% | 1.362%
[7 empty] | 33 | 0% | 6.577% | 3.545% | 2.602%
[7 empty] | 41 | 0% | 0% | 4.197% | 1.176%
[7 empty] | Grand Total | 100% | 100% | 100% | 100%
[7 empty] | Built-Up | 97.92% | 39.51% | 8.67% | 58.63%
[7 empty] | COHORT | 1988-1994
[7 empty] | Sum of WGT2 | sizegroup
[7 empty] | PRI_HVAC | 3 OFF-1: Large | 3 OFF-2: Med | 3 OFF-3: Small | Grand Total
[7 empty] | 11 | 40.18% | 19.87% | 0% | 21.66%
[7 empty] | 12 | 27.74% | 0% | 0% | 10.14%
[7 empty] | 13 | 0% | 2.776% | 0% | 0.9743%
[7 empty] | 21 | 16% | 49.53% | 69.31% | 42.89%
[7 empty] | 22 | 16.07% | 3.629% | 0% | 7.147%
[7 empty] | 23 | 0% | 2.835% | 26.7% | 8.568%
[7 empty] | 24 | 0% | 0% | 3.992% | 1.132%
[7 empty] | 25 | 0% | 13.83% | 0% | 4.854%
[7 empty] | 33 | 0% | 3.439% | 0% | 1.207%
[7 empty] | 41 | 0% | 4.083% | 0% | 1.433%
[7 empty] | Grand Total | 100% | 100% | 100% | 100%
[7 empty] | Built-Up | 84% | 30.36% | 0% | 41.35%
[7 empty] | COHORT | 1995-2001
[7 empty] | Sum of WGT2 | sizegroup
[7 empty] | PRI_HVAC | 3 OFF-1: Large | 3 OFF-2: Med | 3 OFF-3: Small | Grand Total
[7 empty] | 11 | 21.02% | 4.305% | 0% | 9.381%
[7 empty] | 12 | 0% | 10.59% | 0% | 4.049%
[7 empty] | 13 | 9.526% | 4.778% | 6.175% | 6.873%
[7 empty] | 14 | 0% | 0% | 1.615% | 0.4031%
[7 empty] | 21 | 2.979% | 27.82% | 68.19% | 28.76%
[7 empty] | 22 | 55.55% | 43.99% | 9.111% | 39.54%
[7 empty] | 23 | 0% | 0% | 6.618% | 1.652%
[7 empty] | 25 | 10.92% | 0% | 0% | 4.019%
[7 empty] | 33 | 0% | 0% | 1.882% | 0.4698%
[7 empty] | 41 | 0% | 8.516% | 6.406% | 4.856%
[7 empty] | Grand Total | 100% | 100% | 100% | 100%
[7 empty] | Built-Up | 86.1% | 72.18% | 23.31% | 65.1%
Take these values to CHAR

## 6P Savings
Existing
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
2
|  | HVACElecHt | HVACGasHt | HVACHtPmpHt |  | SaveElecHt | SaveGasHt | SaveHtPmpHt | ElecHtEUITYPHeat | ThermsTYPHeat | Gas Save | Cost $/sf
| BType | HVAC Electric EUI - Electric Heat | HVAC Electric EUI - Gas Heat | HVAC Electric EUI - HP Heat | Controls Savings Fraction | ElecHt Savings kWh/sf | GasHt Savings kWh/sf | Heat Pump Savings kWh/sf | Gas Heating EUI (kWh/sf) | Gas Heating therms/sf | Gas Savings Therms | Cost $/sf | Gas heat Savings Fraction
| Large Off | 7.08 | 5.18 | 6.08 | 18.46% | 1.3071 | 0.95631 | 1.1225 | 2 | 0.27 | 0.03975 | 0.45 | 14.72%
15.9836 | Medium Off | 6.08 | 4.18 | 5.08 | 18.46% | 1.1225 | 0.77169 | 0.93785 | 2 | 0.27 | 0.03975 | 0.45 | 14.72% | 1.1252 | 18.51%
| Small Off | 5.28 | 3.38 | 4.28 | 18.46% | 0.97477 | 0.624 | 0.79015 | 2 | 0.27 | 0.03975 | 1 | 14.72%
| Big Box | 6.08 | 4.18 | 5.08 | 18.46% | 1.1225 | 0.77169 | 0.93785 | 2 | 0.29 | 0.042694 | 0.45 | 14.72%
| Small Box | 6.7 | 4.6 | 5.6 | 18.46% | 1.2369 | 0.84923 | 1.0338 | 2.2 | 0.29 | 0.042694 | 1 | 14.72% | 0.89848 | 13.41%
| High End | 9.3 | 6.4 | 7.8 | 18.46% | 1.7169 | 1.1815 | 1.44 | 3 | 0.29 | 0.042694 | 1 | 14.72%
| Anchor | 9.6 | 6.7 | 8.1 | 18.46% | 1.7723 | 1.2369 | 1.4954 | 3 | 0.29 | 0.042694 | 0.45 | 14.72%
| K-12 | 6 | 3.1 | 4.5 | 18.46% | 1.1077 | 0.57231 | 0.83077 | 3 | 0.29 | 0.042694 | 0.5 | 14.72% | 0.6745 | 11.24%
| University | 9 | 5.1 | 7 | 18.46% | 1.6615 | 0.94154 | 1.2923 | 4 | 0.29 | 0.042694 | 0.5 | 14.72% | [5 empty] | Electric Savings |  | Gas Savings |  | Thermal Savings |  | Cost
| Warehouse | 3 | 1.1 | 2 | 18.46% | 0.55385 | 0.20308 | 0.36923 | 2 | 0.17 | 0.025028 | 0.2 | 14.72% | 0.42589 | 14.2% | Study | Cons | Cases | kWh/sf Savings | Elec % | kBtu/sf | Gas % | kBtu/sf | Termal % | Total Cost | Average Building Size | Number type | items | Caveats
| Supermarket | 12.5 | 7.6 | 10 | 18.46% | 2.3077 | 1.4031 | 1.8462 | 5 | 0.5 | 0.073611 | 0.6 | 14.72% | 4.0108 | 32.09% | NEEA | New | 13 | 0.87 |  | 3.3 |  |  |  | 1.11 | 107,000sf | Simple Average
| MIniMart | 14 | 10.1 | 12 | 18.46% | 2.5846 | 1.8646 | 2.2154 | 4 | 0.5 | 0.073611 | 1 | 14.72% | 4.0108 | 28.65% | NEEA | New | 13 | 0.92 |  | 2.4 |  |  |  | 0.73 |  | Area weighted
| Restaurant | 14 | 10.1 | 12 | 18.46% | 2.5846 | 1.8646 | 2.2154 | 4 | 0.5 | 0.073611 | 1 | 14.72% | 3.2239 | 23.03% | LBL | New | 69 | 1.2 |  | 2.1 |  |  |  | 1.64 | 118,000SF | Means, Simple Average | hvac, lighting
| Lodging | 9 | 5.1 | 7 | 18.46% | 1.6615 | 0.94154 | 1.2923 | 4 | 0.3 | 0.044167 | 0.45 | 14.72% | 1.006 | 11.18% | LBL | New | 69 | 0.5 |  | 2.2 |  |  |  | 1 | 69500SF | Median, Simple Average
| Hospital | 15 | 9.2 | 12 | 18.46% | 2.7692 | 1.6985 | 2.2154 | 6 | 0.5 | 0.073611 | 0.5 | 14.72% |  |  | NEEA | Existing | 8 | 2.16 | 18 | 10.6 | 25 |  |  | 1.02 | 99600SF | Simple Average
| OtherHealth | 12.7 | 7.8 | 10.2 | 18.46% | 2.3446 | 1.44 | 1.8831 | 5 | 0.5 | 0.073611 | 0.5 | 14.72% | 1.0738 | 8.455% | NEEA | Existing | 8 | 1.26 | 17 | 6.13 | 27 |  |  | 0.6 |  | Area weighted
| Assembly | 8.5 | 4.6 | 6.5 | 18.46% | 1.5692 | 0.84923 | 1.2 | 4 | 0.4 | 0.058889 | 0.45 | 14.72% | 0.89103 | 10.48% | LBL | Existing | 109 | 2.2 | 11 | 15.6 | 13 | 94 | 37 | 0.41 | 210,000SF | Means, Simple Average | hvac, lighting
| Other | 8.5 | 4.6 | 6.5 | 18.46% | 1.5692 | 0.84923 | 1.2 | 4 | 0.6 | 0.088333 | 0.45 | 14.72% | 0.90728 | 10.67% | LBL | Existing | 109 | 1.7 | 9 | 6.5 | 6 | 64 | 36 | 0.27 | 151,000SF | Median, Simple Average
[16 empty] | PECI | Existing | 52 | 0.942 | 6 | 3.1 | 4.6 |  |  | 0.445 | 353,000SF | Area Weighted | hvac, lighting makes up 0.047kWh/sf of savings | Buildings over 100000sf, with EUIs>15kWh, and with DDC.
New
| BType | [7 empty] | Electric Savings (kWh/sf) |  | Gas Savings Therms | Cost $/sf
| Large Off |  |  |  |  | 1.3071 | 0.95631 | 1.1225 | 0.95631 |  | 0.021 | 1
| Medium Off |  |  |  |  | 0.77169 | 0.77169 | 0.77169 | 0.77169 |  | 0.021 | 1
| Small Off |  |  |  |  | 0.624 | 0.624 | 0.624 | 0.624 |  | 0.021 | 1 |  |  |  | Codes. |  |  |  |  | Completion Requirements
| Big Box |  |  |  |  | 0.77169 | 0.77169 | 0.77169 | 0.77169 |  | 0.021 | 1 |  |  |  |  | State | Code | Section | TAB | HVAC | Lighting
| Small Box |  |  |  |  | 0.84923 | 0.84923 | 0.84923 | 0.84923 |  | 0.021 | 1 |  |  |  |  | Idaho | IECC 2006 | 503.2.9 | No | Terminals and coils must have "means for balancing". Manuals must be provided with equipment details, manuals and design intent. | None
| High End |  |  |  |  | 1.1815 | 1.1815 | 1.1815 | 1.1815 |  | 0.021 | 1 |  |  |  |  | Montana | IECC 2006 | 503.2.9 | No | Terminals and coils must have "means for balancing". Manuals must be provided with equipment details, manuals and design intent. | None
| Anchor |  |  |  |  | 1.2369 | 1.2369 | 1.2369 | 1.2369 |  | 0.021 | 1 |  |  |  |  | Oregon | OR 2007 | ----- | No | None | None
| K-12 |  |  |  |  | 0.57231 | 0.57231 | 0.57231 | 0.57231 |  | 0.021 | 1 |  |  |  |  | Washington | WA 2006 | 1416 | Yes | 2 full pages requiring complete commissioning of all systems in all buildings. Doesn't necessarily require deficiencies to be repaired.. | -----
| University |  |  |  |  | 0.94154 | 0.94154 | 0.94154 | 0.94154 |  | 0.021 | 1 |  |  |  |  | Washington | WA 2006 | 1513.7 | no | ----- | All automatic shut-off controls and systems ( OS, time switches, daylight) shall be tested to determine devices and systems are operating correctly. A complete report of tests and results shall be prepared and filed with the owner.
| Warehouse |  |  |  |  | 0.20308 | 0.20308 | 0.20308 | 0.20308 |  | 0.021 | 0.25
| Supermarket |  |  |  |  | 1.4031 | 1.4031 | 1.4031 | 1.4031 |  | 0.021 | 1
| MIniMart |  |  |  |  | 1.8646 | 1.8646 | 1.8646 | 1.8646 |  | 0.021 | 1
| Restaurant |  |  |  |  | 1.8646 | 1.8646 | 1.8646 | 1.8646 |  | 0.021 | 1
| Lodging |  |  |  |  | 1.6615 | 0.94154 | 1.2923 | 0.94154 |  | 0.021 | 1
| Hospital |  |  |  |  | 1.6985 | 1.6985 | 1.6985 | 1.6985 |  | 0.021 | 1
| OtherHealth |  |  |  |  | 1.44 | 1.44 | 1.44 | 1.44 |  | 0.021 | 1
| Assembly |  |  |  |  | 0.84923 | 0.84923 | 0.84923 | 0.84923 |  | 0.021 | 1
| Other |  |  |  |  | 0.84923 | 0.84923 | 0.84923 | 0.84923 |  | 0.021 | 1
0.021
| building_type | elec.eui.n.mean | 7.04%
| Assembly | 12.6567 | 0.89103
| Food Service | 45.7942 | 3.2239
| Grocery | 56.9718 | 4.0108
| Lodging | 14.29 | 1.006
| Office | 15.9836 | 1.1252
| Residential Care | 15.2525 | 1.0738
| Retail | 12.7625 | 0.89848
| School | 9.5809 | 0.6745
| Warehouse | 6.0495 | 0.42589
| Other | 12.8875 | 0.90728
| All | 14.1571 | 0.99666
[6 empty] | $/sf | $/kWh
|  |  | 7.08 | 5.18 | 6.08 | 0.45 | 0.063559 | 0.086873 | 0.074013
|  |  | 6.08 | 4.18 | 5.08 | 0.45 | 0.074013 | 0.10766 | 0.088583
|  |  | 5.28 | 3.38 | 4.28 | 1 | 0.18939 | 0.29586 | 0.23364
|  |  | 6.08 | 4.18 | 5.08 | 0.45 | 0.074013 | 0.10766 | 0.088583
|  |  | 6.7 | 4.6 | 5.6 | 1 | 0.14925 | 0.21739 | 0.17857
|  |  | 9.3 | 6.4 | 7.8 | 1 | 0.10753 | 0.15625 | 0.12821
|  |  | 9.6 | 6.7 | 8.1 | 0.45 | 0.046875 | 0.067164 | 0.055556
|  |  | 6 | 3.1 | 4.5 | 0.5 | 0.083333 | 0.16129 | 0.11111
|  |  | 9 | 5.1 | 7 | 0.5 | 0.055556 | 0.098039 | 0.071429
|  |  | 3 | 1.1 | 2 | 0.2 | 0.066667 | 0.18182 | 0.1
|  |  | 12.5 | 7.6 | 10 | 0.6 | 0.048 | 0.078947 | 0.06
|  |  | 14 | 10.1 | 12 | 1 | 0.071429 | 0.09901 | 0.083333
|  |  | 14 | 10.1 | 12 | 1 | 0.071429 | 0.09901 | 0.083333
|  |  | 9 | 5.1 | 7 | 0.45 | 0.05 | 0.088235 | 0.064286
|  |  | 15 | 9.2 | 12 | 0.5 | 0.033333 | 0.054348 | 0.041667
|  |  | 12.7 | 7.8 | 10.2 | 0.5 | 0.03937 | 0.064103 | 0.04902
|  |  | 8.5 | 4.6 | 6.5 | 0.45 | 0.052941 | 0.097826 | 0.069231
|  |  | 8.5 | 4.6 | 6.5 | 0.45 | 0.052941 | 0.097826 | 0.069231
0.095162
Note on M7: Mike Kennedy: Costs kept at 5th plan levels except minimum set at $0.45/sf per PECI. This is for complex system commissioning so building with simple system are not counted so categories such at small office, minimart, small box, restaurant don't count for much after the complex system fraction is applied.
Note on N7: Charlie Grist: Mike Kennedy, new for 2008 based on review of gas savings from PECI and LBL. These savings are lower than those assumed in the 5th Plan.
Note on S20: Mike Kennedy: each metric in this row has a different N which makes interpretation difficult.
Note on T20: Mike Kennedy: 29 cases
Note on T21: Mike Kennedy: 29 cases
Note on U24: Mike Kennedy: 46 cases
Note on U25: Mike Kennedy: 46 cases
Note on Z26: Mike Kennedy: Talked with commissioning department of Glumac and they indicated they were not participating any longer due to the low reimbursment. No matter the size of the building. The "investigation" phase does not cover itself in their opinion. If a bunch of measures are found and have to be implemented then it can work out. They also indicated most people were going after a second credit of $0.05/sf to do an energy star rating of the building too. This is info they need for the process.
Note on J30: MDK: currently new and existing eui are the same data so savings taken directly for existing above.
Note on L30: MDK: See savings discussion on Notes & Sources 2008. currently new and existing eui are the same data so savings taken directly for existing above.
Note on D56: Kevin Smit: Commercial SEM savings from ETO = 7.04%, primarily in office buildings
Goal is to capture HVAC commissioning savings and keep lighting savings separated. Data quality, savings methodology, and representativeness of early commissioning projects to the general building population are all major concerns that severely limit the quality of any answers.
The Sixth Plan savings were based primarily on the findings in the PECI study relative savings (6%). Gas savings were based on the average of the LBL/PECI savings, or 5.3%, will be used. These are relative to whole building EUI. Based upon CEUS data HVAC is 32.5% of total electric EUI and 36% of gas. This factor is used to adjust the relative percents here and the resulting number is applied to the HVAC energy estimate.NEEA and LBL show lower savings for New construction. Interestingly, the
New: NEEA and LBL new construction savings are similar to the PECI existing building savings. My suspicion is this may be significant. For electric savings the existing building relative savings of 7.5% is used. Gas savings are dramatically lower in new construction and savings are assumed to be 2.1kBtu/sf.

## To Do 7P
Item | Description | Completion | Notes
1 | Review Savings inputs- SAVE tab. Find source of 6P savings, develop new ones | done | Next time probably need to develop new savings estimates. New modeling?
2 | Revise CHAR matrix with CBSA for baseline EUI | done
3 | Consider expanding breadth of measure. How does SEM fit into this? | done | Compare with SEM, but don't change measure
4 | Measure lives | done
5 | Figure out which systems in CBSA are considered Build-up systems, then add to CHAR | done | Everything but SZ ducted systems
6 | Revise CHAR matriX for gas EUI from CBSA | done
7 | Check 6 going on 7 | done
8 | Need new cost data |  | Couldn't find great cost data, but reduced 6P estimates based on SEM and other data
9 | Apply ramp rates | done
10 | New load shapes | done

## Measure Life
Source
Measure life in the 6p: | 7 | years | Unclear; compliation of numerous studies from around the country
Measure life in the 7p: | 5 | years | Professional judgement. Input from reviewers including Eric Boyer (BPA)

## Achievment
From 6 going on 7 data
|  | 2010 | 2011 | 2012 | 2013
| HVAC Controls | 11.2481 | 13.4996 | 14.7802 | 12.8142 | 52.3421
Council Taxonomy
|  | Achieved aMW (Busbar) |  |  |  | Forecast aMW (Busbar) |  |  |  | Total Achieved aMW (Busbar) | Total Forecast aMW (Busbar)
| Sector and End Use | 2010 | 2011 | 2012 | 2013 | 2010 | 2011 | 2012 | 2013
Agricultural
| Irrigation Scheduling | 5.6271 | 8.179 | 4.9635 | 5.6918 | 1.5606 | 1.5606 | 1.5606 | 1.5606 | 24.4614 | 6.2423
| Irrigation Hardware | 2.5725 | 3.4234 | 3.1083 | 2.86 | 7.0586 | 7.0586 | 7.0586 | 7.0586 | 11.9642 | 28.2343
| Dairy | 1.3614 | 2.0159 | 0.023364 | 0.086721 | 0.85769 | 0.85769 | 0.85769 | 0.85769 | 3.4874 | 3.4308
| unknown | 0.74706 | 0.44233 | 1.1221 | 0.26316 | 0 | 0 | 0 | 0 | 2.5746 | 0
Commercial
| Lighting | 41.099 | 43.6783 | 37.5038 | 37.4342 | 10.225 | 15.6649 | 19.9232 | 23.3046 | 159.7154 | 69.1177
| HVAC Controls | 11.2481 | 13.4996 | 14.7802 | 12.8142 | 6.4265 | 6.4763 | 6.5584 | 6.5891 | 52.3421 | 26.0502 | This says we have achieved twice what we estimated
| unknown | 7.7652 | 11.7104 | 13.091 | 6.1251 | 0 | 0 | 0 | 0 | 38.6917 | 0 | Much of this mis-categorized.
| PC Network/Supply | 8.5744 | 9.4801 | 9.2203 | 10.0961 | 3.4696 | 4.3308 | 5.3086 | 6.3495 | 37.3708 | 19.4585
| Refrigeration | 12.0493 | 10.1954 | 4.5303 | 5.2386 | 5.6365 | 5.5837 | 5.5412 | 5.4986 | 32.0137 | 22.2599
| Rooftop Units | 6.037 | 6.7423 | 4.1212 | 5.6245 | 1.8608 | 2.2737 | 2.7021 | 3.1182 | 22.5251 | 9.9548
BPA Taxonomy
| savingsYear | BPA Sector | BPA EndUse | BPA Category | BPA TAP | SumOfkWhBusbar | SumOfaMWBusbar
| 2010 | Commercial | HVAC | HVAC System Controls | Energy Management Systems/System Controls | 4356166.127 | 0.49728
| 2010 | Commercial | HVAC | HVAC System Controls | HVAC Control Improvements (non-VFD) | 22998774.733 | 2.6254
| 2010 | Commercial | HVAC | HVAC System Controls | Thermostats | 92368.607 | 0.010544
| 2010 | Commercial | HVAC | HVAC System Controls | Unknown | 15752876.923 | 1.7983
| 2011 | Commercial | HVAC | HVAC System Controls | Energy Management Systems/System Controls | 16417870.469 | 1.8742
| 2011 | Commercial | HVAC | HVAC System Controls | HVAC Control Improvements (non-VFD) | 29354751.9385 | 3.351
| 2011 | Commercial | HVAC | HVAC System Controls | HVAC Control Improvements (VFD) | 3011.85 | 0.00034382
| 2011 | Commercial | HVAC | HVAC System Controls | Thermostats | 117584.379 | 0.013423
| 2011 | Commercial | HVAC | HVAC System Controls | Unknown | 17992768.4451 | 2.054
| 2012 | Commercial | HVAC | HVAC System Controls | Energy Management Systems/System Controls | 4585544.71 | 0.52346
| 2012 | Commercial | HVAC | HVAC System Controls | HVAC Control Improvements (non-VFD) | 46944217.796 | 5.3589
| 2012 | Commercial | HVAC | HVAC System Controls | HVAC Control Improvements (VFD) | 134639.7 | 0.01537
| 2012 | Commercial | HVAC | HVAC System Controls | Thermostats | 133904.72 | 0.015286
| 2012 | Commercial | HVAC | HVAC System Controls | Unknown | 31996184.7242 | 3.6525
| 2013 | Commercial | HVAC | HVAC System Controls | Energy Management Systems/System Controls | 17036088.5898 | 1.9448
| 2013 | Commercial | HVAC | HVAC System Controls | HVAC Control Improvements (non-VFD) | 9269348.863 | 1.0581
| 2013 | Commercial | HVAC | HVAC System Controls | HVAC Control Improvements (VFD) | 4375119.0931 | 0.49944
| 2013 | Commercial | HVAC | HVAC System Controls | Pneumatic to DDC Control Improvements | 4843835.16 | 0.55295
| 2013 | Commercial | HVAC | HVAC System Controls | Thermostats | 1309283.5036 | 0.14946
[7 empty] | 25.9948 | This says we have achieved everything
[5 empty] | Energy Management Systems/System Controls |  | 4.8397 | 18.58% | Saturation to Com_Master