## 7PSourceSummary
Measure: | VRF
Item | Methods & Sources | 7P Updates
Measures Described | VRF systems, either heat-pump or heat-recovery models, provide heating and air-conditioning, with: Inverter driven outdoor-unit compressors and condenser fans, providing improved part-load and low-ambient performance; Multiple indoor-units with multi-speed fans, electronic expansion valves and integrated thermostats; Refrigerant piping network for heat transfer; Integrated control system; and Ventilation provided by VRF system, natural ventilation or a dedicated outside air system (DOAS). | Sources of information can be found on the VRF subcommittee web page (of the RTF)
Energy Savings Calculation Basis | Much of the savings is from improved ventilation and reduction of losses. The equipment efficiency is not signficantly better that baseline equipment. | Studies show a wide range of possible savings estmiates. See Savings and Cost tab for the summary of savings values chosen for this analysis. Savings range from 3.8 to 5.4 kWh/sf which are based on installed and metered results. These are relatively high level estimates at this point.
Applicable Stock | Best applications are in new construction and major remodels, where the system is being replaced. For retrofit, the best applications are small to medium sized buildings where there are a variety of indepent systems. In 2010, the primary applications were Offices (46%), Lodging (25%), School (15%), and 14% other (109 installations). Need to make sure there is no overlap with Fan savings measures | See Applicability matrix tab.
Baseline Saturation | Not huge, but some units are being installed. Assume the 3% per national average
Baseline | Modeled baseline is a VAV system with wither gas boiler or electric resistance (ASHRAE system types 5 or 6)
Permutations | Primarily New Construction. Used very low applicability values for retrofit (only for major retrofit situations)
Costs | $2.00 to $4.00 per sf, per multiple studies. Some experts indicate the incremental cost could be zero for VRF. Assume a 15% premium for retrofit costs .
Measure Life | 20 years
Savings Shape | C-All-HVAC-Vent-All-All-E - using a ventilation load shape since most of the savings are from ventilation | Future improvement would be to break out savings by heating, cooling, and ventilation. Need better data for this.
Achievability Ramp Rate | LO1Slow - Slowest ramp rate since this is a new measure. Retro3Slow - some retrofits are already happening | Some experts say this could take of more quickly since it is technologically mature (Europe and Asia)
File Version Updates
v5 | Added the High/Low Forecast. Slighting increased retrofit applicability
Changed Retrofit ramp to Retro3Slow

## forRPM
Ramp Rate | Resource Type | Measure Category | Sector | End Use | kW per unit | kWh per unit | TRC Net Levelized Cost (Net of All Benefits) | segment | measure | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | MAX | Savings Allocation by Category and Month for Segments 1 | [12 empty] | Savings Allocation by Category and Month for Segments 2
[5 empty] | Wholesale KW | Busbar Savings | lvlcost |  |  | aMW_2016 | aMW_2017 | aMW_2018 | aMW_2019 | aMW_2020 | aMW_2021 | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | MAX | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
LO1Slow | New | VRF | Commercial | HVAC | 0.00065676 | 3.4937 | 69.0059 | Large Off | VRF-NEW-Large Off | 0.00033254 | 0.00076004 | 0.0016431 | 0.003617 | 0.0059645 | 0.0077915 | 0.014955 | 0.018742 | 0.025023 | 0.037276 | 0.047489 | 0.063801 | 0.083092 | 0.087318 | 0.10598 | 0.1126 | 0.11718 | 0.11406 | 0.11506 | 0.12193 | 1.0846 | 0.21907 | 0.19698 | 0.22667 | 0.21088 | 0.21529 | 0.21311 | 0.20246 | 0.21096 | 0.1971 | 0.22473 | 0.19888 | 0.21652 |  | 0.093008 | 0.07991 | 0.076651 | 0.080036 | 0.078526 | 0.068904 | 0.080903 | 0.066348 | 0.081682 | 0.073363 | 0.088021 | 0.093648
LO1Slow | New | VRF | Commercial | HVAC | 0.00039672 | 2.1104 | 69.6785 | Medium Off | VRF-NEW-Medium Off | 0.0026063 | 0.0057096 | 0.012658 | 0.028184 | 0.045921 | 0.056711 | 0.11725 | 0.14672 | 0.1918 | 0.29237 | 0.37124 | 0.48774 | 0.6241 | 0.67433 | 0.83283 | 0.85632 | 0.93585 | 0.85153 | 0.86792 | 0.94925 | 8.3511 | 0.13233 | 0.11899 | 0.13692 | 0.12738 | 0.13005 | 0.12873 | 0.1223 | 0.12743 | 0.11906 | 0.13575 | 0.12013 | 0.13079 |  | 0.056182 | 0.04827 | 0.046301 | 0.048346 | 0.047434 | 0.041622 | 0.048869 | 0.040078 | 0.04934 | 0.044315 | 0.053169 | 0.056568
LO1Slow | New | VRF | Commercial | HVAC | 0.00058664 | 3.1207 | 35.2743 | Small Off | VRF-NEW-Small Off | 0.0010119 | 0.002222 | 0.0049608 | 0.010941 | 0.017975 | 0.022089 | 0.045526 | 0.057186 | 0.074669 | 0.11302 | 0.1437 | 0.18919 | 0.2425 | 0.26109 | 0.32335 | 0.33114 | 0.35959 | 0.33105 | 0.33747 | 0.36712 | 3.2358 | 0.19568 | 0.17595 | 0.20247 | 0.18836 | 0.19231 | 0.19036 | 0.18085 | 0.18843 | 0.17606 | 0.20074 | 0.17764 | 0.19341 |  | 0.083079 | 0.071379 | 0.068467 | 0.071491 | 0.070142 | 0.061548 | 0.072265 | 0.059265 | 0.072961 | 0.065531 | 0.078623 | 0.08365
LO1Slow | New | VRF | Commercial | HVAC | 0.00040906 | 2.176 | 111.9041 | XLarge Ret | VRF-NEW-XLarge Ret | 0.0002387 | 0.00059107 | 0.00078 | 0.0014907 | 0.0023809 | 0.0032663 | 0.0049392 | 0.0068933 | 0.011892 | 0.01814 | 0.024536 | 0.04446 | 0.059501 | 0.060939 | 0.066619 | 0.069542 | 0.061906 | 0.065256 | 0.063102 | 0.069219 | 0.63569 | 0.13645 | 0.12269 | 0.14118 | 0.13135 | 0.1341 | 0.13274 | 0.1261 | 0.13139 | 0.12276 | 0.13997 | 0.12387 | 0.13486 |  | 0.05793 | 0.049772 | 0.047742 | 0.04985 | 0.04891 | 0.042917 | 0.05039 | 0.041325 | 0.050875 | 0.045694 | 0.054823 | 0.058329
LO1Slow | New | VRF | Commercial | HVAC | 0.00041155 | 2.1893 | 114.8271 | Large Ret | VRF-NEW-Large Ret | 9.6042e-05 | 0.00023874 | 0.00031997 | 0.00061368 | 0.00097096 | 0.0013147 | 0.0019881 | 0.0027625 | 0.0048758 | 0.0075411 | 0.010123 | 0.018037 | 0.024076 | 0.024709 | 0.027114 | 0.028261 | 0.025256 | 0.026541 | 0.025687 | 0.028058 | 0.25858 | 0.13728 | 0.12344 | 0.14204 | 0.13215 | 0.13491 | 0.13355 | 0.12687 | 0.13219 | 0.12351 | 0.14083 | 0.12462 | 0.13568 |  | 0.058283 | 0.050075 | 0.048032 | 0.050154 | 0.049208 | 0.043178 | 0.050697 | 0.041577 | 0.051185 | 0.045972 | 0.055157 | 0.058684
LO1Slow | New | VRF | Commercial | HVAC | 0.00040512 | 2.155 | 107.2075 | Medium Ret | VRF-NEW-Medium Ret | 0.00035835 | 0.00088459 | 0.0011912 | 0.0022895 | 0.0036146 | 0.0048764 | 0.0072828 | 0.010145 | 0.01802 | 0.028028 | 0.037711 | 0.066636 | 0.089309 | 0.091432 | 0.1006 | 0.10486 | 0.094472 | 0.099178 | 0.095594 | 0.10446 | 0.96095 | 0.13513 | 0.12151 | 0.13982 | 0.13008 | 0.1328 | 0.13146 | 0.12489 | 0.13013 | 0.12158 | 0.13863 | 0.12268 | 0.13356 |  | 0.057372 | 0.049292 | 0.047282 | 0.04937 | 0.048438 | 0.042503 | 0.049904 | 0.040927 | 0.050385 | 0.045254 | 0.054295 | 0.057767
LO1Slow | New | VRF | Commercial | HVAC | 0.00039611 | 2.1071 | 96.1263 | Small Ret | VRF-NEW-Small Ret | 0.00011079 | 0.00027446 | 0.00037001 | 0.00071035 | 0.0011206 | 0.0014821 | 0.0022112 | 0.0030845 | 0.0056241 | 0.0088309 | 0.01188 | 0.020756 | 0.027755 | 0.028447 | 0.031398 | 0.032761 | 0.029585 | 0.031035 | 0.029972 | 0.032792 | 0.3002 | 0.13213 | 0.11881 | 0.13671 | 0.12719 | 0.12985 | 0.12854 | 0.12211 | 0.12723 | 0.11888 | 0.13554 | 0.11995 | 0.13059 |  | 0.056097 | 0.048197 | 0.046231 | 0.048272 | 0.047362 | 0.041559 | 0.048795 | 0.040017 | 0.049265 | 0.044248 | 0.053088 | 0.056482
LO1Slow | New | VRF | Commercial | HVAC | 0.00018837 | 2.0455 | 116.5856 | School K-12 | VRF-NEW-School K-12 | 0.00019687 | 0.0013199 | 0.0024821 | 0.0035263 | 0.0062615 | 0.011427 | 0.02006 | 0.04364 | 0.074769 | 0.086983 | 0.11278 | 0.14838 | 0.18276 | 0.19707 | 0.22555 | 0.22008 | 0.2618 | 0.24337 | 0.27134 | 0.25974 | 2.3736 | 0.15335 | 0.14067 | 0.15482 | 0.14717 | 0.15059 | 0.14416 | 0.12755 | 0.1501 | 0.15482 | 0.15806 | 0.13236 | 0.13623 |  | 0.043903 | 0.032425 | 0.026602 | 0.021484 | 0.01851 | 0.016189 | 0.015869 | 0.0166 | 0.021359 | 0.016362 | 0.026613 | 0.039677
LO1Slow | New | VRF | Commercial | HVAC | 0.00038914 | 2.0701 | 108.3165 | University | VRF-NEW-University | 0.00011308 | 0.00035993 | 0.0015391 | 0.0041393 | 0.0056715 | 0.010003 | 0.013174 | 0.028617 | 0.047838 | 0.063056 | 0.08824 | 0.11071 | 0.14131 | 0.16456 | 0.16412 | 0.16207 | 0.19533 | 0.18492 | 0.19366 | 0.20199 | 1.7814 | 0.1298 | 0.11671 | 0.13431 | 0.12495 | 0.12757 | 0.12627 | 0.11996 | 0.125 | 0.11679 | 0.13316 | 0.11784 | 0.12829 |  | 0.055109 | 0.047348 | 0.045417 | 0.047423 | 0.046528 | 0.040827 | 0.047936 | 0.039313 | 0.048398 | 0.043469 | 0.052154 | 0.055488
LO1Slow | New | VRF | Commercial | HVAC | 0.00041062 | 2.1843 | 115.1134 | Warehouse | VRF-NEW-Warehouse | 4.0793e-05 | 0.00012104 | 0.0001969 | 0.00031507 | 0.00040296 | 0.00056487 | 0.001099 | 0.0017614 | 0.0025917 | 0.0033144 | 0.0043634 | 0.0049139 | 0.0050637 | 0.005989 | 0.0066916 | 0.0081152 | 0.0081964 | 0.0081271 | 0.0084071 | 0.0075786 | 0.077854 | 0.13697 | 0.12315 | 0.14172 | 0.13184 | 0.13461 | 0.13324 | 0.12658 | 0.13189 | 0.12323 | 0.14051 | 0.12434 | 0.13537 |  | 0.05815 | 0.049961 | 0.047923 | 0.05004 | 0.049096 | 0.04308 | 0.050582 | 0.041482 | 0.051069 | 0.045868 | 0.055032 | 0.05855
LO1Slow | New | VRF | Commercial | HVAC | 0.00061845 | 3.2899 | 68.1601 | Supermarket | VRF-NEW-Supermarket | 1.5614e-05 | 4.131e-05 | 7.8607e-05 | 0.00014673 | 0.00024848 | 0.00039182 | 0.000582 | 0.00082287 | 0.001113 | 0.0014539 | 0.0018314 | 0.0022279 | 0.0026299 | 0.0028474 | 0.0033369 | 0.0035926 | 0.0037755 | 0.0038857 | 0.0039401 | 0.0039514 | 0.036913 | 0.20629 | 0.18549 | 0.21345 | 0.19858 | 0.20274 | 0.20068 | 0.19065 | 0.19865 | 0.1856 | 0.21162 | 0.18728 | 0.20389 |  | 0.087583 | 0.075249 | 0.07218 | 0.075367 | 0.073946 | 0.064885 | 0.076183 | 0.062478 | 0.076917 | 0.069084 | 0.082886 | 0.088186
LO1Slow | New | VRF | Commercial | HVAC | 0.0010483 | 5.5767 | 69.9303 | MiniMart | VRF-NEW-MiniMart | 1.3439e-05 | 3.7928e-05 | 4.2636e-05 | 8.4298e-05 | 0.00012278 | 0.0001496 | 0.00019736 | 0.00027282 | 0.00050365 | 0.0008293 | 0.0011923 | 0.0021378 | 0.0026264 | 0.0027861 | 0.0032654 | 0.003266 | 0.0028646 | 0.0030463 | 0.0029717 | 0.0031751 | 0.029586 | 0.34969 | 0.31442 | 0.36182 | 0.33661 | 0.34366 | 0.34018 | 0.32317 | 0.33673 | 0.31462 | 0.35872 | 0.31745 | 0.34562 |  | 0.14846 | 0.12755 | 0.12235 | 0.12776 | 0.12535 | 0.10999 | 0.12914 | 0.10591 | 0.13038 | 0.1171 | 0.1405 | 0.14948
LO1Slow | New | VRF | Commercial | HVAC | 0.00099175 | 5.2756 | 69.2453 | Restaurant | VRF-NEW-Restaurant | 0.00015082 | 0.00045706 | 0.00095074 | 0.0017853 | 0.0030365 | 0.0048164 | 0.0072202 | 0.010305 | 0.014087 | 0.018542 | 0.023646 | 0.039431 | 0.052571 | 0.059355 | 0.068373 | 0.077283 | 0.073195 | 0.076516 | 0.071505 | 0.079232 | 0.68246 | 0.33081 | 0.29745 | 0.34229 | 0.31844 | 0.32511 | 0.32181 | 0.30573 | 0.31856 | 0.29763 | 0.33936 | 0.30031 | 0.32696 |  | 0.14045 | 0.12067 | 0.11575 | 0.12086 | 0.11858 | 0.10405 | 0.12217 | 0.10019 | 0.12334 | 0.11078 | 0.13292 | 0.14141
LO1Slow | New | VRF | Commercial | HVAC | 0.000671 | 3.5694 | 59.0411 | Lodging | VRF-NEW-Lodging | 0.00062919 | 0.0018562 | 0.0029645 | 0.0057095 | 0.0084293 | 0.01286 | 0.018853 | 0.026881 | 0.039747 | 0.055958 | 0.081043 | 0.17229 | 0.24022 | 0.28239 | 0.32001 | 0.36429 | 0.32625 | 0.32755 | 0.31375 | 0.34014 | 2.9418 | 0.22382 | 0.20125 | 0.23159 | 0.21545 | 0.21996 | 0.21773 | 0.20685 | 0.21553 | 0.20137 | 0.2296 | 0.20319 | 0.22122 |  | 0.095024 | 0.081642 | 0.078312 | 0.081771 | 0.080228 | 0.070398 | 0.082656 | 0.067786 | 0.083452 | 0.074953 | 0.089928 | 0.095678
LO1Slow | New | VRF | Commercial | HVAC | 0.00051744 | 4.2671 | 91.7575 | Hospital | VRF-NEW-Hospital | 0.00021506 | 0.00055547 | 0.0010904 | 0.0017008 | 0.0020546 | 0.0028816 | 0.004009 | 0.0050508 | 0.0069719 | 0.0097101 | 0.014681 | 0.021734 | 0.02947 | 0.030323 | 0.032524 | 0.03427 | 0.033242 | 0.032483 | 0.030591 | 0.031202 | 0.32476 | 0.20224 | 0.18577 | 0.21685 | 0.20092 | 0.21116 | 0.21432 | 0.20946 | 0.22667 | 0.19873 | 0.2194 | 0.19289 | 0.20144 |  | 0.15821 | 0.13925 | 0.14178 | 0.14547 | 0.14949 | 0.1396 | 0.15991 | 0.14505 | 0.15549 | 0.14212 | 0.15317 | 0.1577
LO1Slow | New | VRF | Commercial | HVAC | 0.0004412 | 3.6384 | 76.9287 | Residential Care | VRF-NEW-Residential Care | 0.0031961 | 0.0086816 | 0.016694 | 0.026587 | 0.034448 | 0.050901 | 0.071159 | 0.093555 | 0.13531 | 0.1893 | 0.27589 | 0.41174 | 0.53555 | 0.55002 | 0.62597 | 0.65947 | 0.63788 | 0.64634 | 0.63321 | 0.63194 | 6.2378 | 0.17244 | 0.1584 | 0.1849 | 0.17131 | 0.18005 | 0.18274 | 0.1786 | 0.19328 | 0.16945 | 0.18707 | 0.16447 | 0.17176 |  | 0.1349 | 0.11874 | 0.12089 | 0.12403 | 0.12746 | 0.11903 | 0.13635 | 0.12368 | 0.13258 | 0.12118 | 0.1306 | 0.13446
LO1Slow | New | VRF | Commercial | HVAC | 0.00072766 | 3.8708 | 51.8106 | Assembly | VRF-NEW-Assembly | 0.0007517 | 0.0022433 | 0.0034966 | 0.0075665 | 0.011404 | 0.017109 | 0.017734 | 0.026819 | 0.055681 | 0.10236 | 0.14428 | 0.21722 | 0.33788 | 0.43051 | 0.51211 | 0.54233 | 0.54689 | 0.55548 | 0.56023 | 0.54913 | 4.6412 | 0.24272 | 0.21825 | 0.25114 | 0.23364 | 0.23854 | 0.23612 | 0.22432 | 0.23373 | 0.21838 | 0.24899 | 0.22035 | 0.2399 |  | 0.10305 | 0.088537 | 0.084926 | 0.088676 | 0.087004 | 0.076343 | 0.089637 | 0.073511 | 0.0905 | 0.081283 | 0.097523 | 0.10376
LO1Slow | New | VRF | Commercial | HVAC | 0.00075402 | 4.0111 | 49.9198 | Other | VRF-NEW-Other | 0.010065 | 0.02516 | 0.051966 | 0.091218 | 0.12149 | 0.21474 | 0.31585 | 0.49031 | 0.73088 | 0.93898 | 1.3444 | 1.7493 | 2.1177 | 2.2686 | 2.7134 | 2.6544 | 2.9132 | 2.874 | 2.7844 | 2.7246 | 27.1347 | 0.25151 | 0.22615 | 0.26024 | 0.24211 | 0.24718 | 0.24467 | 0.23244 | 0.2422 | 0.22629 | 0.25801 | 0.22833 | 0.24859 |  | 0.10678 | 0.091744 | 0.088002 | 0.091889 | 0.090155 | 0.079109 | 0.092884 | 0.076174 | 0.093779 | 0.084228 | 0.10106 | 0.10752
Retro3Slow | Retro | VRF | Commercial | HVAC | 0.00074926 | 3.9857 | 69.9954 | Large Off | VRF-Retro-Large Off | 0.020183 | 0.032283 | 0.065369 | 0.11578 | 0.18272 | 0.25931 | 0.33351 | 0.39454 | 0.42985 | 0.43462 | 0.41078 | 0.3639 | 0.30376 | 0.23979 | 0.17902 | 0.12711 | 0.085909 | 0.055398 | 0.034132 | 0.020147 | 3.446 | 0.24992 | 0.22472 | 0.2586 | 0.24058 | 0.24562 | 0.24313 | 0.23097 | 0.24067 | 0.22486 | 0.25638 | 0.22689 | 0.24702 | 0 | 0.10611 | 0.091165 | 0.087446 | 0.091308 | 0.089586 | 0.078609 | 0.092297 | 0.075693 | 0.093186 | 0.083696 | 0.10042 | 0.10684
Retro3Slow | Retro | VRF | Commercial | HVAC | 0.00045259 | 2.4076 | 70.6764 | Medium Off | VRF-Retro-Medium Off | 0.017131 | 0.027739 | 0.056617 | 0.10109 | 0.161 | 0.23028 | 0.2976 | 0.3545 | 0.38817 | 0.39384 | 0.37335 | 0.33125 | 0.27642 | 0.21772 | 0.16205 | 0.11456 | 0.076995 | 0.049368 | 0.030225 | 0.017728 | 2.9248 | 0.15097 | 0.13574 | 0.15621 | 0.14532 | 0.14837 | 0.14686 | 0.13952 | 0.14538 | 0.13583 | 0.15487 | 0.13705 | 0.14921 | 0 | 0.064095 | 0.055068 | 0.052822 | 0.055155 | 0.054114 | 0.047484 | 0.055752 | 0.045722 | 0.056289 | 0.050557 | 0.060657 | 0.064536
Retro3Slow | Retro | VRF | Commercial | HVAC | 0.00066926 | 3.5602 | 35.8449 | Small Off | VRF-Retro-Small Off | 0.024449 | 0.038663 | 0.077602 | 0.1363 | 0.21303 | 0.29952 | 0.38216 | 0.44775 | 0.48369 | 0.4849 | 0.45387 | 0.3981 | 0.32859 | 0.25611 | 0.18896 | 0.13245 | 0.088361 | 0.05626 | 0.034246 | 0.019975 | 4.1744 | 0.22324 | 0.20073 | 0.23099 | 0.21489 | 0.21939 | 0.21717 | 0.20632 | 0.21497 | 0.20085 | 0.22901 | 0.20266 | 0.22065 | 0 | 0.094779 | 0.081432 | 0.07811 | 0.08156 | 0.080021 | 0.070216 | 0.082443 | 0.067612 | 0.083237 | 0.07476 | 0.089697 | 0.095431
Retro3Slow | Retro | VRF | Commercial | HVAC | 0.00040466 | 2.1526 | 132.4438 | XLarge Ret | VRF-Retro-XLarge Ret | 0.00079136 | 0.0012544 | 0.0025241 | 0.0044254 | 0.0068976 | 0.0096715 | 0.012318 | 0.01438 | 0.015494 | 0.01552 | 0.014521 | 0.01274 | 0.010554 | 0.0082646 | 0.0061228 | 0.0043076 | 0.0028848 | 0.0018415 | 0.0011245 | 0.00065776 | 0.13105 | 0.13498 | 0.12137 | 0.13966 | 0.12993 | 0.13265 | 0.13131 | 0.12475 | 0.12998 | 0.12144 | 0.13847 | 0.12254 | 0.13341 | 0 | 0.057307 | 0.049236 | 0.047228 | 0.049314 | 0.048384 | 0.042455 | 0.049848 | 0.04088 | 0.050328 | 0.045203 | 0.054234 | 0.057701
Retro3Slow | Retro | VRF | Commercial | HVAC | 0.00040713 | 2.1657 | 135.8566 | Large Ret | VRF-Retro-Large Ret | 0.016834 | 0.026431 | 0.052771 | 0.092089 | 0.14285 | 0.19941 | 0.25299 | 0.29423 | 0.31585 | 0.31495 | 0.2932 | 0.25591 | 0.2104 | 0.16342 | 0.12021 | 0.083996 | 0.055889 | 0.035483 | 0.021549 | 0.01254 | 2.7878 | 0.1358 | 0.12211 | 0.14051 | 0.13072 | 0.13346 | 0.13211 | 0.12551 | 0.13077 | 0.12218 | 0.13931 | 0.12328 | 0.13422 | 0 | 0.057656 | 0.049536 | 0.047516 | 0.049614 | 0.048678 | 0.042714 | 0.050152 | 0.041129 | 0.050635 | 0.045478 | 0.054564 | 0.058053
Retro3Slow | Retro | VRF | Commercial | HVAC | 0.00040076 | 2.1319 | 126.9602 | Medium Ret | VRF-Retro-Medium Ret | 0.0077017 | 0.01239 | 0.025229 | 0.044559 | 0.069969 | 0.098766 | 0.12648 | 0.14845 | 0.16076 | 0.16208 | 0.15279 | 0.13508 | 0.11303 | 0.089487 | 0.066917 | 0.047501 | 0.032077 | 0.020621 | 0.01268 | 0.0074649 | 1.2754 | 0.13368 | 0.1202 | 0.13832 | 0.12868 | 0.13138 | 0.13004 | 0.12354 | 0.12873 | 0.12027 | 0.13713 | 0.12136 | 0.13213 | 0 | 0.056755 | 0.048762 | 0.046773 | 0.048839 | 0.047917 | 0.042046 | 0.049368 | 0.040486 | 0.049843 | 0.044767 | 0.053711 | 0.057145
Retro3Slow | Retro | VRF | Commercial | HVAC | 0.00039185 | 2.0845 | 114.0222 | Small Ret | VRF-Retro-Small Ret | 0.0030318 | 0.0047814 | 0.0095811 | 0.016758 | 0.026055 | 0.036449 | 0.046324 | 0.053966 | 0.058027 | 0.057989 | 0.054122 | 0.047365 | 0.039083 | 0.030477 | 0.022496 | 0.015772 | 0.010529 | 0.006703 | 0.004082 | 0.0023817 | 0.50208 | 0.13071 | 0.11753 | 0.13524 | 0.12582 | 0.12845 | 0.12715 | 0.1208 | 0.12587 | 0.1176 | 0.13409 | 0.11866 | 0.12919 | 0 | 0.055493 | 0.047678 | 0.045733 | 0.047753 | 0.046852 | 0.041112 | 0.04827 | 0.039587 | 0.048735 | 0.043772 | 0.052517 | 0.055875
Retro3Slow | Retro | VRF | Commercial | HVAC | 0.00018294 | 1.9865 | 139.6415 | School K-12 | VRF-Retro-School K-12 | 0.0063636 | 0.0099824 | 0.019974 | 0.034949 | 0.054303 | 0.075944 | 0.096589 | 0.11266 | 0.1215 | 0.1218 | 0.11383 | 0.099706 | 0.082184 | 0.063957 | 0.04712 | 0.03297 | 0.021957 | 0.01396 | 0.0084856 | 0.0049438 | 1.0639 | 0.14893 | 0.13662 | 0.15036 | 0.14293 | 0.14625 | 0.14001 | 0.12388 | 0.14578 | 0.15036 | 0.1535 | 0.12855 | 0.13231 | 0 | 0.042638 | 0.031491 | 0.025835 | 0.020865 | 0.017977 | 0.015723 | 0.015412 | 0.016122 | 0.020744 | 0.015891 | 0.025846 | 0.038533
Retro3Slow | Retro | VRF | Commercial | HVAC | 0.00038914 | 2.0701 | 126.7607 | University | VRF-Retro-University | 0.0033594 | 0.0052711 | 0.010525 | 0.01843 | 0.028744 | 0.040291 | 0.051365 | 0.059974 | 0.06478 | 0.065041 | 0.060916 | 0.053491 | 0.044185 | 0.034462 | 0.025448 | 0.017832 | 0.01189 | 0.0075691 | 0.0046064 | 0.0026865 | 0.56166 | 0.1298 | 0.11671 | 0.13431 | 0.12495 | 0.12757 | 0.12627 | 0.11996 | 0.125 | 0.11679 | 0.13316 | 0.11784 | 0.12829 | 0 | 0.055109 | 0.047348 | 0.045417 | 0.047423 | 0.046528 | 0.040827 | 0.047936 | 0.039313 | 0.048398 | 0.043469 | 0.052154 | 0.055488
Retro3Slow | Retro | VRF | Commercial | HVAC | 0.00056074 | 2.9829 | 95.7151 | Warehouse | VRF-Retro-Warehouse | 0.017781 | 0.028324 | 0.057387 | 0.1013 | 0.15865 | 0.22303 | 0.28478 | 0.33396 | 0.36186 | 0.36432 | 0.34221 | 0.30144 | 0.2497 | 0.1951 | 0.14446 | 0.10161 | 0.068132 | 0.043589 | 0.026665 | 0.015633 | 2.9957 | 0.18704 | 0.16818 | 0.19353 | 0.18005 | 0.18382 | 0.18195 | 0.17286 | 0.18011 | 0.16828 | 0.19188 | 0.1698 | 0.18487 | 0 | 0.07941 | 0.068227 | 0.065444 | 0.068335 | 0.067045 | 0.05883 | 0.069074 | 0.056648 | 0.06974 | 0.062637 | 0.075152 | 0.079957
Retro3Slow | Retro | VRF | Commercial | HVAC | 0.00062419 | 3.3204 | 79.5429 | Supermarket | VRF-Retro-Supermarket | 0.0066354 | 0.010412 | 0.020771 | 0.03623 | 0.056174 | 0.078387 | 0.09944 | 0.11563 | 0.12411 | 0.1237 | 0.11506 | 0.10034 | 0.082353 | 0.063837 | 0.046868 | 0.032699 | 0.021727 | 0.013781 | 0.0083613 | 0.0048617 | 1.0101 | 0.20821 | 0.18721 | 0.21543 | 0.20042 | 0.20462 | 0.20254 | 0.19242 | 0.20049 | 0.18733 | 0.21359 | 0.18901 | 0.20579 | 0 | 0.088396 | 0.075947 | 0.072849 | 0.076067 | 0.074632 | 0.065487 | 0.07689 | 0.063058 | 0.077631 | 0.069725 | 0.083655 | 0.089004
Retro3Slow | Retro | VRF | Commercial | HVAC | 0.0010581 | 5.6284 | 81.5687 | MiniMart | VRF-Retro-MiniMart | 0.004709 | 0.0074322 | 0.014917 | 0.026094 | 0.040584 | 0.05677 | 0.07213 | 0.08398 | 0.090247 | 0.09013 | 0.08408 | 0.073573 | 0.060718 | 0.047335 | 0.034942 | 0.024512 | 0.016368 | 0.010422 | 0.0063489 | 0.0037055 | 0.77804 | 0.35293 | 0.31734 | 0.36518 | 0.33973 | 0.34685 | 0.34333 | 0.32617 | 0.33986 | 0.31754 | 0.36205 | 0.3204 | 0.34883 | 0 | 0.14984 | 0.12874 | 0.12349 | 0.12894 | 0.12651 | 0.11101 | 0.13034 | 0.10689 | 0.13159 | 0.11819 | 0.1418 | 0.15087
Retro3Slow | Retro | VRF | Commercial | HVAC | 0.0010976 | 5.8389 | 72.7283 | Restaurant | VRF-Retro-Restaurant | 0.00015996 | 0.00025254 | 0.00050733 | 0.00089139 | 0.0013921 | 0.0019565 | 0.0024996 | 0.0029269 | 0.0031632 | 0.0031739 | 0.0029718 | 0.0026083 | 0.0021598 | 0.0016907 | 0.0012532 | 0.00088262 | 0.00059217 | 0.00037877 | 0.00023174 | 0.00013576 | 0.026429 | 0.36613 | 0.32921 | 0.37884 | 0.35244 | 0.35982 | 0.35617 | 0.33837 | 0.35257 | 0.32941 | 0.37559 | 0.33238 | 0.36187 | 0 | 0.15544 | 0.13355 | 0.12811 | 0.13376 | 0.13124 | 0.11516 | 0.13521 | 0.11089 | 0.13651 | 0.12261 | 0.14711 | 0.15651
Retro3Slow | Retro | VRF | Commercial | HVAC | 0.00071027 | 3.7783 | 65.3946 | Lodging | VRF-Retro-Lodging | 0.0017082 | 0.002695 | 0.005409 | 0.009484 | 0.014782 | 0.020723 | 0.026404 | 0.030833 | 0.033232 | 0.033261 | 0.031072 | 0.027218 | 0.022485 | 0.01755 | 0.012973 | 0.0091064 | 0.0060871 | 0.0038801 | 0.0023651 | 0.0013811 | 0.295 | 0.23692 | 0.21303 | 0.24514 | 0.22806 | 0.23284 | 0.23048 | 0.21896 | 0.22814 | 0.21316 | 0.24304 | 0.21508 | 0.23417 | 0 | 0.10059 | 0.086421 | 0.082896 | 0.086557 | 0.084924 | 0.074519 | 0.087494 | 0.071754 | 0.088337 | 0.079341 | 0.095193 | 0.10128
Retro3Slow | Retro | VRF | Commercial | HVAC | 0.00051744 | 4.2671 | 107.0478 | Hospital | VRF-Retro-Hospital | 0.0011908 | 0.0019416 | 0.0040022 | 0.0071897 | 0.01142 | 0.016212 | 0.020879 | 0.02462 | 0.026754 | 0.026994 | 0.025432 | 0.022506 | 0.018791 | 0.014846 | 0.011089 | 0.0078621 | 0.0053058 | 0.0034136 | 0.0020989 | 0.0012355 | 0.20683 | 0.20224 | 0.18577 | 0.21685 | 0.20092 | 0.21116 | 0.21432 | 0.20946 | 0.22667 | 0.19873 | 0.2194 | 0.19289 | 0.20144 | 0 | 0.15821 | 0.13925 | 0.14178 | 0.14547 | 0.14949 | 0.1396 | 0.15991 | 0.14505 | 0.15549 | 0.14212 | 0.15317 | 0.1577
Retro3Slow | Retro | VRF | Commercial | HVAC | 0.00048344 | 3.9867 | 81.4608 | Residential Care | VRF-Retro-Residential Care | 0.0068192 | 0.011068 | 0.02276 | 0.040775 | 0.064638 | 0.091707 | 0.11809 | 0.13919 | 0.1512 | 0.15249 | 0.14351 | 0.12668 | 0.10536 | 0.082728 | 0.061396 | 0.04325 | 0.028987 | 0.018523 | 0.011317 | 0.0066227 | 1.1777 | 0.18895 | 0.17357 | 0.2026 | 0.18772 | 0.19729 | 0.20024 | 0.1957 | 0.21178 | 0.18567 | 0.20499 | 0.18021 | 0.1882 | 0 | 0.14782 | 0.13011 | 0.13247 | 0.13591 | 0.13967 | 0.13043 | 0.1494 | 0.13552 | 0.14527 | 0.13279 | 0.1431 | 0.14734
Retro3Slow | Retro | VRF | Commercial | HVAC | 0.00060272 | 3.2062 | 76.4559 | Assembly | VRF-Retro-Assembly | 0.044833 | 0.070755 | 0.14207 | 0.249 | 0.38827 | 0.54445 | 0.69379 | 0.809 | 0.87092 | 0.8723 | 0.81718 | 0.71817 | 0.59504 | 0.46695 | 0.3475 | 0.24581 | 0.1655 | 0.10626 | 0.065238 | 0.038371 | 7.4406 | 0.20105 | 0.18077 | 0.20802 | 0.19353 | 0.19758 | 0.19558 | 0.1858 | 0.1936 | 0.18088 | 0.20624 | 0.18251 | 0.19871 | 0 | 0.085356 | 0.073335 | 0.070344 | 0.073451 | 0.072065 | 0.063235 | 0.074246 | 0.060889 | 0.074961 | 0.067327 | 0.080779 | 0.085943
Retro3Slow | Retro | VRF | Commercial | HVAC | 0.0008105 | 4.3115 | 54.4355 | Other | VRF-Retro-Other | 0.0039254 | 0.0063461 | 0.012966 | 0.023132 | 0.036597 | 0.051802 | 0.066758 | 0.078771 | 0.085848 | 0.086914 | 0.081973 | 0.07252 | 0.060339 | 0.047345 | 0.035103 | 0.024714 | 0.016534 | 0.010554 | 0.0064384 | 0.0037613 | 0.59758 | 0.27035 | 0.24309 | 0.27973 | 0.26024 | 0.26569 | 0.263 | 0.24985 | 0.26034 | 0.24324 | 0.27734 | 0.24543 | 0.26721 | 0 | 0.11478 | 0.098616 | 0.094594 | 0.098771 | 0.096908 | 0.085034 | 0.099841 | 0.08188 | 0.1008 | 0.090537 | 0.10863 | 0.11557
Note on A1: Charlie Grist: Lookup in ComMaster
Note on B1: Charlie Grist: New, NR, Retro
Note on C1: Charlie Grist: Measure Index Name
Note on E1: Charlie Grist: Use Massoud's Names
Note on F1: Charlie Grist: From Shaped Savings column 14
Note on G1: Charlie Grist: From SC or from Shaped Savings column 3.
Note on H1: Charlie Grist: From SC or from Shaped Savings column K (column 11)
Note on I1: Charlie Grist: From SC
Note on J1: Charlie Grist: From SC
Note on K1: Charlie Grist: From SC
Note on AF1: Charlie Grist: From Shaped Savings. Copy whole row down since column increment is hardwired into formula.

## SC-New
Units Methodology | VRF in new construction. Use slow ramp rate because it is a new measure.
| Vintage | New | New
End-Use: | Measure Bundle | VRF-NEW | Region
HVAC | Report Year | 2035 | Base
| Total Potential (aMW) | 61.089 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
UNITS FOR EXISTING STOCK |  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
|  |  |  | FLOOR_2016 | FLOOR_2017 | FLOOR_2018 | FLOOR_2019 | FLOOR_2020 | FLOOR_2021 | FLOOR_2022 | FLOOR_2023 | FLOOR_2024 | FLOOR_2025 | FLOOR_2026 | FLOOR_2027 | FLOOR_2028 | FLOOR_2029 | FLOOR_2030 | FLOOR_2031 | FLOOR_2032 | FLOOR_2033 | FLOOR_2034 | FLOOR_2035
|  | Large Off |  | 7.8067 | 5.9497 | 5.8909 | 6.8916 | 6.641 | 5.4382 | 6.9237 | 6.0406 | 5.862 | 6.6048 | 6.6082 | 7.2276 | 7.9321 | 7.259 | 7.9122 | 7.7623 | 7.6402 | 7.1725 | 7.081 | 7.4281
|  | Medium Off |  | 6.3307 | 4.6246 | 4.6954 | 5.5562 | 5.2903 | 4.0955 | 5.6166 | 4.8928 | 4.649 | 5.3601 | 5.3451 | 5.7169 | 6.1644 | 5.8004 | 6.4332 | 6.1077 | 6.3133 | 5.5403 | 5.5266 | 5.9833
|  | Small Off |  | 1.6621 | 1.2171 | 1.2444 | 1.4586 | 1.4004 | 1.0788 | 1.4748 | 1.2896 | 1.2239 | 1.4012 | 1.3991 | 1.4996 | 1.6198 | 1.5187 | 1.6891 | 1.5972 | 1.6405 | 1.4566 | 1.4532 | 1.5649
|  | XLarge Ret |  | 1.7994 | 1.4858 | 0.89794 | 0.91202 | 0.85125 | 0.73204 | 0.73428 | 0.71341 | 0.89456 | 1.0321 | 1.0963 | 1.6173 | 1.8239 | 1.6267 | 1.597 | 1.5393 | 1.2961 | 1.3176 | 1.247 | 1.354
|  | Large Ret |  | 0.7196 | 0.59648 | 0.36612 | 0.37318 | 0.34505 | 0.29286 | 0.29376 | 0.28416 | 0.36455 | 0.42647 | 0.44956 | 0.65214 | 0.73354 | 0.65561 | 0.64605 | 0.62178 | 0.52555 | 0.53266 | 0.50454 | 0.54553
|  | Medium Ret |  | 2.7276 | 2.2452 | 1.3847 | 1.4143 | 1.3049 | 1.1035 | 1.0932 | 1.0602 | 1.3687 | 1.6102 | 1.7014 | 2.4475 | 2.7643 | 2.4645 | 2.4352 | 2.3437 | 1.9971 | 2.0221 | 1.9075 | 2.0634
|  | Small Ret |  | 0.8625 | 0.71244 | 0.43988 | 0.4488 | 0.41374 | 0.34302 | 0.33947 | 0.32966 | 0.43689 | 0.51887 | 0.54817 | 0.7797 | 0.87859 | 0.7842 | 0.77729 | 0.74887 | 0.63964 | 0.64715 | 0.61166 | 0.66242
|  | School K-12 |  | 0.49337 | 1.103 | 0.94992 | 0.71721 | 0.74423 | 0.8514 | 0.99139 | 1.5015 | 1.8698 | 1.6453 | 1.6753 | 1.7943 | 1.8624 | 1.7489 | 1.7976 | 1.6195 | 1.8221 | 1.6337 | 1.7826 | 1.6891
|  | University |  | 0.28002 | 0.2972 | 0.58203 | 0.83189 | 0.6661 | 0.73648 | 0.64334 | 0.97289 | 1.1821 | 1.1785 | 1.2952 | 1.3229 | 1.4229 | 1.443 | 1.2924 | 1.1785 | 1.3434 | 1.2266 | 1.2571 | 1.298
|  | Warehouse |  | 7.6587 | 7.5775 | 5.6454 | 4.8008 | 3.5881 | 3.153 | 4.0692 | 4.54 | 4.8555 | 4.6966 | 4.8557 | 4.4518 | 3.8658 | 3.9817 | 3.9952 | 4.4738 | 4.2737 | 4.087 | 4.1377 | 3.6922
|  | Supermarket |  | 0.38925 | 0.34341 | 0.29927 | 0.29689 | 0.2938 | 0.29042 | 0.28614 | 0.28164 | 0.27689 | 0.27358 | 0.27063 | 0.26801 | 0.2666 | 0.25138 | 0.26455 | 0.26299 | 0.26141 | 0.25948 | 0.25751 | 0.25563
|  | MiniMart |  | 0.19766 | 0.18601 | 0.095761 | 0.10062 | 0.085647 | 0.065415 | 0.057243 | 0.055087 | 0.073916 | 0.092056 | 0.10394 | 0.15172 | 0.15707 | 0.14511 | 0.15273 | 0.14105 | 0.11701 | 0.12001 | 0.11457 | 0.12118
|  | Restaurant |  | 0.46895 | 0.47387 | 0.45145 | 0.45051 | 0.44778 | 0.44523 | 0.44274 | 0.43991 | 0.43709 | 0.43514 | 0.4358 | 0.59162 | 0.66468 | 0.65354 | 0.67606 | 0.7056 | 0.63207 | 0.63726 | 0.58284 | 0.63928
|  | Lodging |  | 1.0327 | 1.0159 | 0.74305 | 0.76054 | 0.65616 | 0.62755 | 0.61023 | 0.60572 | 0.65098 | 0.6932 | 0.78844 | 1.3646 | 1.6032 | 1.6413 | 1.6703 | 1.7557 | 1.4871 | 1.44 | 1.35 | 1.4487
|  | Hospital |  | 4.1336 | 3.5601 | 3.2008 | 2.6531 | 1.873 | 1.6467 | 1.5196 | 1.3328 | 1.3372 | 1.4087 | 1.6726 | 2.0158 | 2.3034 | 2.0639 | 1.988 | 1.9342 | 1.7745 | 1.6724 | 1.5414 | 1.5563
|  | Residential Care |  | 4.5029 | 4.0786 | 3.592 | 3.0401 | 2.3019 | 2.1321 | 1.9772 | 1.8096 | 1.9023 | 2.013 | 2.304 | 2.7992 | 3.0682 | 2.7442 | 2.8047 | 2.7283 | 2.496 | 2.4392 | 2.3387 | 2.3104
|  | Assembly |  | 3.1855 | 3.1699 | 2.2629 | 2.6024 | 2.292 | 2.1556 | 1.482 | 1.5603 | 2.3546 | 3.274 | 3.6242 | 4.442 | 5.8224 | 6.4604 | 6.9015 | 6.7485 | 6.4365 | 6.3053 | 6.2237 | 6.0387
|  | Other |  | 12.8631 | 10.722 | 10.1421 | 9.4612 | 7.3639 | 8.1591 | 7.9604 | 8.6026 | 9.3208 | 9.0573 | 10.1844 | 10.7877 | 11.0054 | 10.2671 | 11.0275 | 9.9609 | 10.34 | 9.8384 | 9.3283 | 9.0356
|  |  |  | 57.1143 | 49.3587 | 42.884 | 42.7699 | 36.5593 | 33.3471 | 36.5153 | 36.3126 | 39.0609 | 41.7212 | 44.3582 | 49.9305 | 53.9587 | 51.5098 | 54.0605 | 52.2301 | 51.0362 | 48.3482 | 47.246 | 47.6867
Incremental based on achievability, ramp rate, and applicability |  |  | Achievability | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 85%
| Applicability | VRF-NEW | LO1Slow | 0.2564% | 0.769% | 1.679% | 3.16% | 5.407% | 8.625% | 13% | 18.68% | 25.7% | 33.98% | 43.26% | 53.14% | 63.06% | 72.42% | 80.64% | 87.33% | 92.33% | 95.74% | 97.82% | 98.82%
| 4.9% | Large Off |  | 0.00083381 | 0.0019057 | 0.00412 | 0.0090694 | 0.014955 | 0.019537 | 0.037498 | 0.046994 | 0.062743 | 0.093465 | 0.11907 | 0.15998 | 0.20835 | 0.21894 | 0.26574 | 0.28234 | 0.29382 | 0.286 | 0.2885 | 0.30573 | 5.7507
| 78.4% | Medium Off |  | 0.010819 | 0.0237 | 0.052543 | 0.11699 | 0.19062 | 0.2354 | 0.4867 | 0.60904 | 0.79615 | 1.2136 | 1.541 | 2.0246 | 2.5906 | 2.7991 | 3.457 | 3.5546 | 3.8847 | 3.5347 | 3.6027 | 3.9403 | 73.3323
| 78.4% | Small Off |  | 0.0028404 | 0.0062374 | 0.013925 | 0.030713 | 0.050459 | 0.062007 | 0.1278 | 0.16053 | 0.2096 | 0.31726 | 0.40338 | 0.53108 | 0.68072 | 0.73291 | 0.90766 | 0.92956 | 1.0094 | 0.9293 | 0.9473 | 1.0305 | 19.2521
| 24.5% | XLarge Ret |  | 0.00096095 | 0.0023795 | 0.0031401 | 0.0060011 | 0.009585 | 0.013149 | 0.019884 | 0.027751 | 0.047874 | 0.073025 | 0.098775 | 0.17898 | 0.23953 | 0.24532 | 0.26819 | 0.27996 | 0.24921 | 0.2627 | 0.25403 | 0.27866 | 5.1163
| 24.5% | Large Ret |  | 0.00038429 | 0.00095528 | 0.0012803 | 0.0024555 | 0.0038852 | 0.0052605 | 0.0079549 | 0.011053 | 0.01951 | 0.030175 | 0.040503 | 0.072172 | 0.096335 | 0.098869 | 0.10849 | 0.11308 | 0.10106 | 0.1062 | 0.10278 | 0.11227 | 2.0678
| 24.5% | Medium Ret |  | 0.0014566 | 0.0035957 | 0.0048421 | 0.0093064 | 0.014693 | 0.019822 | 0.029604 | 0.04124 | 0.07325 | 0.11393 | 0.15329 | 0.27087 | 0.36303 | 0.37166 | 0.40894 | 0.42624 | 0.38402 | 0.40315 | 0.38858 | 0.42464 | 7.8009
| 24.5% | Small Ret |  | 0.00046061 | 0.001141 | 0.0015382 | 0.0029531 | 0.0046587 | 0.0061613 | 0.0091925 | 0.012823 | 0.023381 | 0.036713 | 0.049388 | 0.086288 | 0.11538 | 0.11826 | 0.13053 | 0.13619 | 0.12299 | 0.12902 | 0.1246 | 0.13632 | 2.483
| 78.4% | School K-12 |  | 0.00084313 | 0.0056526 | 0.01063 | 0.015102 | 0.026816 | 0.048938 | 0.085908 | 0.18689 | 0.32021 | 0.37251 | 0.483 | 0.63544 | 0.7827 | 0.84399 | 0.96596 | 0.94253 | 1.1212 | 1.0423 | 1.1621 | 1.1124 | 18.8542
| 78.4% | University |  | 0.00047853 | 0.0015231 | 0.006513 | 0.017517 | 0.024001 | 0.042332 | 0.055748 | 0.1211 | 0.20244 | 0.26684 | 0.37341 | 0.4685 | 0.59798 | 0.69637 | 0.6945 | 0.68586 | 0.82661 | 0.78253 | 0.81951 | 0.85479 | 13.6283
| 0.98% | Warehouse |  | 0.0001636 | 0.00048542 | 0.00078966 | 0.0012636 | 0.0016161 | 0.0022654 | 0.0044076 | 0.007064 | 0.010394 | 0.013292 | 0.017499 | 0.019707 | 0.020308 | 0.024019 | 0.026836 | 0.032546 | 0.032871 | 0.032594 | 0.033716 | 0.030394 | 0.76969
| 4.9% | Supermarket |  | 4.1575e-05 | 0.00011 | 0.00020931 | 0.00039071 | 0.00066163 | 0.0010433 | 0.0015497 | 0.0021911 | 0.0029636 | 0.0038714 | 0.0048765 | 0.0059322 | 0.0070026 | 0.007582 | 0.0088852 | 0.009566 | 0.010053 | 0.010347 | 0.010491 | 0.010521 | 0.2353
| 4.9% | MiniMart |  | 2.1111e-05 | 5.9579e-05 | 6.6974e-05 | 0.00013242 | 0.00019287 | 0.000235 | 0.00031002 | 0.00042856 | 0.00079115 | 0.0013027 | 0.0018728 | 0.0033582 | 0.0041256 | 0.0043766 | 0.0051295 | 0.0051304 | 0.0044998 | 0.0047852 | 0.0046681 | 0.0049875 | 0.097202
| 24.5% | Restaurant |  | 0.00025044 | 0.00075893 | 0.0015787 | 0.0029644 | 0.0050419 | 0.0079974 | 0.011989 | 0.017112 | 0.023391 | 0.030788 | 0.039264 | 0.065474 | 0.087292 | 0.098557 | 0.11353 | 0.12833 | 0.12154 | 0.12705 | 0.11873 | 0.13156 | 2.2307
| 68.6% | Lodging |  | 0.0015442 | 0.0045555 | 0.0072755 | 0.014012 | 0.020687 | 0.031562 | 0.046269 | 0.065972 | 0.097547 | 0.13733 | 0.1989 | 0.42284 | 0.58954 | 0.69303 | 0.78537 | 0.89404 | 0.80068 | 0.80387 | 0.77002 | 0.83479 | 12.7963
| 4.9% | Hospital |  | 0.0004415 | 0.0011403 | 0.0022386 | 0.0034916 | 0.0042179 | 0.0059158 | 0.0082301 | 0.010369 | 0.014313 | 0.019934 | 0.030138 | 0.044619 | 0.0605 | 0.06225 | 0.066769 | 0.070355 | 0.068243 | 0.066685 | 0.062802 | 0.064056 | 1.7155
| 78.4% | Residential Care |  | 0.0076951 | 0.020903 | 0.040195 | 0.064013 | 0.08294 | 0.12255 | 0.17133 | 0.22525 | 0.32578 | 0.45577 | 0.66426 | 0.99133 | 1.2894 | 1.3243 | 1.5071 | 1.5878 | 1.5358 | 1.5562 | 1.5246 | 1.5215 | 35.5742
| 24.5% | Assembly |  | 0.0017012 | 0.0050767 | 0.0079131 | 0.017124 | 0.025807 | 0.03872 | 0.040133 | 0.060695 | 0.12601 | 0.23165 | 0.32652 | 0.4916 | 0.76466 | 0.97427 | 1.159 | 1.2273 | 1.2376 | 1.2571 | 1.2678 | 1.2427 | 17.3561
| 78.4% | Other |  | 0.021982 | 0.05495 | 0.11349 | 0.19922 | 0.26533 | 0.46898 | 0.6898 | 1.0708 | 1.5962 | 2.0507 | 2.9362 | 3.8204 | 4.6251 | 4.9547 | 5.9259 | 5.797 | 6.3624 | 6.2768 | 6.081 | 5.9504 | 130.233
SUPPLY CURVE SAVINGS BY BUNDLE |  | VRF-NEW |  | 2016: aMW
Savings Per SF |  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | MAX
Busbar Savings (kWh) | lvlcost | segment | measure | aMW_2016 | aMW_2017 | aMW_2018 | aMW_2019 | aMW_2020 | aMW_2021 | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | MAX
3.4937 | 69.0059 | Large Off | VRF-NEW-Large Off | 0.00033254 | 0.00076004 | 0.0016431 | 0.003617 | 0.0059645 | 0.0077915 | 0.014955 | 0.018742 | 0.025023 | 0.037276 | 0.047489 | 0.063801 | 0.083092 | 0.087318 | 0.10598 | 0.1126 | 0.11718 | 0.11406 | 0.11506 | 0.12193 | 1.0846
2.1104 | 69.6785 | Medium Off | VRF-NEW-Medium Off | 0.0026063 | 0.0057096 | 0.012658 | 0.028184 | 0.045921 | 0.056711 | 0.11725 | 0.14672 | 0.1918 | 0.29237 | 0.37124 | 0.48774 | 0.6241 | 0.67433 | 0.83283 | 0.85632 | 0.93585 | 0.85153 | 0.86792 | 0.94925 | 8.3511
3.1207 | 35.2743 | Small Off | VRF-NEW-Small Off | 0.0010119 | 0.002222 | 0.0049608 | 0.010941 | 0.017975 | 0.022089 | 0.045526 | 0.057186 | 0.074669 | 0.11302 | 0.1437 | 0.18919 | 0.2425 | 0.26109 | 0.32335 | 0.33114 | 0.35959 | 0.33105 | 0.33747 | 0.36712 | 3.2358
2.176 | 111.9041 | XLarge Ret | VRF-NEW-XLarge Ret | 0.0002387 | 0.00059107 | 0.00078 | 0.0014907 | 0.0023809 | 0.0032663 | 0.0049392 | 0.0068933 | 0.011892 | 0.01814 | 0.024536 | 0.04446 | 0.059501 | 0.060939 | 0.066619 | 0.069542 | 0.061906 | 0.065256 | 0.063102 | 0.069219 | 0.63569
2.1893 | 114.8271 | Large Ret | VRF-NEW-Large Ret | 9.6042e-05 | 0.00023874 | 0.00031997 | 0.00061368 | 0.00097096 | 0.0013147 | 0.0019881 | 0.0027625 | 0.0048758 | 0.0075411 | 0.010123 | 0.018037 | 0.024076 | 0.024709 | 0.027114 | 0.028261 | 0.025256 | 0.026541 | 0.025687 | 0.028058 | 0.25858
2.155 | 107.2075 | Medium Ret | VRF-NEW-Medium Ret | 0.00035835 | 0.00088459 | 0.0011912 | 0.0022895 | 0.0036146 | 0.0048764 | 0.0072828 | 0.010145 | 0.01802 | 0.028028 | 0.037711 | 0.066636 | 0.089309 | 0.091432 | 0.1006 | 0.10486 | 0.094472 | 0.099178 | 0.095594 | 0.10446 | 0.96095
2.1071 | 96.1263 | Small Ret | VRF-NEW-Small Ret | 0.00011079 | 0.00027446 | 0.00037001 | 0.00071035 | 0.0011206 | 0.0014821 | 0.0022112 | 0.0030845 | 0.0056241 | 0.0088309 | 0.01188 | 0.020756 | 0.027755 | 0.028447 | 0.031398 | 0.032761 | 0.029585 | 0.031035 | 0.029972 | 0.032792 | 0.3002
2.0455 | 116.5856 | School K-12 | VRF-NEW-School K-12 | 0.00019687 | 0.0013199 | 0.0024821 | 0.0035263 | 0.0062615 | 0.011427 | 0.02006 | 0.04364 | 0.074769 | 0.086983 | 0.11278 | 0.14838 | 0.18276 | 0.19707 | 0.22555 | 0.22008 | 0.2618 | 0.24337 | 0.27134 | 0.25974 | 2.3736
2.0701 | 108.3165 | University | VRF-NEW-University | 0.00011308 | 0.00035993 | 0.0015391 | 0.0041393 | 0.0056715 | 0.010003 | 0.013174 | 0.028617 | 0.047838 | 0.063056 | 0.08824 | 0.11071 | 0.14131 | 0.16456 | 0.16412 | 0.16207 | 0.19533 | 0.18492 | 0.19366 | 0.20199 | 1.7814
2.1843 | 115.1134 | Warehouse | VRF-NEW-Warehouse | 4.0793e-05 | 0.00012104 | 0.0001969 | 0.00031507 | 0.00040296 | 0.00056487 | 0.001099 | 0.0017614 | 0.0025917 | 0.0033144 | 0.0043634 | 0.0049139 | 0.0050637 | 0.005989 | 0.0066916 | 0.0081152 | 0.0081964 | 0.0081271 | 0.0084071 | 0.0075786 | 0.077854
3.2899 | 68.1601 | Supermarket | VRF-NEW-Supermarket | 1.5614e-05 | 4.131e-05 | 7.8607e-05 | 0.00014673 | 0.00024848 | 0.00039182 | 0.000582 | 0.00082287 | 0.001113 | 0.0014539 | 0.0018314 | 0.0022279 | 0.0026299 | 0.0028474 | 0.0033369 | 0.0035926 | 0.0037755 | 0.0038857 | 0.0039401 | 0.0039514 | 0.036913
5.5767 | 69.9303 | MiniMart | VRF-NEW-MiniMart | 1.3439e-05 | 3.7928e-05 | 4.2636e-05 | 8.4298e-05 | 0.00012278 | 0.0001496 | 0.00019736 | 0.00027282 | 0.00050365 | 0.0008293 | 0.0011923 | 0.0021378 | 0.0026264 | 0.0027861 | 0.0032654 | 0.003266 | 0.0028646 | 0.0030463 | 0.0029717 | 0.0031751 | 0.029586
5.2756 | 69.2453 | Restaurant | VRF-NEW-Restaurant | 0.00015082 | 0.00045706 | 0.00095074 | 0.0017853 | 0.0030365 | 0.0048164 | 0.0072202 | 0.010305 | 0.014087 | 0.018542 | 0.023646 | 0.039431 | 0.052571 | 0.059355 | 0.068373 | 0.077283 | 0.073195 | 0.076516 | 0.071505 | 0.079232 | 0.68246
3.5694 | 59.0411 | Lodging | VRF-NEW-Lodging | 0.00062919 | 0.0018562 | 0.0029645 | 0.0057095 | 0.0084293 | 0.01286 | 0.018853 | 0.026881 | 0.039747 | 0.055958 | 0.081043 | 0.17229 | 0.24022 | 0.28239 | 0.32001 | 0.36429 | 0.32625 | 0.32755 | 0.31375 | 0.34014 | 2.9418
4.2671 | 91.7575 | Hospital | VRF-NEW-Hospital | 0.00021506 | 0.00055547 | 0.0010904 | 0.0017008 | 0.0020546 | 0.0028816 | 0.004009 | 0.0050508 | 0.0069719 | 0.0097101 | 0.014681 | 0.021734 | 0.02947 | 0.030323 | 0.032524 | 0.03427 | 0.033242 | 0.032483 | 0.030591 | 0.031202 | 0.32476
3.6384 | 76.9287 | Residential Care | VRF-NEW-Residential Care | 0.0031961 | 0.0086816 | 0.016694 | 0.026587 | 0.034448 | 0.050901 | 0.071159 | 0.093555 | 0.13531 | 0.1893 | 0.27589 | 0.41174 | 0.53555 | 0.55002 | 0.62597 | 0.65947 | 0.63788 | 0.64634 | 0.63321 | 0.63194 | 6.2378
3.8708 | 51.8106 | Assembly | VRF-NEW-Assembly | 0.0007517 | 0.0022433 | 0.0034966 | 0.0075665 | 0.011404 | 0.017109 | 0.017734 | 0.026819 | 0.055681 | 0.10236 | 0.14428 | 0.21722 | 0.33788 | 0.43051 | 0.51211 | 0.54233 | 0.54689 | 0.55548 | 0.56023 | 0.54913 | 4.6412
4.0111 | 49.9198 | Other | VRF-NEW-Other | 0.010065 | 0.02516 | 0.051966 | 0.091218 | 0.12149 | 0.21474 | 0.31585 | 0.49031 | 0.73088 | 0.93898 | 1.3444 | 1.7493 | 2.1177 | 2.2686 | 2.7134 | 2.6544 | 2.9132 | 2.874 | 2.7844 | 2.7246 | 27.1347
|  |  |  | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
RECOMBINE MEASURE BUNDLES INTO SUPPLY CURVE CUMULATIVE
|  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | Max
|  | lvlcost | lvlcost | aMW_2016 | aMW_2017 | aMW_2018 | aMW_2019 | aMW_2020 | aMW_2021 | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | max
| Block 1: <= 0 mills/kWh | >=-9999 | <=0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 2: <= 10 mills/kWh | >0 | <=10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 3: 10-20 mills/kWh | >10 | <=20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 4: 20-30 mills/kWh | >20 | <=30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 5: 30-40 mills/kWh | >30 | <=40 | 0.0010119 | 0.002222 | 0.0049608 | 0.010941 | 0.017975 | 0.022089 | 0.045526 | 0.057186 | 0.074669 | 0.11302 | 0.1437 | 0.18919 | 0.2425 | 0.26109 | 0.32335 | 0.33114 | 0.35959 | 0.33105 | 0.33747 | 0.36712 | 3.2358
| Block 6: 40-50 mills/kWh | >40 | <=50 | 0.011077 | 0.027382 | 0.056927 | 0.10216 | 0.13947 | 0.23683 | 0.36137 | 0.54749 | 0.80555 | 1.052 | 1.4881 | 1.9385 | 2.3602 | 2.5297 | 3.0367 | 2.9855 | 3.2728 | 3.2051 | 3.1218 | 3.0917 | 30.3705
| Block 7: 50-60 mills/kWh | >50 | <=60 | 0.012458 | 0.031482 | 0.063388 | 0.11544 | 0.1593 | 0.2668 | 0.39796 | 0.60119 | 0.90097 | 1.2103 | 1.7135 | 2.328 | 2.9383 | 3.2426 | 3.8688 | 3.8921 | 4.146 | 4.0881 | 3.9958 | 3.981 | 37.9535
| Block 8: 60-70 mills/kWh | >60 | <=70 | 0.015577 | 0.038488 | 0.078761 | 0.14925 | 0.21459 | 0.33666 | 0.53816 | 0.77806 | 1.1335 | 1.5608 | 2.1589 | 2.9233 | 3.7034 | 4.0693 | 4.8826 | 4.9452 | 5.2788 | 5.1372 | 5.0572 | 5.1385 | 48.1382
| Block 9: 70-80 mills/kWh | >70 | <=80 | 0.018773 | 0.04717 | 0.095456 | 0.17584 | 0.24904 | 0.38756 | 0.60932 | 0.87161 | 1.2688 | 1.7501 | 2.4348 | 3.3351 | 4.2389 | 4.6193 | 5.5086 | 5.6047 | 5.9167 | 5.7835 | 5.6904 | 5.7704 | 54.376
| Block 10: 80-90 mills/kWh | >80 | <=90 | 0.018773 | 0.04717 | 0.095456 | 0.17584 | 0.24904 | 0.38756 | 0.60932 | 0.87161 | 1.2688 | 1.7501 | 2.4348 | 3.3351 | 4.2389 | 4.6193 | 5.5086 | 5.6047 | 5.9167 | 5.7835 | 5.6904 | 5.7704 | 54.376
| Block 11: 90-100 mills/kWh | >90 | <=100 | 0.019099 | 0.047999 | 0.096916 | 0.17825 | 0.25221 | 0.39192 | 0.61554 | 0.87975 | 1.2814 | 1.7686 | 2.4613 | 3.3776 | 4.2961 | 4.6781 | 5.5725 | 5.6717 | 5.9795 | 5.847 | 5.751 | 5.8344 | 55.001
| Block 12: 100-110 mills/kWh | >100 | <=110 | 0.01957 | 0.049244 | 0.099646 | 0.18468 | 0.2615 | 0.4068 | 0.636 | 0.91851 | 1.3473 | 1.8597 | 2.5873 | 3.5549 | 4.5268 | 4.9341 | 5.8372 | 5.9386 | 6.2693 | 6.1311 | 6.0402 | 6.1409 | 57.7434
| Block 13: 110-120 mills/kWh | >110 | <=120 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
| Block 14: 120-130 mills/kWh | >120 | <=130 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
| Block 15: 130-140 mills/kWh | >130 | <=140 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
| Block 16: 140-150 mills/kWh | >140 | <=150 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
| Block 17: 150-160 mills/kWh | >150 | <=160 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
| Block 18: 160-170 mills/kWh | >160 | <=170 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
| Block 19: 170-180 mills/kWh | >170 | <=180 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
| Block 20: 180-190 mills/kWh | >180 | <=190 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
| Block 21: 190-200 mills/kWh | >190 | <=200 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
| Block 22: 200-210 mills/kWh | >200 | <=210 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
| Block 23: 210-220 mills/kWh | >210 | <=220 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
| Block 24: 220-230 mills/kWh | >220 | <=230 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
| Block 25: 230-240 mills/kWh | >230 | <=240 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
| Block 26: 240-250 mills/kWh | >240 | <=250 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
| Block 27: 250-260 mills/kWh | >250 | <=260 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
| Block 28: 260-270 mills/kWh | >260 | <=270 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
| Block 29: 270-280 mills/kWh | >270 | <=280 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
| Block 30: 280-290 mills/kWh | >280 | <=290 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
| Block 31: 290-300 mills/kWh | >290 | <=300 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
| Block 32: >300 mills/kWh | >300 | <=999 | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
|  |  |  | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055 | 61.089
RECOMBINE MEASURE BUNDLES INTO SUPPLY CURVE INCREMENTAL
|  |  | VRF-NEW | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | Max
|  |  |  | aMW_2016 | aMW_2017 | aMW_2018 | aMW_2019 | aMW_2020 | aMW_2021 | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | aMW_
|  | Block 1: <= 0 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 2: <= 10 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 3: 10-20 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 4: 20-30 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 5: 30-40 mills/kWh |  | 0.0010119 | 0.002222 | 0.0049608 | 0.010941 | 0.017975 | 0.022089 | 0.045526 | 0.057186 | 0.074669 | 0.11302 | 0.1437 | 0.18919 | 0.2425 | 0.26109 | 0.32335 | 0.33114 | 0.35959 | 0.33105 | 0.33747 | 0.36712 | 3.2358
|  | Block 6: 40-50 mills/kWh |  | 0.010065 | 0.02516 | 0.051966 | 0.091218 | 0.12149 | 0.21474 | 0.31585 | 0.49031 | 0.73088 | 0.93898 | 1.3444 | 1.7493 | 2.1177 | 2.2686 | 2.7134 | 2.6544 | 2.9132 | 2.874 | 2.7844 | 2.7246 | 27.1347
|  | Block 7: 50-60 mills/kWh |  | 0.0013809 | 0.0040995 | 0.0064611 | 0.013276 | 0.019833 | 0.02997 | 0.036587 | 0.053701 | 0.095428 | 0.15832 | 0.22532 | 0.38952 | 0.5781 | 0.71289 | 0.83212 | 0.90662 | 0.87313 | 0.88303 | 0.87398 | 0.88928 | 7.5831
|  | Block 8: 60-70 mills/kWh |  | 0.0031187 | 0.007006 | 0.015373 | 0.033818 | 0.055294 | 0.06986 | 0.14021 | 0.17686 | 0.23253 | 0.35047 | 0.4454 | 0.59534 | 0.76502 | 0.82664 | 1.0138 | 1.0531 | 1.1329 | 1.049 | 1.0614 | 1.1575 | 10.1846
|  | Block 9: 70-80 mills/kWh |  | 0.0031961 | 0.0086816 | 0.016694 | 0.026587 | 0.034448 | 0.050901 | 0.071159 | 0.093555 | 0.13531 | 0.1893 | 0.27589 | 0.41174 | 0.53555 | 0.55002 | 0.62597 | 0.65947 | 0.63788 | 0.64634 | 0.63321 | 0.63194 | 6.2378
|  | Block 10: 80-90 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 11: 90-100 mills/kWh |  | 0.00032585 | 0.00082993 | 0.0014604 | 0.0024111 | 0.0031752 | 0.0043637 | 0.0062201 | 0.0081353 | 0.012596 | 0.018541 | 0.026561 | 0.04249 | 0.057225 | 0.05877 | 0.063921 | 0.067031 | 0.062827 | 0.063519 | 0.060564 | 0.063994 | 0.62496
|  | Block 12: 100-110 mills/kWh |  | 0.00047143 | 0.0012445 | 0.0027303 | 0.0064288 | 0.0092862 | 0.01488 | 0.020456 | 0.038763 | 0.065858 | 0.091084 | 0.12595 | 0.17735 | 0.23062 | 0.25599 | 0.26472 | 0.26693 | 0.28981 | 0.2841 | 0.28925 | 0.30646 | 2.7424
|  | Block 13: 110-120 mills/kWh |  | 0.00057241 | 0.0022708 | 0.003779 | 0.0059457 | 0.010016 | 0.016573 | 0.028086 | 0.055057 | 0.094128 | 0.11598 | 0.1518 | 0.21579 | 0.2714 | 0.28871 | 0.32598 | 0.326 | 0.35716 | 0.3433 | 0.36854 | 0.36459 | 3.3457
|  | Block 14: 120-130 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 15: 130-140 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 16: 140-150 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 17: 150-160 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 18: 160-170 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 19: 170-180 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 20: 180-190 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 21: 190-200 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 22: 200-210 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 23: 210-220 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 24: 220-230 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 25: 230-240 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 26: 240-250 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 27: 250-260 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 28: 260-270 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 29: 270-280 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 30: 280-290 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 31: 290-300 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 32: >300 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total per Year |  | 0.020142 | 0.051515 | 0.10343 | 0.19063 | 0.27152 | 0.42338 | 0.66409 | 0.97357 | 1.4414 | 1.9757 | 2.7391 | 3.7707 | 4.7982 | 5.2228 | 6.1632 | 6.2646 | 6.6265 | 6.4744 | 6.4088 | 6.5055
|  | Total Cumulative |  | 0.020142 | 0.071657 | 0.17508 | 0.36571 | 0.63723 | 1.0606 | 1.7247 | 2.6983 | 4.1396 | 6.1153 | 8.8544 | 12.6251 | 17.4233 | 22.646 | 28.8092 | 35.0739 | 41.7004 | 48.1748 | 54.5835 | 61.089 | 61.089
|  | Ramp Rate | LO1Slow | 0.2564% | 0.769% | 1.679% | 3.16% | 5.407% | 8.625% | 13% | 18.68% | 25.7% | 33.98% | 43.26% | 53.14% | 63.06% | 72.42% | 80.64% | 87.33% | 92.33% | 95.74% | 97.82% | 98.82%
| Leftovers - cumulative |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
|  | Large Off |  | 7.8058 | 13.7536 | 19.6404 | 26.5229 | 33.149 | 38.5676 | 45.4538 | 51.4474 | 57.2467 | 63.758 | 70.2472 | 77.3148 | 85.0386 | 92.0787 | 99.7252 | 107.2052 | 114.5516 | 121.4381 | 128.2306 | 135.353
|  | Medium Off |  | 6.3199 | 10.9207 | 15.5636 | 21.0028 | 26.1025 | 29.9626 | 35.0925 | 39.3763 | 43.2292 | 47.3756 | 51.1797 | 54.872 | 58.4458 | 61.4471 | 64.4232 | 66.9764 | 69.405 | 71.4107 | 73.3346 | 75.3776
|  | Small Off |  | 1.6593 | 2.8701 | 4.1006 | 5.5285 | 6.8785 | 7.8952 | 9.2422 | 10.3713 | 11.3857 | 12.4696 | 13.4654 | 14.4339 | 15.373 | 16.1588 | 16.9402 | 17.6079 | 18.239 | 18.7663 | 19.2722 | 19.8065
|  | XLarge Ret |  | 1.7985 | 3.2818 | 4.1766 | 5.0827 | 5.9243 | 6.6432 | 7.3576 | 8.0433 | 8.89 | 9.849 | 10.8466 | 12.2849 | 13.8693 | 15.2507 | 16.5795 | 17.8389 | 18.8857 | 19.9407 | 20.9337 | 22.009
|  | Large Ret |  | 0.71922 | 1.3147 | 1.6796 | 2.0503 | 2.3915 | 2.6791 | 2.9649 | 3.238 | 3.583 | 3.9793 | 4.3884 | 4.9683 | 5.6055 | 6.1623 | 6.6998 | 7.2085 | 7.633 | 8.0595 | 8.4613 | 8.8945
|  | Medium Ret |  | 2.7261 | 4.9677 | 6.3475 | 7.7526 | 9.0428 | 10.1265 | 11.1901 | 12.2091 | 13.5046 | 15.0008 | 16.549 | 18.7257 | 21.1269 | 23.2197 | 25.246 | 27.1634 | 28.7765 | 30.3955 | 31.9143 | 33.5531
|  | Small Ret |  | 0.86204 | 1.5733 | 2.0117 | 2.4575 | 2.8666 | 3.2035 | 3.5337 | 3.8506 | 4.2641 | 4.7462 | 5.245 | 5.9384 | 6.7016 | 7.3676 | 8.0143 | 8.627 | 9.1436 | 9.6618 | 10.1488 | 10.6749
|  | School K-12 |  | 0.49253 | 1.5898 | 2.5291 | 3.2312 | 3.9487 | 4.7511 | 5.6566 | 6.9712 | 8.5208 | 9.7935 | 10.9858 | 12.1447 | 13.2244 | 14.1294 | 14.961 | 15.638 | 16.3389 | 16.9303 | 17.5509 | 18.1276
|  | University |  | 0.27954 | 0.57522 | 1.1507 | 1.9651 | 2.6072 | 3.3014 | 3.889 | 4.7408 | 5.7204 | 6.6321 | 7.5539 | 8.4083 | 9.2332 | 9.9799 | 10.5778 | 11.0704 | 11.5872 | 12.0312 | 12.4689 | 12.9121
|  | Warehouse |  | 7.6585 | 15.2355 | 20.8801 | 25.6796 | 29.2661 | 32.4168 | 36.4816 | 41.0146 | 45.8597 | 50.5431 | 55.3813 | 59.8133 | 63.6588 | 67.6165 | 71.5849 | 76.0262 | 80.267 | 84.3214 | 88.4255 | 92.0873
|  | Supermarket |  | 0.38921 | 0.73251 | 1.0316 | 1.3281 | 1.6212 | 1.9106 | 2.1952 | 2.4746 | 2.7485 | 3.0183 | 3.284 | 3.5461 | 3.8057 | 4.0495 | 4.3052 | 4.5586 | 4.8099 | 5.0591 | 5.3061 | 5.5512
|  | MiniMart |  | 0.19763 | 0.38358 | 0.47927 | 0.57976 | 0.66522 | 0.7304 | 0.78733 | 0.84199 | 0.91511 | 1.0059 | 1.1079 | 1.2563 | 1.4092 | 1.55 | 1.6976 | 1.8335 | 1.946 | 2.0612 | 2.1711 | 2.2873
|  | Restaurant |  | 0.4687 | 0.94181 | 1.3917 | 1.8392 | 2.282 | 2.7192 | 3.15 | 3.5727 | 3.9864 | 4.3908 | 4.7873 | 5.3135 | 5.8909 | 6.4458 | 7.0084 | 7.5856 | 8.0962 | 8.6064 | 9.0705 | 9.5782
|  | Lodging |  | 1.0311 | 2.0425 | 2.7782 | 3.5248 | 4.1602 | 4.7562 | 5.3202 | 5.8599 | 6.4134 | 6.9692 | 7.5588 | 8.5005 | 9.5142 | 10.4624 | 11.3473 | 12.2089 | 12.8954 | 13.5315 | 14.1115 | 14.7254
|  | Hospital |  | 4.1332 | 7.6922 | 10.8907 | 13.5404 | 15.4092 | 17.05 | 18.5614 | 19.8838 | 21.2067 | 22.5955 | 24.2379 | 26.2091 | 28.452 | 30.4537 | 32.3749 | 34.2388 | 35.9451 | 37.5508 | 39.0294 | 40.5216
|  | Residential Care |  | 4.4952 | 8.553 | 12.1047 | 15.0808 | 17.2997 | 19.3093 | 21.1152 | 22.6995 | 24.2761 | 25.8333 | 27.4731 | 29.281 | 31.0598 | 32.4797 | 33.7772 | 34.9177 | 35.8778 | 36.7608 | 37.575 | 38.3638
|  | Assembly |  | 3.1838 | 6.3486 | 8.6036 | 11.1888 | 13.4549 | 15.5719 | 17.0138 | 18.5134 | 20.742 | 23.7844 | 27.0821 | 31.0325 | 36.0902 | 41.5764 | 47.3189 | 52.8401 | 58.0389 | 63.0872 | 68.043 | 72.8389
|  | Other |  | 12.8411 | 23.5082 | 33.5368 | 42.7988 | 49.8974 | 57.5875 | 64.8581 | 72.3899 | 80.1145 | 87.121 | 94.3692 | 101.3365 | 107.7168 | 113.0293 | 118.1309 | 122.2948 | 126.2724 | 129.834 | 133.0813 | 136.1665
|  |  |  | 57.0614 | 106.2849 | 148.8966 | 191.1538 | 226.9669 | 259.1821 | 293.8631 | 327.4984 | 362.6068 | 398.8658 | 435.7426 | 475.3799 | 516.2161 | 553.4574 | 590.7123 | 625.8399 | 658.7094 | 689.4464 | 719.1285 | 748.8287
Note on B35: Kevin Smit: Includes baseline saturation

## SC-Retro
Units Methodology | Retrofit is for major retrofits of commercial buildings.
| Vintage | Retro | Stock 2016
End-Use: | Measure Bundle | VRF-Retro | Region
HVAC | Report Year | 2035 | Base
| Total Potential (aMW) | 31.3952 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
UNITS FOR EXISTING STOCK |  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
Plus Untreated New |  |  |  | FLOOR_2016 | FLOOR_2017 | FLOOR_2018 | FLOOR_2019 | FLOOR_2020 | FLOOR_2021 | FLOOR_2022 | FLOOR_2023 | FLOOR_2024 | FLOOR_2025 | FLOOR_2026 | FLOOR_2027 | FLOOR_2028 | FLOOR_2029 | FLOOR_2030 | FLOOR_2031 | FLOOR_2032 | FLOOR_2033 | FLOOR_2034 | FLOOR_2035
|  | Large Off |  | 380.0883 | 378.948 | 377.8112 | 376.6777 | 375.5477 | 374.4211 | 373.2978 | 372.1779 | 371.0614 | 369.9482 | 368.8383 | 367.7318 | 366.6286 | 365.5288 | 364.4322 | 363.3389 | 362.2489 | 361.1621 | 360.0786 | 358.9984
|  | Medium Off |  | 190.7369 | 190.1647 | 189.5942 | 189.0254 | 188.4583 | 187.8929 | 187.3293 | 186.7673 | 186.207 | 185.6483 | 185.0914 | 184.5361 | 183.9825 | 183.4306 | 182.8803 | 182.3316 | 181.7846 | 181.2393 | 180.6956 | 180.1535
|  | Small Off |  | 184.0914 | 183.5391 | 182.9885 | 182.4395 | 181.8922 | 181.3465 | 180.8025 | 180.2601 | 179.7193 | 179.1801 | 178.6426 | 178.1067 | 177.5723 | 177.0396 | 176.5085 | 175.979 | 175.451 | 174.9247 | 174.3999 | 173.8767
|  | XLarge Ret |  | 138.3573 | 137.7209 | 137.0874 | 136.4568 | 135.8291 | 135.2043 | 134.5823 | 133.9632 | 133.347 | 132.7336 | 132.123 | 131.5153 | 130.9103 | 130.3081 | 129.7087 | 129.112 | 128.5181 | 127.9269 | 127.3385 | 126.7527
|  | Large Ret |  | 208.9575 | 207.9962 | 207.0395 | 206.0871 | 205.1391 | 204.1954 | 203.2561 | 202.3212 | 201.3905 | 200.4641 | 199.542 | 198.6241 | 197.7104 | 196.8009 | 195.8956 | 194.9945 | 194.0975 | 193.2047 | 192.316 | 191.4313
|  | Medium Ret |  | 97.1157 | 96.669 | 96.2243 | 95.7816 | 95.3411 | 94.9025 | 94.4659 | 94.0314 | 93.5988 | 93.1683 | 92.7397 | 92.3131 | 91.8885 | 91.4658 | 91.045 | 90.6262 | 90.2094 | 89.7944 | 89.3813 | 88.9702
|  | Small Ret |  | 109.4797 | 108.9761 | 108.4748 | 107.9758 | 107.4791 | 106.9847 | 106.4926 | 106.0027 | 105.5151 | 105.0297 | 104.5466 | 104.0657 | 103.587 | 103.1105 | 102.6362 | 102.164 | 101.6941 | 101.2263 | 100.7606 | 100.2971
|  | School K-12 |  | 241.1176 | 240.1291 | 239.1445 | 238.164 | 237.1876 | 236.2151 | 235.2466 | 234.2821 | 233.3215 | 232.3649 | 231.4122 | 230.4634 | 229.5185 | 228.5775 | 227.6403 | 226.707 | 225.7775 | 224.8518 | 223.9299 | 223.0118
|  | University |  | 122.1534 | 121.6526 | 121.1538 | 120.6571 | 120.1624 | 119.6697 | 119.1791 | 118.6904 | 118.2038 | 117.7192 | 117.2365 | 116.7558 | 116.2771 | 115.8004 | 115.3256 | 114.8528 | 114.3819 | 113.9129 | 113.4459 | 112.9808
|  | Warehouse |  | 448.6983 | 447.0381 | 445.3841 | 443.7362 | 442.0943 | 440.4586 | 438.8289 | 437.2052 | 435.5876 | 433.9759 | 432.3702 | 430.7704 | 429.1765 | 427.5886 | 426.0065 | 424.4303 | 422.8599 | 421.2953 | 419.7365 | 418.1835
|  | Supermarket |  | 53.7209 | 53.2375 | 52.7583 | 52.2835 | 51.8129 | 51.3466 | 50.8845 | 50.4265 | 49.9727 | 49.5229 | 49.0772 | 48.6355 | 48.1978 | 47.764 | 47.3342 | 46.9082 | 46.486 | 46.0676 | 45.653 | 45.2421
|  | MiniMart |  | 22.491 | 22.3849 | 22.2792 | 22.174 | 22.0694 | 21.9652 | 21.8615 | 21.7584 | 21.6557 | 21.5534 | 21.4517 | 21.3505 | 21.2497 | 21.1494 | 21.0496 | 20.9502 | 20.8513 | 20.7529 | 20.6549 | 20.5575
|  | Restaurant |  | 51.5509 | 51.3075 | 51.0654 | 50.8243 | 50.5844 | 50.3457 | 50.1081 | 49.8715 | 49.6362 | 49.4019 | 49.1687 | 48.9366 | 48.7056 | 48.4757 | 48.2469 | 48.0192 | 47.7926 | 47.567 | 47.3425 | 47.119
|  | Lodging |  | 170.1519 | 169.7435 | 169.3361 | 168.9297 | 168.5243 | 168.1199 | 167.7164 | 167.3138 | 166.9123 | 166.5117 | 166.1121 | 165.7134 | 165.3157 | 164.9189 | 164.5231 | 164.1283 | 163.7344 | 163.3414 | 162.9494 | 162.5583
|  | Hospital |  | 105.0295 | 104.8089 | 104.5888 | 104.3692 | 104.15 | 103.9313 | 103.713 | 103.4952 | 103.2779 | 103.061 | 102.8446 | 102.6286 | 102.4131 | 102.198 | 101.9834 | 101.7692 | 101.5555 | 101.3423 | 101.1294 | 100.9171
|  | Residential Care |  | 128.7482 | 128.4392 | 128.131 | 127.8234 | 127.5167 | 127.2106 | 126.9053 | 126.6008 | 126.2969 | 125.9938 | 125.6914 | 125.3898 | 125.0888 | 124.7886 | 124.4891 | 124.1903 | 123.8923 | 123.5949 | 123.2983 | 123.0024
|  | Assembly |  | 375.9022 | 374.2157 | 372.5367 | 370.8653 | 369.2013 | 367.5448 | 365.8958 | 364.2541 | 362.6198 | 360.9929 | 359.3732 | 357.7609 | 356.1557 | 354.5577 | 352.967 | 351.3833 | 349.8068 | 348.2373 | 346.6749 | 345.1195
|  | Other |  | 342.6499 | 339.566 | 336.5099 | 333.4814 | 330.48 | 327.5057 | 324.5581 | 321.6371 | 318.7424 | 315.8737 | 313.0308 | 310.2136 | 307.4216 | 304.6549 | 301.913 | 299.1957 | 296.503 | 293.8345 | 291.1899 | 288.5692
|  |  |  | 3371.0405 | 3356.5369 | 3342.1076 | 3327.752 | 3313.4699 | 3299.2606 | 3285.1238 | 3271.059 | 3257.0658 | 3243.1437 | 3229.2923 | 3215.5112 | 3201.7999 | 3188.1581 | 3174.5852 | 3161.0809 | 3147.6447 | 3134.2763 | 3120.9752 | 3107.7411
Add the untreated new into this section
Incremental based on achievability, ramp rate, and applicability |  |  | Achievability | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 85%
| Applicability | VRF-Retro | Retro3Slow | 0.5532% | 0.8696% | 1.739% | 3.044% | 4.734% | 6.628% | 8.436% | 9.842% | 10.6% | 10.6% | 9.892% | 8.656% | 7.128% | 5.544% | 4.085% | 2.86% | 1.906% | 1.213% | 0.7385% | 0.4308%
| 2.482% | Large Off |  | 0.04436 | 0.070953 | 0.14367 | 0.25448 | 0.4016 | 0.56993 | 0.73301 | 0.86715 | 0.94476 | 0.95524 | 0.90283 | 0.7998 | 0.66763 | 0.52702 | 0.39345 | 0.27937 | 0.18882 | 0.12176 | 0.075017 | 0.044279 | 7.5738
| 6.95% | Medium Off |  | 0.062331 | 0.10093 | 0.206 | 0.36783 | 0.5858 | 0.83788 | 1.0828 | 1.2898 | 1.4124 | 1.433 | 1.3584 | 1.2052 | 1.0058 | 0.79217 | 0.58962 | 0.41683 | 0.28015 | 0.17962 | 0.10997 | 0.064504 | 10.642
| 6.95% | Small Off |  | 0.060159 | 0.095133 | 0.19094 | 0.33538 | 0.52416 | 0.73698 | 0.94032 | 1.1017 | 1.1902 | 1.1931 | 1.1168 | 0.97953 | 0.8085 | 0.63017 | 0.46495 | 0.32589 | 0.21742 | 0.13843 | 0.084264 | 0.049149 | 10.2712
| 0.495% | XLarge Ret |  | 0.0032204 | 0.0051047 | 0.010272 | 0.018009 | 0.02807 | 0.039358 | 0.050126 | 0.05852 | 0.063053 | 0.063157 | 0.059092 | 0.051847 | 0.042948 | 0.033633 | 0.024916 | 0.01753 | 0.01174 | 0.007494 | 0.0045761 | 0.0026768 | 0.53331
| 6.93% | Large Ret |  | 0.068092 | 0.10691 | 0.21345 | 0.37249 | 0.57781 | 0.80658 | 1.0233 | 1.1901 | 1.2776 | 1.2739 | 1.1859 | 1.0351 | 0.85103 | 0.66102 | 0.48623 | 0.33975 | 0.22606 | 0.14352 | 0.087161 | 0.050722 | 11.2763
| 6.93% | Medium Ret |  | 0.031647 | 0.050913 | 0.10367 | 0.1831 | 0.28751 | 0.40584 | 0.51974 | 0.61 | 0.66059 | 0.66599 | 0.62781 | 0.55505 | 0.46446 | 0.36771 | 0.27497 | 0.19518 | 0.13181 | 0.084734 | 0.052102 | 0.030674 | 5.2408
| 2.475% | Small Ret |  | 0.012741 | 0.020094 | 0.040264 | 0.070424 | 0.1095 | 0.15318 | 0.19468 | 0.22679 | 0.24386 | 0.2437 | 0.22745 | 0.19905 | 0.16425 | 0.12808 | 0.09454 | 0.066283 | 0.044246 | 0.028169 | 0.017155 | 0.010009 | 2.11
| 2.475% | School K-12 |  | 0.028061 | 0.044019 | 0.08808 | 0.15411 | 0.23946 | 0.33489 | 0.42592 | 0.49679 | 0.53579 | 0.53711 | 0.50197 | 0.43967 | 0.3624 | 0.28203 | 0.20778 | 0.14539 | 0.096824 | 0.061558 | 0.037419 | 0.021801 | 4.6916
| 2.475% | University |  | 0.014216 | 0.022306 | 0.044538 | 0.077992 | 0.12164 | 0.1705 | 0.21737 | 0.2538 | 0.27414 | 0.27524 | 0.25778 | 0.22636 | 0.18698 | 0.14584 | 0.10769 | 0.075459 | 0.050315 | 0.032031 | 0.019493 | 0.011369 | 2.3768
| 2.475% | Warehouse |  | 0.05222 | 0.083182 | 0.16853 | 0.29749 | 0.4659 | 0.65499 | 0.83632 | 0.98076 | 1.0627 | 1.0699 | 1.005 | 0.88526 | 0.7333 | 0.57297 | 0.42423 | 0.2984 | 0.20009 | 0.12801 | 0.078307 | 0.04591 | 8.7975
| 6.93% | Supermarket |  | 0.017506 | 0.027469 | 0.054799 | 0.095584 | 0.1482 | 0.2068 | 0.26235 | 0.30507 | 0.32744 | 0.32635 | 0.30356 | 0.26472 | 0.21727 | 0.16842 | 0.12365 | 0.086268 | 0.057322 | 0.036358 | 0.022059 | 0.012826 | 2.665
| 6.93% | MiniMart |  | 0.007329 | 0.011567 | 0.023217 | 0.040613 | 0.063164 | 0.088357 | 0.11226 | 0.13071 | 0.14046 | 0.14028 | 0.13086 | 0.11451 | 0.094501 | 0.073673 | 0.054383 | 0.03815 | 0.025475 | 0.016221 | 0.0098813 | 0.0057672 | 1.2109
| 0.099% | Restaurant |  | 0.00023998 | 0.00037888 | 0.00076113 | 0.0013373 | 0.0020886 | 0.0029354 | 0.0037501 | 0.0043912 | 0.0047457 | 0.0047617 | 0.0044585 | 0.0039132 | 0.0032403 | 0.0025365 | 0.0018802 | 0.0013242 | 0.00088841 | 0.00056826 | 0.00034767 | 0.00020368 | 0.039651
| 0.495% | Lodging |  | 0.0039605 | 0.0062483 | 0.012541 | 0.021988 | 0.034272 | 0.048046 | 0.061217 | 0.071487 | 0.077048 | 0.077116 | 0.07204 | 0.063104 | 0.052131 | 0.040691 | 0.030077 | 0.021113 | 0.014113 | 0.008996 | 0.0054834 | 0.0032021 | 0.68396
| 0.495% | Hospital |  | 0.0024447 | 0.003986 | 0.0082162 | 0.01476 | 0.023444 | 0.033282 | 0.042864 | 0.050543 | 0.054924 | 0.055417 | 0.052211 | 0.046204 | 0.038577 | 0.030477 | 0.022764 | 0.01614 | 0.010893 | 0.0070078 | 0.0043089 | 0.0025365 | 0.42461
| 2.475% | Residential Care |  | 0.014984 | 0.024319 | 0.05001 | 0.089594 | 0.14203 | 0.20151 | 0.25949 | 0.30584 | 0.33222 | 0.33506 | 0.31534 | 0.27836 | 0.2315 | 0.18178 | 0.1349 | 0.095033 | 0.063693 | 0.040701 | 0.024866 | 0.014552 | 2.5877
| 6.93% | Assembly |  | 0.12249 | 0.19332 | 0.38815 | 0.68031 | 1.0608 | 1.4875 | 1.8956 | 2.2103 | 2.3795 | 2.3833 | 2.2327 | 1.9622 | 1.6258 | 1.2758 | 0.94943 | 0.67161 | 0.45217 | 0.29034 | 0.17824 | 0.10484 | 20.3293
| 0.495% | Other |  | 0.0079756 | 0.012894 | 0.026345 | 0.046999 | 0.074357 | 0.10525 | 0.13564 | 0.16005 | 0.17443 | 0.17659 | 0.16655 | 0.14735 | 0.1226 | 0.096195 | 0.071323 | 0.050213 | 0.033593 | 0.021444 | 0.013082 | 0.0076422 | 1.2142
SUPPLY CURVE SAVINGS BY BUNDLE |  | VRF-Retro |  | Add the untreated new into this section 2016: aMW
Savings Per SF |  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | MAX
Busbar Savings (kWh) | lvlcost | segment | measure | aMW_2016 | aMW_2017 | aMW_2018 | aMW_2019 | aMW_2020 | aMW_2021 | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | MAX
3.9857 | 69.9954 | Large Off | VRF-Retro-Large Off | 0.020183 | 0.032283 | 0.065369 | 0.11578 | 0.18272 | 0.25931 | 0.33351 | 0.39454 | 0.42985 | 0.43462 | 0.41078 | 0.3639 | 0.30376 | 0.23979 | 0.17902 | 0.12711 | 0.085909 | 0.055398 | 0.034132 | 0.020147 | 3.446 | 7.5341
2.4076 | 70.6764 | Medium Off | VRF-Retro-Medium Off | 0.017131 | 0.027739 | 0.056617 | 0.10109 | 0.161 | 0.23028 | 0.2976 | 0.3545 | 0.38817 | 0.39384 | 0.37335 | 0.33125 | 0.27642 | 0.21772 | 0.16205 | 0.11456 | 0.076995 | 0.049368 | 0.030225 | 0.017728 | 2.9248 | 6.6025
3.5602 | 35.8449 | Small Off | VRF-Retro-Small Off | 0.024449 | 0.038663 | 0.077602 | 0.1363 | 0.21303 | 0.29952 | 0.38216 | 0.44775 | 0.48369 | 0.4849 | 0.45387 | 0.3981 | 0.32859 | 0.25611 | 0.18896 | 0.13245 | 0.088361 | 0.05626 | 0.034246 | 0.019975 | 4.1744
2.1526 | 132.4438 | XLarge Ret | VRF-Retro-XLarge Ret | 0.00079136 | 0.0012544 | 0.0025241 | 0.0044254 | 0.0068976 | 0.0096715 | 0.012318 | 0.01438 | 0.015494 | 0.01552 | 0.014521 | 0.01274 | 0.010554 | 0.0082646 | 0.0061228 | 0.0043076 | 0.0028848 | 0.0018415 | 0.0011245 | 0.00065776 | 0.13105
2.1657 | 135.8566 | Large Ret | VRF-Retro-Large Ret | 0.016834 | 0.026431 | 0.052771 | 0.092089 | 0.14285 | 0.19941 | 0.25299 | 0.29423 | 0.31585 | 0.31495 | 0.2932 | 0.25591 | 0.2104 | 0.16342 | 0.12021 | 0.083996 | 0.055889 | 0.035483 | 0.021549 | 0.01254 | 2.7878 | 5.7488
2.1319 | 126.9602 | Medium Ret | VRF-Retro-Medium Ret | 0.0077017 | 0.01239 | 0.025229 | 0.044559 | 0.069969 | 0.098766 | 0.12648 | 0.14845 | 0.16076 | 0.16208 | 0.15279 | 0.13508 | 0.11303 | 0.089487 | 0.066917 | 0.047501 | 0.032077 | 0.020621 | 0.01268 | 0.0074649 | 1.2754
2.0845 | 114.0222 | Small Ret | VRF-Retro-Small Ret | 0.0030318 | 0.0047814 | 0.0095811 | 0.016758 | 0.026055 | 0.036449 | 0.046324 | 0.053966 | 0.058027 | 0.057989 | 0.054122 | 0.047365 | 0.039083 | 0.030477 | 0.022496 | 0.015772 | 0.010529 | 0.006703 | 0.004082 | 0.0023817 | 0.50208
1.9865 | 139.6415 | School K-12 | VRF-Retro-School K-12 | 0.0063636 | 0.0099824 | 0.019974 | 0.034949 | 0.054303 | 0.075944 | 0.096589 | 0.11266 | 0.1215 | 0.1218 | 0.11383 | 0.099706 | 0.082184 | 0.063957 | 0.04712 | 0.03297 | 0.021957 | 0.01396 | 0.0084856 | 0.0049438 | 1.0639
2.0701 | 126.7607 | University | VRF-Retro-University | 0.0033594 | 0.0052711 | 0.010525 | 0.01843 | 0.028744 | 0.040291 | 0.051365 | 0.059974 | 0.06478 | 0.065041 | 0.060916 | 0.053491 | 0.044185 | 0.034462 | 0.025448 | 0.017832 | 0.01189 | 0.0075691 | 0.0046064 | 0.0026865 | 0.56166
2.9829 | 95.7151 | Warehouse | VRF-Retro-Warehouse | 0.017781 | 0.028324 | 0.057387 | 0.1013 | 0.15865 | 0.22303 | 0.28478 | 0.33396 | 0.36186 | 0.36432 | 0.34221 | 0.30144 | 0.2497 | 0.1951 | 0.14446 | 0.10161 | 0.068132 | 0.043589 | 0.026665 | 0.015633 | 2.9957
3.3204 | 79.5429 | Supermarket | VRF-Retro-Supermarket | 0.0066354 | 0.010412 | 0.020771 | 0.03623 | 0.056174 | 0.078387 | 0.09944 | 0.11563 | 0.12411 | 0.1237 | 0.11506 | 0.10034 | 0.082353 | 0.063837 | 0.046868 | 0.032699 | 0.021727 | 0.013781 | 0.0083613 | 0.0048617 | 1.0101
5.6284 | 81.5687 | MiniMart | VRF-Retro-MiniMart | 0.004709 | 0.0074322 | 0.014917 | 0.026094 | 0.040584 | 0.05677 | 0.07213 | 0.08398 | 0.090247 | 0.09013 | 0.08408 | 0.073573 | 0.060718 | 0.047335 | 0.034942 | 0.024512 | 0.016368 | 0.010422 | 0.0063489 | 0.0037055 | 0.77804
5.8389 | 72.7283 | Restaurant | VRF-Retro-Restaurant | 0.00015996 | 0.00025254 | 0.00050733 | 0.00089139 | 0.0013921 | 0.0019565 | 0.0024996 | 0.0029269 | 0.0031632 | 0.0031739 | 0.0029718 | 0.0026083 | 0.0021598 | 0.0016907 | 0.0012532 | 0.00088262 | 0.00059217 | 0.00037877 | 0.00023174 | 0.00013576 | 0.026429
3.7783 | 65.3946 | Lodging | VRF-Retro-Lodging | 0.0017082 | 0.002695 | 0.005409 | 0.009484 | 0.014782 | 0.020723 | 0.026404 | 0.030833 | 0.033232 | 0.033261 | 0.031072 | 0.027218 | 0.022485 | 0.01755 | 0.012973 | 0.0091064 | 0.0060871 | 0.0038801 | 0.0023651 | 0.0013811 | 0.295
4.2671 | 107.0478 | Hospital | VRF-Retro-Hospital | 0.0011908 | 0.0019416 | 0.0040022 | 0.0071897 | 0.01142 | 0.016212 | 0.020879 | 0.02462 | 0.026754 | 0.026994 | 0.025432 | 0.022506 | 0.018791 | 0.014846 | 0.011089 | 0.0078621 | 0.0053058 | 0.0034136 | 0.0020989 | 0.0012355 | 0.20683
3.9867 | 81.4608 | Residential Care | VRF-Retro-Residential Care | 0.0068192 | 0.011068 | 0.02276 | 0.040775 | 0.064638 | 0.091707 | 0.11809 | 0.13919 | 0.1512 | 0.15249 | 0.14351 | 0.12668 | 0.10536 | 0.082728 | 0.061396 | 0.04325 | 0.028987 | 0.018523 | 0.011317 | 0.0066227 | 1.1777
3.2062 | 76.4559 | Assembly | VRF-Retro-Assembly | 0.044833 | 0.070755 | 0.14207 | 0.249 | 0.38827 | 0.54445 | 0.69379 | 0.809 | 0.87092 | 0.8723 | 0.81718 | 0.71817 | 0.59504 | 0.46695 | 0.3475 | 0.24581 | 0.1655 | 0.10626 | 0.065238 | 0.038371 | 7.4406
4.3115 | 54.4355 | Other | VRF-Retro-Other | 0.0039254 | 0.0063461 | 0.012966 | 0.023132 | 0.036597 | 0.051802 | 0.066758 | 0.078771 | 0.085848 | 0.086914 | 0.081973 | 0.07252 | 0.060339 | 0.047345 | 0.035103 | 0.024714 | 0.016534 | 0.010554 | 0.0064384 | 0.0037613 | 0.59758
|  |  |  | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952 | 14.1366
RECOMBINE MEASURE BUNDLES INTO SUPPLY CURVE CUMULATIVE
|  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | Max
|  | lvlcost | lvlcost | aMW_2016 | aMW_2017 | aMW_2018 | aMW_2019 | aMW_2020 | aMW_2021 | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | max
| Block 1: <= 0 mills/kWh | >=-9999 | <=0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 2: <= 10 mills/kWh | >0 | <=10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 3: 10-20 mills/kWh | >10 | <=20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 4: 20-30 mills/kWh | >20 | <=30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 5: 30-40 mills/kWh | >30 | <=40 | 0.024449 | 0.038663 | 0.077602 | 0.1363 | 0.21303 | 0.29952 | 0.38216 | 0.44775 | 0.48369 | 0.4849 | 0.45387 | 0.3981 | 0.32859 | 0.25611 | 0.18896 | 0.13245 | 0.088361 | 0.05626 | 0.034246 | 0.019975 | 4.1744
| Block 6: 40-50 mills/kWh | >40 | <=50 | 0.024449 | 0.038663 | 0.077602 | 0.1363 | 0.21303 | 0.29952 | 0.38216 | 0.44775 | 0.48369 | 0.4849 | 0.45387 | 0.3981 | 0.32859 | 0.25611 | 0.18896 | 0.13245 | 0.088361 | 0.05626 | 0.034246 | 0.019975 | 4.1744
| Block 7: 50-60 mills/kWh | >50 | <=60 | 0.028375 | 0.045009 | 0.090569 | 0.15943 | 0.24962 | 0.35132 | 0.44892 | 0.52653 | 0.56954 | 0.57182 | 0.53585 | 0.47062 | 0.38893 | 0.30345 | 0.22406 | 0.15716 | 0.10489 | 0.066815 | 0.040684 | 0.023736 | 4.7719
| Block 8: 60-70 mills/kWh | >60 | <=70 | 0.050266 | 0.079987 | 0.16135 | 0.2847 | 0.44713 | 0.63135 | 0.80883 | 0.9519 | 1.0326 | 1.0397 | 0.9777 | 0.86174 | 0.71518 | 0.56079 | 0.41605 | 0.29338 | 0.19689 | 0.12609 | 0.077181 | 0.045264 | 8.513
| Block 9: 70-80 mills/kWh | >70 | <=80 | 0.11903 | 0.18915 | 0.38131 | 0.67192 | 1.054 | 1.4864 | 1.9022 | 2.234 | 2.419 | 2.4327 | 2.2863 | 2.0141 | 1.6712 | 1.311 | 0.97372 | 0.68733 | 0.4617 | 0.29589 | 0.18124 | 0.10636 | 19.915
| Block 10: 80-90 mills/kWh | >80 | <=90 | 0.13055 | 0.20765 | 0.41899 | 0.73878 | 1.1592 | 1.6349 | 2.0924 | 2.4571 | 2.6604 | 2.6753 | 2.5139 | 2.2144 | 1.8372 | 1.441 | 1.0701 | 0.75509 | 0.50706 | 0.32483 | 0.1989 | 0.11669 | 21.8707
| Block 11: 90-100 mills/kWh | >90 | <=100 | 0.14834 | 0.23597 | 0.47637 | 0.84008 | 1.3178 | 1.8579 | 2.3772 | 2.7911 | 3.0223 | 3.0396 | 2.8561 | 2.5158 | 2.0869 | 1.6361 | 1.2145 | 0.8567 | 0.57519 | 0.36842 | 0.22557 | 0.13232 | 24.8664
| Block 12: 100-110 mills/kWh | >100 | <=110 | 0.14953 | 0.23791 | 0.48037 | 0.84727 | 1.3293 | 1.8741 | 2.398 | 2.8157 | 3.0491 | 3.0666 | 2.8815 | 2.5383 | 2.1057 | 1.651 | 1.2256 | 0.86456 | 0.58049 | 0.37183 | 0.22767 | 0.13356 | 25.0732
| Block 13: 110-120 mills/kWh | >110 | <=120 | 0.15256 | 0.24269 | 0.48996 | 0.86403 | 1.3553 | 1.9106 | 2.4444 | 2.8697 | 3.1071 | 3.1246 | 2.9356 | 2.5857 | 2.1448 | 1.6815 | 1.2481 | 0.88034 | 0.59102 | 0.37854 | 0.23175 | 0.13594 | 25.5753
| Block 14: 120-130 mills/kWh | >120 | <=130 | 0.16362 | 0.26035 | 0.52571 | 0.92702 | 1.454 | 2.0497 | 2.6222 | 3.0781 | 3.3326 | 3.3517 | 3.1493 | 2.7742 | 2.302 | 1.8054 | 1.3405 | 0.94567 | 0.63499 | 0.40673 | 0.24903 | 0.14609 | 27.4123
| Block 15: 130-140 mills/kWh | >130 | <=140 | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952
| Block 16: 140-150 mills/kWh | >140 | <=150 | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952
| Block 17: 150-160 mills/kWh | >150 | <=160 | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952
| Block 18: 160-170 mills/kWh | >160 | <=170 | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952
| Block 19: 170-180 mills/kWh | >170 | <=180 | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952
| Block 20: 180-190 mills/kWh | >180 | <=190 | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952
| Block 21: 190-200 mills/kWh | >190 | <=200 | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952
| Block 22: 200-210 mills/kWh | >200 | <=210 | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952
| Block 23: 210-220 mills/kWh | >210 | <=220 | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952
| Block 24: 220-230 mills/kWh | >220 | <=230 | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952
| Block 25: 230-240 mills/kWh | >230 | <=240 | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952
| Block 26: 240-250 mills/kWh | >240 | <=250 | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952
| Block 27: 250-260 mills/kWh | >250 | <=260 | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952
| Block 28: 260-270 mills/kWh | >260 | <=270 | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952
| Block 29: 270-280 mills/kWh | >270 | <=280 | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952
| Block 30: 280-290 mills/kWh | >280 | <=290 | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952
| Block 31: 290-300 mills/kWh | >290 | <=300 | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952
| Block 32: >300 mills/kWh | >300 | <=999 | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952
|  |  |  | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423 | 31.3952
RECOMBINE MEASURE BUNDLES INTO SUPPLY CURVE INCREMENTAL
|  |  | VRF-Retro | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | Max
|  |  |  | aMW_2016 | aMW_2017 | aMW_2018 | aMW_2019 | aMW_2020 | aMW_2021 | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | aMW_
|  | Block 1: <= 0 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 2: <= 10 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 3: 10-20 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 4: 20-30 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 5: 30-40 mills/kWh |  | 0.024449 | 0.038663 | 0.077602 | 0.1363 | 0.21303 | 0.29952 | 0.38216 | 0.44775 | 0.48369 | 0.4849 | 0.45387 | 0.3981 | 0.32859 | 0.25611 | 0.18896 | 0.13245 | 0.088361 | 0.05626 | 0.034246 | 0.019975 | 4.1744
|  | Block 6: 40-50 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 7: 50-60 mills/kWh |  | 0.0039254 | 0.0063461 | 0.012966 | 0.023132 | 0.036597 | 0.051802 | 0.066758 | 0.078771 | 0.085848 | 0.086914 | 0.081973 | 0.07252 | 0.060339 | 0.047345 | 0.035103 | 0.024714 | 0.016534 | 0.010554 | 0.0064384 | 0.0037613 | 0.59758
|  | Block 8: 60-70 mills/kWh |  | 0.021892 | 0.034978 | 0.070778 | 0.12527 | 0.19751 | 0.28003 | 0.35991 | 0.42538 | 0.46309 | 0.46788 | 0.44185 | 0.39112 | 0.32625 | 0.25734 | 0.19199 | 0.13622 | 0.091996 | 0.059279 | 0.036497 | 0.021528 | 3.741
|  | Block 9: 70-80 mills/kWh |  | 0.06876 | 0.10916 | 0.21996 | 0.38721 | 0.60684 | 0.85508 | 1.0933 | 1.2821 | 1.3864 | 1.393 | 1.3086 | 1.1524 | 0.95598 | 0.75019 | 0.55767 | 0.39395 | 0.26481 | 0.16979 | 0.10406 | 0.061097 | 11.402
|  | Block 10: 80-90 mills/kWh |  | 0.011528 | 0.0185 | 0.037677 | 0.066869 | 0.10522 | 0.14848 | 0.19022 | 0.22317 | 0.24144 | 0.24262 | 0.22759 | 0.20026 | 0.16607 | 0.13006 | 0.096338 | 0.067762 | 0.045355 | 0.028946 | 0.017665 | 0.010328 | 1.9557
|  | Block 11: 90-100 mills/kWh |  | 0.017781 | 0.028324 | 0.057387 | 0.1013 | 0.15865 | 0.22303 | 0.28478 | 0.33396 | 0.36186 | 0.36432 | 0.34221 | 0.30144 | 0.2497 | 0.1951 | 0.14446 | 0.10161 | 0.068132 | 0.043589 | 0.026665 | 0.015633 | 2.9957
|  | Block 12: 100-110 mills/kWh |  | 0.0011908 | 0.0019416 | 0.0040022 | 0.0071897 | 0.01142 | 0.016212 | 0.020879 | 0.02462 | 0.026754 | 0.026994 | 0.025432 | 0.022506 | 0.018791 | 0.014846 | 0.011089 | 0.0078621 | 0.0053058 | 0.0034136 | 0.0020989 | 0.0012355 | 0.20683
|  | Block 13: 110-120 mills/kWh |  | 0.0030318 | 0.0047814 | 0.0095811 | 0.016758 | 0.026055 | 0.036449 | 0.046324 | 0.053966 | 0.058027 | 0.057989 | 0.054122 | 0.047365 | 0.039083 | 0.030477 | 0.022496 | 0.015772 | 0.010529 | 0.006703 | 0.004082 | 0.0023817 | 0.50208
|  | Block 14: 120-130 mills/kWh |  | 0.011061 | 0.017662 | 0.035754 | 0.06299 | 0.098713 | 0.13906 | 0.17785 | 0.20843 | 0.22554 | 0.22712 | 0.2137 | 0.18857 | 0.15722 | 0.12395 | 0.092365 | 0.065332 | 0.043967 | 0.02819 | 0.017286 | 0.010151 | 1.8371
|  | Block 15: 130-140 mills/kWh |  | 0.023989 | 0.037668 | 0.075269 | 0.13146 | 0.20405 | 0.28503 | 0.3619 | 0.42127 | 0.45285 | 0.45227 | 0.42155 | 0.36835 | 0.30314 | 0.23565 | 0.17345 | 0.12127 | 0.080731 | 0.051285 | 0.031159 | 0.018141 | 3.9828
|  | Block 16: 140-150 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 17: 150-160 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 18: 160-170 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 19: 170-180 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 20: 180-190 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 21: 190-200 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 22: 200-210 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 23: 210-220 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 24: 220-230 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 25: 230-240 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 26: 240-250 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 27: 250-260 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 28: 260-270 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 29: 270-280 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 30: 280-290 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 31: 290-300 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 32: >300 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total per Year |  | 0.18761 | 0.29802 | 0.60098 | 1.0585 | 1.6581 | 2.3347 | 2.9841 | 3.4994 | 3.7855 | 3.804 | 3.5709 | 3.1426 | 2.6052 | 2.0411 | 1.5139 | 1.0669 | 0.71572 | 0.45801 | 0.28019 | 0.16423
|  | Total Cumulative |  | 0.18761 | 0.48563 | 1.0866 | 2.1451 | 3.8032 | 6.1378 | 9.122 | 12.6213 | 16.4068 | 20.2108 | 23.7817 | 26.9243 | 29.5295 | 31.5705 | 33.0844 | 34.1514 | 34.8671 | 35.3251 | 35.6053 | 35.7695 | 31.3952 | -0.13933
|  | Ramp Rate | Retro3Slow | 0.5532% | 0.8696% | 1.739% | 3.044% | 4.734% | 6.628% | 8.436% | 9.842% | 10.6% | 10.6% | 9.892% | 8.656% | 7.128% | 5.544% | 4.085% | 2.86% | 1.906% | 1.213% | 0.7385% | 0.4308%
Note on B35: Kevin Smit: Includes baseline saturation

## M_Input_Out
Shaped Savings Results; By Category and sorted by TRC BC ratio
[14 empty] | Savings Allocation by Category and Month for Segments 1 | [11 empty] | Savings Allocation by Category and Month for Segments 2
Category | Measure | Busbar Savings | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Wholesale KW | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
VRF-New-Small Off |  | 3.1207 | 1.5351 | 0.30702 | 1.8421 | 1.9487 | 2.0768 | 5170.9703 | 20.4634 | 35.2743 | 1.0658 | 0.029647 | 0.00058664 | 0.19568 | 0.17595 | 0.20247 | 0.18836 | 0.19231 | 0.19036 | 0.18085 | 0.18843 | 0.17606 | 0.20074 | 0.17764 | 0.19341 | 0.083079 | 0.071379 | 0.068467 | 0.071491 | 0.070142 | 0.061548 | 0.072265 | 0.059265 | 0.072961 | 0.065531 | 0.078623 | 0.08365
VRF-New-Other |  | 4.0111 | 2.602 | 0.5204 | 3.1224 | 3.303 | 2.6694 | 6819.1906 | 30.388 | 49.9198 | 0.80817 | 0.038105 | 0.00075402 | 0.25151 | 0.22615 | 0.26024 | 0.24211 | 0.24718 | 0.24467 | 0.23244 | 0.2422 | 0.22629 | 0.25801 | 0.22833 | 0.24859 | 0.10678 | 0.091744 | 0.088002 | 0.091889 | 0.090155 | 0.079109 | 0.092884 | 0.076174 | 0.093779 | 0.084228 | 0.10106 | 0.10752
VRF-New-Assembly |  | 3.8708 | 2.5894 | 0.51788 | 3.1073 | 3.287 | 2.5761 | 7031.9817 | 31.6693 | 51.8106 | 0.78371 | 0.036773 | 0.00072766 | 0.24272 | 0.21825 | 0.25114 | 0.23364 | 0.23854 | 0.23612 | 0.22432 | 0.23373 | 0.21838 | 0.24899 | 0.22035 | 0.2399 | 0.10305 | 0.088537 | 0.084926 | 0.088676 | 0.087004 | 0.076343 | 0.089637 | 0.073511 | 0.0905 | 0.081283 | 0.097523 | 0.10376
VRF-New-Lodging |  | 3.5694 | 2.664 | 0.53281 | 3.1968 | 3.3818 | 2.3755 | 7845.7085 | 36.569 | 59.0411 | 0.70243 | 0.033909 | 0.000671 | 0.22382 | 0.20125 | 0.23159 | 0.21545 | 0.21996 | 0.21773 | 0.20685 | 0.21553 | 0.20137 | 0.2296 | 0.20319 | 0.22122 | 0.095024 | 0.081642 | 0.078312 | 0.081771 | 0.080228 | 0.070398 | 0.082656 | 0.067786 | 0.083452 | 0.074953 | 0.089928 | 0.095678
VRF-New-Supermarket |  | 3.2899 | 2.7766 | 0.55532 | 3.3319 | 3.5247 | 2.1894 | 8871.9635 | 42.7485 | 68.1601 | 0.62118 | 0.031254 | 0.00061845 | 0.20629 | 0.18549 | 0.21345 | 0.19858 | 0.20274 | 0.20068 | 0.19065 | 0.19865 | 0.1856 | 0.21162 | 0.18728 | 0.20389 | 0.087583 | 0.075249 | 0.07218 | 0.075367 | 0.073946 | 0.064885 | 0.076183 | 0.062478 | 0.076917 | 0.069084 | 0.082886 | 0.088186
VRF-New-Large Off |  | 3.4937 | 2.9802 | 0.59605 | 3.5763 | 3.7832 | 2.3251 | 8967.1516 | 43.3217 | 69.0059 | 0.61458 | 0.03319 | 0.00065676 | 0.21907 | 0.19698 | 0.22667 | 0.21088 | 0.21529 | 0.21311 | 0.20246 | 0.21096 | 0.1971 | 0.22473 | 0.19888 | 0.21652 | 0.093008 | 0.07991 | 0.076651 | 0.080036 | 0.078526 | 0.068904 | 0.080903 | 0.066348 | 0.081682 | 0.073363 | 0.088021 | 0.093648
VRF-New-Restaurant |  | 5.2756 | 4.5138 | 0.90277 | 5.4166 | 5.73 | 3.511 | 8994.0983 | 43.484 | 69.2453 | 0.61274 | 0.050119 | 0.00099175 | 0.33081 | 0.29745 | 0.34229 | 0.31844 | 0.32511 | 0.32181 | 0.30573 | 0.31856 | 0.29763 | 0.33936 | 0.30031 | 0.32696 | 0.14045 | 0.12067 | 0.11575 | 0.12086 | 0.11858 | 0.10405 | 0.12217 | 0.10019 | 0.12334 | 0.11078 | 0.13292 | 0.14141
VRF-New-Medium Off |  | 2.1104 | 1.8154 | 0.36308 | 2.1785 | 2.3045 | 1.4045 | 9042.8549 | 43.7775 | 69.6785 | 0.60944 | 0.020049 | 0.00039672 | 0.13233 | 0.11899 | 0.13692 | 0.12738 | 0.13005 | 0.12873 | 0.1223 | 0.12743 | 0.11906 | 0.13575 | 0.12013 | 0.13079 | 0.056182 | 0.04827 | 0.046301 | 0.048346 | 0.047434 | 0.041622 | 0.048869 | 0.040078 | 0.04934 | 0.044315 | 0.053169 | 0.056568
VRF-New-MiniMart |  | 5.5767 | 4.8123 | 0.96246 | 5.7748 | 6.1088 | 3.7113 | 9071.1834 | 43.9481 | 69.9303 | 0.60754 | 0.052979 | 0.0010483 | 0.34969 | 0.31442 | 0.36182 | 0.33661 | 0.34366 | 0.34018 | 0.32317 | 0.33673 | 0.31462 | 0.35872 | 0.31745 | 0.34562 | 0.14846 | 0.12755 | 0.12235 | 0.12776 | 0.12535 | 0.10999 | 0.12914 | 0.10591 | 0.13038 | 0.1171 | 0.1405 | 0.14948
VRF-New-Residential Care |  | 3.6384 | 3.2647 | 0.65294 | 3.9176 | 4.1443 | 2.1749 | 9432.4469 | 49.9118 | 76.9287 | 0.5248 | 0.034565 | 0.0004412 | 0.17244 | 0.1584 | 0.1849 | 0.17131 | 0.18005 | 0.18274 | 0.1786 | 0.19328 | 0.16945 | 0.18707 | 0.16447 | 0.17176 | 0.1349 | 0.11874 | 0.12089 | 0.12403 | 0.12746 | 0.11903 | 0.13635 | 0.12368 | 0.13258 | 0.12118 | 0.1306 | 0.13446
VRF-New-Small Ret |  | 2.1071 | 2.4093 | 0.48186 | 2.8911 | 3.0584 | 1.4023 | 12019.3081 | 61.7 | 96.1263 | 0.45852 | 0.020018 | 0.00039611 | 0.13213 | 0.11881 | 0.13671 | 0.12719 | 0.12985 | 0.12854 | 0.12211 | 0.12723 | 0.11888 | 0.13554 | 0.11995 | 0.13059 | 0.056097 | 0.048197 | 0.046231 | 0.048272 | 0.047362 | 0.041559 | 0.048795 | 0.040017 | 0.049265 | 0.044248 | 0.053088 | 0.056482
VRF-New-Hospital |  | 4.2671 | 4.5063 | 0.90126 | 5.4075 | 5.7204 | 2.5508 | 11101.2964 | 59.9606 | 91.7575 | 0.44591 | 0.040538 | 0.00051744 | 0.20224 | 0.18577 | 0.21685 | 0.20092 | 0.21116 | 0.21432 | 0.20946 | 0.22667 | 0.19873 | 0.2194 | 0.19289 | 0.20144 | 0.15821 | 0.13925 | 0.14178 | 0.14547 | 0.14949 | 0.1396 | 0.15991 | 0.14505 | 0.15549 | 0.14212 | 0.15317 | 0.1577
VRF-New-Medium Ret |  | 2.155 | 2.7197 | 0.54394 | 3.2637 | 3.4525 | 1.4342 | 13266.3956 | 69.2092 | 107.2075 | 0.41542 | 0.020473 | 0.00040512 | 0.13513 | 0.12151 | 0.13982 | 0.13008 | 0.1328 | 0.13146 | 0.12489 | 0.13013 | 0.12158 | 0.13863 | 0.12268 | 0.13356 | 0.057372 | 0.049292 | 0.047282 | 0.04937 | 0.048438 | 0.042503 | 0.049904 | 0.040927 | 0.050385 | 0.045254 | 0.054295 | 0.057767
VRF-New-University |  | 2.0701 | 2.637 | 0.52741 | 3.1644 | 3.3475 | 1.3776 | 13391.2012 | 69.9607 | 108.3165 | 0.41154 | 0.019666 | 0.00038914 | 0.1298 | 0.11671 | 0.13431 | 0.12495 | 0.12757 | 0.12627 | 0.11996 | 0.125 | 0.11679 | 0.13316 | 0.11784 | 0.12829 | 0.055109 | 0.047348 | 0.045417 | 0.047423 | 0.046528 | 0.040827 | 0.047936 | 0.039313 | 0.048398 | 0.043469 | 0.052154 | 0.055488
VRF-New-Xlarge Ret |  | 2.176 | 2.8556 | 0.57112 | 3.4267 | 3.6249 | 1.4482 | 13794.9546 | 72.3919 | 111.9041 | 0.3995 | 0.020672 | 0.00040906 | 0.13645 | 0.12269 | 0.14118 | 0.13135 | 0.1341 | 0.13274 | 0.1261 | 0.13139 | 0.12276 | 0.13997 | 0.12387 | 0.13486 | 0.05793 | 0.049772 | 0.047742 | 0.04985 | 0.04891 | 0.042917 | 0.05039 | 0.041325 | 0.050875 | 0.045694 | 0.054823 | 0.058329
VRF-New-Large Ret |  | 2.1893 | 2.9415 | 0.5883 | 3.5298 | 3.734 | 1.457 | 14123.9118 | 74.3727 | 114.8271 | 0.39019 | 0.020798 | 0.00041155 | 0.13728 | 0.12344 | 0.14204 | 0.13215 | 0.13491 | 0.13355 | 0.12687 | 0.13219 | 0.12351 | 0.14083 | 0.12462 | 0.13568 | 0.058283 | 0.050075 | 0.048032 | 0.050154 | 0.049208 | 0.043178 | 0.050697 | 0.041577 | 0.051185 | 0.045972 | 0.055157 | 0.058684
VRF-New-Warehouse |  | 2.1843 | 2.9415 | 0.5883 | 3.5298 | 3.734 | 1.4537 | 14156.138 | 74.5667 | 115.1134 | 0.38931 | 0.020751 | 0.00041062 | 0.13697 | 0.12315 | 0.14172 | 0.13184 | 0.13461 | 0.13324 | 0.12658 | 0.13189 | 0.12323 | 0.14051 | 0.12434 | 0.13537 | 0.05815 | 0.049961 | 0.047923 | 0.05004 | 0.049096 | 0.04308 | 0.050582 | 0.041482 | 0.051069 | 0.045868 | 0.055032 | 0.05855
VRF-New-School K-12 |  | 2.0455 | 2.6676 | 0.53352 | 3.2011 | 3.3863 | 1.2409 | 13709.0826 | 77.3194 | 116.5856 | 0.36646 | 0.019432 | 0.00018837 | 0.15335 | 0.14067 | 0.15482 | 0.14717 | 0.15059 | 0.14416 | 0.12755 | 0.1501 | 0.15482 | 0.15806 | 0.13236 | 0.13623 | 0.043903 | 0.032425 | 0.026602 | 0.021484 | 0.01851 | 0.016189 | 0.015869 | 0.0166 | 0.021359 | 0.016362 | 0.026613 | 0.039677

## M_Input
Data Set Name
Measure Index Name | VRF
Costs must be denominated in the same year as 'Input Cost Reference Year' = |  | 2012
| Cost inflator 2006 to 2012 | 1.1074
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105
Input Data | [7 empty] | Periodic Replacement Costs and Savings and Replacement Period | [5 empty] | Gas Inputs |  | Retro or LO | Early Retrofit Parameters
Category Name | Measure Name | Savings (kwh/yr) | Life (yrs) | Capital Cost | Annual O&M | Shape Pointer | Non-E Val ($/yr) | Cost 1 ($) | Period 1 | Cost 2 ($) | Period 2 | Cost 3 ($) | Period 3 | Savings (therms/yr) | Shape Pointer | R or L | Savings 2 (kWh) | Remaining Life (yrs) | Salvage Value ($)
VRF-New-Large Off | VRF-New-Large Off-ElecHt | 1.0891 | 20 | 0.77071 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Medium Off | VRF-New-Medium Off-ElecHt | 0.62631 | 20 | 0.5068 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Small Off | VRF-New-Small Off-ElecHt | 1.5933 | 20 | 0.70168 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Xlarge Ret | VRF-New-Xlarge Ret-ElecHt | 0.15581 | 20 | 0.14132 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Large Ret | VRF-New-Large Ret-ElecHt | 0.031144 | 20 | 0.028248 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Medium Ret | VRF-New-Medium Ret-ElecHt | 0.35298 | 20 | 0.32017 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Small Ret | VRF-New-Small Ret-ElecHt | 0.80348 | 20 | 0.72878 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-School K-12 | VRF-New-School K-12-ElecHt | 0.17161 | 20 | 0.15565 |  | Commercial-School-Vent | [9 empty] | L
VRF-New-University | VRF-New-University-ElecHt | 0.294 | 20 | 0.26667 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Warehouse | VRF-New-Warehouse-ElecHt | 0.018795 | 20 | 0.017048 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Supermarket | VRF-New-Supermarket-ElecHt | 0.28701 | 20 | 0.19395 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-MiniMart | VRF-New-MiniMart-ElecHt | 0.072472 | 20 | 0.048976 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Restaurant | VRF-New-Restaurant-ElecHt | 0.22012 | 20 | 0.14875 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Lodging | VRF-New-Lodging-ElecHt | 2.3233 | 20 | 1.6442 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Hospital | VRF-New-Hospital-ElecHt | 0.42548 | 20 | 0.3304 |  | Commercial-Healthcare-Vent | [9 empty] | L
VRF-New-Residential Care | VRF-New-Residential Care-ElecHt | 1.8075 | 20 | 1.4036 |  | Commercial-Healthcare-Vent | [9 empty] | L
VRF-New-Assembly | VRF-New-Assembly-ElecHt | 0.5659 | 20 | 0.28374 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Other | VRF-New-Other-ElecHt | 0.90092 | 20 | 0.45172 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Large Off | VRF-New-Large Off-GasHt | 2.1615 | 20 | 2.2095 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Medium Off | VRF-New-Medium Off-GasHt | 1.3372 | 20 | 1.3086 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Small Off | VRF-New-Small Off-GasHt | 1.3102 | 20 | 0.83341 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Xlarge Ret | VRF-New-Xlarge Ret-GasHt | 1.8688 | 20 | 2.7143 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Large Ret | VRF-New-Large Ret-GasHt | 2.0058 | 20 | 2.9133 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Medium Ret | VRF-New-Medium Ret-GasHt | 1.6521 | 20 | 2.3996 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Small Ret | VRF-New-Small Ret-GasHt | 1.157 | 20 | 1.6805 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-School K-12 | VRF-New-School K-12-GasHt | 1.7295 | 20 | 2.5119 |  | Commercial-School-Vent | [9 empty] | L
VRF-New-University | VRF-New-University-GasHt | 1.632 | 20 | 2.3704 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Warehouse | VRF-New-Warehouse-GasHt | 2.0135 | 20 | 2.9245 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Supermarket | VRF-New-Supermarket-GasHt | 2.7739 | 20 | 2.5826 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-MiniMart | VRF-New-MiniMart-GasHt | 5.1161 | 20 | 4.7633 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Restaurant | VRF-New-Restaurant-GasHt | 4.6884 | 20 | 4.3651 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Lodging | VRF-New-Lodging-GasHt | 0.99767 | 20 | 1.0198 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Hospital | VRF-New-Hospital-GasHt | 3.5499 | 20 | 4.1759 |  | Commercial-Healthcare-Vent | [9 empty] | L
VRF-New-Residential Care | VRF-New-Residential Care-GasHt | 1.5821 | 20 | 1.8611 |  | Commercial-Healthcare-Vent | [9 empty] | L
VRF-New-Assembly | VRF-New-Assembly-GasHt | 3.0356 | 20 | 2.3056 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | l
VRF-New-Other | VRF-New-Other-GasHt | 2.831 | 20 | 2.1503 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | l
ProCost Results
Version: | ProCost 3.0 - Beta04
Run Time: | Thursday, 19 March , 2015 at 9:19 AM
Regurgitation of ProData input parameters which were used for this run
| Run Parameters |  | Run Parameters |  |  | Marginal Cost & Conservation Load Shape Parameters | [9 empty] | Sponsor Parameters | [5 empty] | Program Parameters |  |  | Utility System Parameters
| Run Type | Electric | Run Type | Electric |  | Marginal Costs and Savings Shape File | Q:\SeventhPlan\Conservation Analysis\Global EE Inputs\MC Files\MC_AND_LOADSHAPE_v3.0_24segment-7P-D9 - NewSegValues.xlsx |  |  | 6P MidC Final (with carbon) | [6 empty] | Customer | Wholesale Elec | Retail Elec | Nat Gas |  | Program Life (yrs) | 20 |  |  | Electric | Gas
| Negative B/C Ratios | Off | Negative B/C Ratios | Off |  | Marginal Elec Avoided Cost Input Worksheet | 7P Mid |  |  | Conservation Load Shapes | [5 empty] | Real After-Tax Cost of Capital | 0.068013 | 0.043878 | 0.053289 | 0.054479 |  | Program Start Date | 2016 |  | Bulk System T&D Loss Factor | 0.0040389 | 0.01
| Admin Cost @ Category Level | On | Admin Cost @ Category Level | On |  | Elec Savings Shape Input Worksheet | GLSShapes |  |  | 6P_Gas_Final | [5 empty] | Financial Life (years) | 12 | 12 | 1 | 1 |  | Present Value Time Zero | 2016 |  | Bulk System T&D Credit ($/kw-yr)($/dailytherm-yr) | 26 | 0
| Repeat Periodic Replacement | On | Repeat Periodic Replacement | On |  | Marginal Gas Avoided Cost Input Worksheet | 7P Gas |  |  | Conservation Load Shapes | [6 empty] | Customer | Wholesale Elec | Retail Elec | Nat Gas |  | Input Cost Reference Year | 2012 |  | Bulk System T&D I2R Loss Component (%) | 0.9 | N/A
[6 empty] | Gas Savings Shape Input Worksheet | GLSShapes | [8 empty] | Sponsor Share of Initial Capital Cost | 0.35 | 0.195 | 0.455 | 0 |  | Real Discount Rate | 0.04 |  | Local System Dist Loss Factor | 0.047399 | 0
| Run Type: | Electric |  |  |  | Marginal Elec CO2 per kWh Input Worksheet | CO2 lbs per kWh .95 |  |  | CO2 lbs per therm | [5 empty] | Sponsor Share of Annual O&M | 1 | 0 | 0 | 0 |  | Capital Real Escalation Rate | 0 |  | Local System Dist Credit ($/kw-yr)($/dailytherm-yr) | 31 | 0
| Negative B/C Ratios: | False: (Converts Negative B/C Ratios) |  |  |  | Marginal Gas CO2 per therm Input Worksheet | CO2 lbs per therm |  |  | Zero Dollars per ton CO2 | [5 empty] | Sponsor Share of Periodic Replacement Cost | 1 | 0 | 0 | 0 |  | Admin Cost (as % of Initial Capital Cost) | 0.2 |  | Local System Dist I2R Loss Component (%) | 0.7 | N/A
| Admin Cost / Category Level: | True: Admin Costs added at Category Results |  |  |  | Marginal Avoided Cost CO2 Input Worksheet | Zero Dollars per ton CO2 |  |  | LineLossShapes | [5 empty] | Sponsor Share of Admin Cost |  | 0.3 | 0.7 | 0 |  | Regional Act Conservation Credit (%) | 0 |  | Risk-Mitigation Credit (mills/kWh)(mills/therm) - Retro. | 0 | 0
| Periodic O&M Treatment: | True: (Periodic O&M Repeats over measure life) |  |  |  | Line Loss Shape Input Worksheet | LineLossShapes | [8 empty] | Last Year of Non-Customer O&M & Period Replacement |  | 20 |  |  |  | Report Annual Carbon Saved for Year | 2018 |  | Risk-Mitigation Credit (mills/kWh)(mills/therm) - Lost Op. | 0 | 0
Measure Results; Sorted in same order as input
Total Results |  | Measure Input Data | [8 empty] | Savings | [5 empty] | PV Capital |  |  |  | PV Admin |  |  |  | PV O&M |  |  |  | PV Periodic Repl. |  |  |  | Total PV Capital, O&M and Periodic Repl Costs |  |  |  |  | PV Wholesale Electric Utility Costs & Benefits | [6 empty] | PV Retail Electric Utility Costs & Benefits | [6 empty] | PV Electric Utility System Costs & Benefits | [5 empty] | Electric Utility System Economics |  | Sponsor Levelized Cost (mills/kwh) |  |  |  |  | PV Regional Costs & Benefits | [15 empty] | TRC Economics |  | Physical CO2 | [6 empty] | Gas Inputs |  |  |  | PV Gas Utility System Costs & Benefits |  |  |  |  | Gas Utility System Economics
Category | Measure | Measure Life | Site Savings (kWh) | Site Savings (therms) | Capital Cost ($/unit) | Annual O&M Cost ($/unit) | PV Per. Repl. Cost ($/unit) | Load Shape (electric) | Diversified Load Factor (electric) | Wholesale Power Coincidence Factor (electric) | Wholesale Electric Energy (kWh) | Wholesale Electric Demand (kw) | Retail Electric Demand (kW) | Wholesale Gas Energy (therms/yr) | Wholesale Gas Demand (therms/day) | Retail Gas Demand (therms/day) | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Total | Wholesale Utility System Energy | Wholesale Utility System T&D Def. Cap. | Wholesale Utility System Act C-E Credit | Wholesale Utility System Risk Mitigation Benefit | Wholesale Utility System Total System Benefit | Wholesale Utility System Total Non-Consumer Cost | Wholesale Utility System B/C Ratio | Retail Utility System Energy | Retail Utility System T&D Def. Cap. | Retail Utility System Act C-E Credit | Retail Utility System Risk Mitigation Benefit | Retail Utility System Total System Benefit | Retail Utility System Total Non-Consumer Cost | Retail Utility System System B/C Ratio | Utility System Energy | Utility System T&D Def. Cap. | Utility System Act C-E Credit | Utility System Total Risk Mitigation Benefit | Utility System Total System Benefit | Utility System Total Non-Consumer Cost | Utility System Net Levelized Cost (Net of Elec T&D Capacity Benefits, Act Credit & Risk-Mitigation Benefit) in mills/kwh | Utility System System B/C Ratio | Wholesale Electric Levelized Cost | Retail Electric Levelized Cost | Natural Gas Levelized Cost | Customer Levelized Cost | Total Levelized Cost | PV Regional Electric Energy | PV Regional Gas Energy | PV Regional Electric T&D Def. Cap. | PV Regional Gas T&D Def. Cap. | PV Regional Electric System CO2 | PV Regional Gas System CO2 | PV Regional Electric System Risk-Mitigation Benefit | PV Regional Gas System Risk-Mitigation Benefit | PV Regional Non-E Value | PV Regional Act Credit | PV Regional Capital Cost | PV Regional Admin Cost | PV Regional Annual O&M Cost | PV Regional Periodic Replacement Cost | PV Total Regional Benefit | PV Total Regional Cost | TRC B/C Ratio | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | Electric System CO2 Avoided (Lifetime Tons) | Gas System CO2 Avoided (Lifetime Tons) | Total System CO2 Avoided (Lifetime Tons) | Electric System CO2 Avoided (Annual Tons in 2018) | Gas System CO2 Avoided (Annual Tons in 2018) | Total System CO2 Avoided (Annual Tons in 2018) |  | Gas Site Savings (therms) | Load Shape (gas) | Diversitfied Load Factor (gas) | Wholesale Coincidence Factor (gas) | Total Gas Utility System Energy | Gas Utility System T&D Def. Cap. | Gas Utility System Risk Mitigation Benefit | Gas Utility System Total System Benefit | Gas Utility System Total Non-Consumer Cost | Gas Utility System Net Levelized Cost (Net of Gas T&D Capacity Benefits & Risk-Mitigation Benefits) in cents/therm | Gas Utility System System B/C Ratio
VRF-New-Large Off | VRF-New-Large Off-ElecHt | 20 | 1.0891 | 0 | 0.77071 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.1705 | 0.00022004 | 0.00021845 | 0 | 0 | 0 | 0.15369 | 0.35516 | 0 | 0.31537 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15369 | 0.35516 | 0 | 0.31537 | 0.82421 | 0.6092 | 0.077751 | 0 | 0 | 0.68695 | 0.15369 | 4.4697 | 0.6092 | 0.092033 | 0 | 0 | 0.70123 | 0.35516 | 1.9744 | 0.6092 | 0.16978 | 0 | 0 | 0.77898 | 0.50885 | 21.3145 | 1.5309 | 9.6615 | 22.3262 | 0 | 19.8251 | 51.8127 | 0.6092 | 0 | 0.16978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82421 |  | 0 | 0 | 0.77898 | 0.82421 | 0.94512 | 41.1396 | 0.01112 | 0 | 0.01112 | 0.00055599 | 0 | 0.00055599 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Medium Off | VRF-New-Medium Off-ElecHt | 20 | 0.62631 | 0 | 0.5068 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.67316 | 0.00012654 | 0.00012563 | 0 | 0 | 0 | 0.10106 | 0.23354 | 0 | 0.20738 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10106 | 0.23354 | 0 | 0.20738 | 0.54199 | 0.35035 | 0.044714 | 0 | 0 | 0.39506 | 0.10106 | 3.9091 | 0.35035 | 0.052928 | 0 | 0 | 0.40328 | 0.23354 | 1.7268 | 0.35035 | 0.097643 | 0 | 0 | 0.44799 | 0.33461 | 25.9021 | 1.3389 | 11.0471 | 25.5281 | 0 | 22.6683 | 59.2435 | 0.35035 | 0 | 0.097643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54199 |  | 0 | 0 | 0.44799 | 0.54199 | 0.82658 | 48.5704 | 0.0063951 | 0 | 0.0063951 | 0.00031975 | 0 | 0.00031975 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Small Off | VRF-New-Small Off-ElecHt | 20 | 1.5933 | 0 | 0.70168 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.7125 | 0.00032193 | 0.0003196 | 0 | 0 | 0 | 0.13992 | 0.32334 | 0 | 0.28712 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13992 | 0.32334 | 0 | 0.28712 | 0.75039 | 0.89129 | 0.11375 | 0 | 0 | 1.005 | 0.13992 | 7.1828 | 0.89129 | 0.13465 | 0 | 0 | 1.0259 | 0.32334 | 3.1729 | 0.89129 | 0.2484 | 0 | 0 | 1.1397 | 0.46327 | 9.2322 | 2.4601 | 6.0122 | 13.8932 | 0 | 12.3368 | 32.2422 | 0.89129 | 0 | 0.2484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75039 |  | 0 | 0 | 1.1397 | 0.75039 | 1.5188 | 21.569 | 0.016269 | 0 | 0.016269 | 0.00081344 | 0 | 0.00081344 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Xlarge Ret | VRF-New-Xlarge Ret-ElecHt | 20 | 0.15581 | 0 | 0.14132 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.16746 | 3.148e-05 | 3.1253e-05 | 0 | 0 | 0 | 0.028182 | 0.065123 | 0 | 0.057828 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028182 | 0.065123 | 0 | 0.057828 | 0.15113 | 0.087157 | 0.011124 | 0 | 0 | 0.09828 | 0.028182 | 3.4874 | 0.087157 | 0.013167 | 0 | 0 | 0.10032 | 0.065123 | 1.5405 | 0.087157 | 0.024291 | 0 | 0 | 0.11145 | 0.093305 | 30.3245 | 1.1944 | 12.3828 | 28.6148 | 0 | 25.4093 | 66.4069 | 0.087157 | 0 | 0.024291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15113 |  | 0 | 0 | 0.11145 | 0.15113 | 0.73741 | 55.7338 | 0.0015909 | 0 | 0.0015909 | 7.9544e-05 | 0 | 7.9544e-05 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Large Ret | VRF-New-Large Ret-ElecHt | 20 | 0.031144 | 0 | 0.028248 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.033473 | 6.2925e-06 | 6.2471e-06 | 0 | 0 | 0 | 0.0056331 | 0.013017 | 0 | 0.011559 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0056331 | 0.013017 | 0 | 0.011559 | 0.030209 | 0.017421 | 0.0022234 | 0 | 0 | 0.019645 | 0.0056331 | 3.4874 | 0.017421 | 0.0026319 | 0 | 0 | 0.020053 | 0.013017 | 1.5405 | 0.017421 | 0.0048553 | 0 | 0 | 0.022277 | 0.01865 | 30.3245 | 1.1944 | 12.3828 | 28.6148 | 0 | 25.4093 | 66.4069 | 0.017421 | 0 | 0.0048553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030209 |  | 0 | 0 | 0.022277 | 0.030209 | 0.73741 | 55.7338 | 0.000318 | 0 | 0.000318 | 1.59e-05 | 0 | 1.59e-05 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Medium Ret | VRF-New-Medium Ret-ElecHt | 20 | 0.35298 | 0 | 0.32017 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.37938 | 7.1319e-05 | 7.0804e-05 | 0 | 0 | 0 | 0.063845 | 0.14754 | 0 | 0.13101 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063845 | 0.14754 | 0 | 0.13101 | 0.34239 | 0.19745 | 0.025201 | 0 | 0 | 0.22265 | 0.063845 | 3.4874 | 0.19745 | 0.02983 | 0 | 0 | 0.22728 | 0.14754 | 1.5405 | 0.19745 | 0.05503 | 0 | 0 | 0.25248 | 0.21138 | 30.3245 | 1.1944 | 12.3828 | 28.6148 | 0 | 25.4093 | 66.4069 | 0.19745 | 0 | 0.05503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34239 |  | 0 | 0 | 0.25248 | 0.34239 | 0.73741 | 55.7338 | 0.0036042 | 0 | 0.0036042 | 0.00018021 | 0 | 0.00018021 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Small Ret | VRF-New-Small Ret-ElecHt | 20 | 0.80348 | 0 | 0.72878 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.86357 | 0.00016234 | 0.00016117 | 0 | 0 | 0 | 0.14533 | 0.33583 | 0 | 0.29821 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14533 | 0.33583 | 0 | 0.29821 | 0.77937 | 0.44945 | 0.057363 | 0 | 0 | 0.50682 | 0.14533 | 3.4874 | 0.44945 | 0.0679 | 0 | 0 | 0.51735 | 0.33583 | 1.5405 | 0.44945 | 0.12526 | 0 | 0 | 0.57472 | 0.48116 | 30.3245 | 1.1944 | 12.3828 | 28.6148 | 0 | 25.4093 | 66.4069 | 0.44945 | 0 | 0.12526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77937 |  | 0 | 0 | 0.57472 | 0.77937 | 0.73741 | 55.7338 | 0.008204 | 0 | 0.008204 | 0.0004102 | 0 | 0.0004102 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-School K-12 | VRF-New-School K-12-ElecHt | 20 | 0.17161 | 0 | 0.15565 | 0 | 0 | Commercial-School-Vent |  |  | 0.18464 | 1.7004e-05 | 1.6881e-05 | 0 | 0 | 0 | 0.031039 | 0.071726 | 0 | 0.063691 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031039 | 0.071726 | 0 | 0.063691 | 0.16646 | 0.098897 | 0.0060083 | 0 | 0 | 0.10491 | 0.031039 | 3.3798 | 0.098897 | 0.007112 | 0 | 0 | 0.10601 | 0.071726 | 1.478 | 0.098897 | 0.01312 | 0 | 0 | 0.11202 | 0.10277 | 35.7246 | 1.09 | 12.3694 | 28.5838 | 0 | 25.3817 | 66.335 | 0.098897 | 0 | 0.01312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16646 |  | 0 | 0 | 0.11202 | 0.16646 | 0.67295 | 61.1064 | 0.0017541 | 0 | 0.0017541 | 8.7705e-05 | 0 | 8.7705e-05 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-University | VRF-New-University-ElecHt | 20 | 0.294 | 0 | 0.26667 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.31599 | 5.9402e-05 | 5.8973e-05 | 0 | 0 | 0 | 0.053177 | 0.12288 | 0 | 0.10912 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053177 | 0.12288 | 0 | 0.10912 | 0.28518 | 0.16446 | 0.02099 | 0 | 0 | 0.18545 | 0.053177 | 3.4874 | 0.16446 | 0.024845 | 0 | 0 | 0.1893 | 0.12288 | 1.5405 | 0.16446 | 0.045835 | 0 | 0 | 0.21029 | 0.17606 | 30.3245 | 1.1944 | 12.3828 | 28.6148 | 0 | 25.4093 | 66.4069 | 0.16446 | 0 | 0.045835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28518 |  | 0 | 0 | 0.21029 | 0.28518 | 0.73741 | 55.7338 | 0.0030019 | 0 | 0.0030019 | 0.0001501 | 0 | 0.0001501 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Warehouse | VRF-New-Warehouse-ElecHt | 20 | 0.018795 | 0 | 0.017048 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.020201 | 3.7975e-06 | 3.7701e-06 | 0 | 0 | 0 | 0.0033996 | 0.0078559 | 0 | 0.0069758 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0033996 | 0.0078559 | 0 | 0.0069758 | 0.018231 | 0.010514 | 0.0013418 | 0 | 0 | 0.011856 | 0.0033996 | 3.4874 | 0.010514 | 0.0015883 | 0 | 0 | 0.012102 | 0.0078559 | 1.5405 | 0.010514 | 0.0029302 | 0 | 0 | 0.013444 | 0.011255 | 30.3245 | 1.1944 | 12.3828 | 28.6148 | 0 | 25.4093 | 66.4069 | 0.010514 | 0 | 0.0029302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018231 |  | 0 | 0 | 0.013444 | 0.018231 | 0.73741 | 55.7338 | 0.00019191 | 0 | 0.00019191 | 9.5955e-06 | 0 | 9.5955e-06 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Supermarket | VRF-New-Supermarket-ElecHt | 20 | 0.28701 | 0 | 0.19395 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.30847 | 5.7989e-05 | 5.757e-05 | 0 | 0 | 0 | 0.038677 | 0.089377 | 0 | 0.079364 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038677 | 0.089377 | 0 | 0.079364 | 0.20742 | 0.16055 | 0.02049 | 0 | 0 | 0.18104 | 0.038677 | 4.6808 | 0.16055 | 0.024254 | 0 | 0 | 0.1848 | 0.089377 | 2.0677 | 0.16055 | 0.044745 | 0 | 0 | 0.20529 | 0.12805 | 19.8722 | 1.6032 | 9.2258 | 21.3195 | 0 | 18.9312 | 49.4765 | 0.16055 | 0 | 0.044745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20742 |  | 0 | 0 | 0.20529 | 0.20742 | 0.98975 | 38.8033 | 0.0029305 | 0 | 0.0029305 | 0.00014652 | 0 | 0.00014652 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-MiniMart | VRF-New-MiniMart-ElecHt | 20 | 0.072472 | 0 | 0.048976 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.077893 | 1.4643e-05 | 1.4537e-05 | 0 | 0 | 0 | 0.0097664 | 0.022569 | 0 | 0.02004 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0097664 | 0.022569 | 0 | 0.02004 | 0.052375 | 0.04054 | 0.005174 | 0 | 0 | 0.045714 | 0.0097664 | 4.6808 | 0.04054 | 0.0061245 | 0 | 0 | 0.046664 | 0.022569 | 2.0677 | 0.04054 | 0.011298 | 0 | 0 | 0.051839 | 0.032335 | 19.8722 | 1.6032 | 9.2258 | 21.3195 | 0 | 18.9312 | 49.4765 | 0.04054 | 0 | 0.011298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052375 |  | 0 | 0 | 0.051839 | 0.052375 | 0.98975 | 38.8033 | 0.00073999 | 0 | 0.00073999 | 3.6999e-05 | 0 | 3.6999e-05 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Restaurant | VRF-New-Restaurant-ElecHt | 20 | 0.22012 | 0 | 0.14875 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.23658 | 4.4474e-05 | 4.4153e-05 | 0 | 0 | 0 | 0.029663 | 0.068546 | 0 | 0.060867 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029663 | 0.068546 | 0 | 0.060867 | 0.15908 | 0.12313 | 0.015715 | 0 | 0 | 0.13884 | 0.029663 | 4.6808 | 0.12313 | 0.018602 | 0 | 0 | 0.14173 | 0.068546 | 2.0677 | 0.12313 | 0.034316 | 0 | 0 | 0.15745 | 0.098209 | 19.8722 | 1.6032 | 9.2258 | 21.3195 | 0 | 18.9312 | 49.4765 | 0.12313 | 0 | 0.034316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15908 |  | 0 | 0 | 0.15745 | 0.15908 | 0.98975 | 38.8033 | 0.0022475 | 0 | 0.0022475 | 0.00011238 | 0 | 0.00011238 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Lodging | VRF-New-Lodging-ElecHt | 20 | 2.3233 | 0 | 1.6442 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 2.4971 | 0.00046942 | 0.00046603 | 0 | 0 | 0 | 0.32787 | 0.75767 | 0 | 0.67279 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32787 | 0.75767 | 0 | 0.67279 | 1.7583 | 1.2996 | 0.16587 | 0 | 0 | 1.4655 | 0.32787 | 4.4697 | 1.2996 | 0.19634 | 0 | 0 | 1.496 | 0.75767 | 1.9744 | 1.2996 | 0.36221 | 0 | 0 | 1.6618 | 1.0855 | 21.3145 | 1.5309 | 9.6615 | 22.3262 | 0 | 19.8251 | 51.8127 | 1.2996 | 0 | 0.36221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7583 |  | 0 | 0 | 1.6618 | 1.7583 | 0.94512 | 41.1396 | 0.023723 | 0 | 0.023723 | 0.0011861 | 0 | 0.0011861 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Hospital | VRF-New-Hospital-ElecHt | 20 | 0.42548 | 0 | 0.3304 | 0 | 0 | Commercial-Healthcare-Vent |  |  | 0.4567 | 5.5381e-05 | 5.4981e-05 | 0 | 0 | 0 | 0.065886 | 0.15225 | 0 | 0.1352 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065886 | 0.15225 | 0 | 0.1352 | 0.35334 | 0.23027 | 0.019569 | 0 | 0 | 0.24984 | 0.065886 | 3.792 | 0.23027 | 0.023163 | 0 | 0 | 0.25343 | 0.15225 | 1.6646 | 0.23027 | 0.042732 | 0 | 0 | 0.273 | 0.21814 | 28.2609 | 1.2515 | 10.6153 | 24.5304 | 0 | 21.7824 | 56.9281 | 0.23027 | 0 | 0.042732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35334 |  | 0 | 0 | 0.273 | 0.35334 | 0.77265 | 50.0433 | 0.0043387 | 0 | 0.0043387 | 0.00021693 | 0 | 0.00021693 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Residential Care | VRF-New-Residential Care-ElecHt | 20 | 1.8075 | 0 | 1.4036 | 0 | 0 | Commercial-Healthcare-Vent |  |  | 1.9402 | 0.00023527 | 0.00023357 | 0 | 0 | 0 | 0.2799 | 0.6468 | 0 | 0.57434 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2799 | 0.6468 | 0 | 0.57434 | 1.501 | 0.97824 | 0.083132 | 0 | 0 | 1.0614 | 0.2799 | 3.792 | 0.97824 | 0.098403 | 0 | 0 | 1.0766 | 0.6468 | 1.6646 | 0.97824 | 0.18153 | 0 | 0 | 1.1598 | 0.9267 | 28.2609 | 1.2515 | 10.6153 | 24.5304 | 0 | 21.7824 | 56.9281 | 0.97824 | 0 | 0.18153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.501 |  | 0 | 0 | 1.1598 | 1.501 | 0.77265 | 50.0433 | 0.018432 | 0 | 0.018432 | 0.00092157 | 0 | 0.00092157 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Assembly | VRF-New-Assembly-ElecHt | 20 | 0.5659 | 0 | 0.28374 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.60822 | 0.00011434 | 0.00011351 | 0 | 0 | 0 | 0.056581 | 0.13075 | 0 | 0.1161 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056581 | 0.13075 | 0 | 0.1161 | 0.30344 | 0.31655 | 0.040401 | 0 | 0 | 0.35696 | 0.056581 | 6.3087 | 0.31655 | 0.047823 | 0 | 0 | 0.36438 | 0.13075 | 2.7868 | 0.31655 | 0.088224 | 0 | 0 | 0.40478 | 0.18733 | 11.99 | 2.1608 | 6.8451 | 15.818 | 0 | 14.046 | 36.7091 | 0.31655 | 0 | 0.088224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30344 |  | 0 | 0 | 0.40478 | 0.30344 | 1.334 | 26.036 | 0.0057782 | 0 | 0.0057782 | 0.00028891 | 0 | 0.00028891 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Other | VRF-New-Other-ElecHt | 20 | 0.90092 | 0 | 0.45172 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.96831 | 0.00018203 | 0.00018071 | 0 | 0 | 0 | 0.090079 | 0.20816 | 0 | 0.18484 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.090079 | 0.20816 | 0 | 0.18484 | 0.48308 | 0.50396 | 0.06432 | 0 | 0 | 0.56828 | 0.090079 | 6.3087 | 0.50396 | 0.076135 | 0 | 0 | 0.5801 | 0.20816 | 2.7868 | 0.50396 | 0.14045 | 0 | 0 | 0.64442 | 0.29824 | 11.99 | 2.1608 | 6.8451 | 15.818 | 0 | 14.046 | 36.7091 | 0.50396 | 0 | 0.14045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48308 |  | 0 | 0 | 0.64442 | 0.48308 | 1.334 | 26.036 | 0.009199 | 0 | 0.009199 | 0.00045995 | 0 | 0.00045995 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Large Off | VRF-New-Large Off-GasHt | 20 | 2.1615 | 0 | 2.2095 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 2.3232 | 0.00043672 | 0.00043357 | 0 | 0 | 0 | 0.44061 | 1.0182 | 0 | 0.90411 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44061 | 1.0182 | 0 | 0.90411 | 2.3629 | 1.2091 | 0.15431 | 0 | 0 | 1.3634 | 0.44061 | 3.0944 | 1.2091 | 0.18266 | 0 | 0 | 1.3918 | 1.0182 | 1.3669 | 1.2091 | 0.33698 | 0 | 0 | 1.5461 | 1.4588 | 35.5312 | 1.0598 | 13.9555 | 32.2489 | 0 | 28.6362 | 74.8406 | 1.2091 | 0 | 0.33698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3629 |  | 0 | 0 | 1.5461 | 2.3629 | 0.65432 | 64.1674 | 0.02207 | 0 | 0.02207 | 0.0011035 | 0 | 0.0011035 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Medium Off | VRF-New-Medium Off-GasHt | 20 | 1.3372 | 0 | 1.3086 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.4372 | 0.00027017 | 0.00026822 | 0 | 0 | 0 | 0.26095 | 0.60303 | 0 | 0.53547 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26095 | 0.60303 | 0 | 0.53547 | 1.3995 | 0.748 | 0.095465 | 0 | 0 | 0.84347 | 0.26095 | 3.2322 | 0.748 | 0.113 | 0 | 0 | 0.861 | 0.60303 | 1.4278 | 0.748 | 0.20847 | 0 | 0 | 0.95647 | 0.86398 | 33.561 | 1.1071 | 13.3604 | 30.8738 | 0 | 27.4151 | 71.6492 | 0.748 | 0 | 0.20847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3995 |  | 0 | 0 | 0.95647 | 1.3995 | 0.68346 | 60.9761 | 0.013654 | 0 | 0.013654 | 0.00068267 | 0 | 0.00068267 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Small Off | VRF-New-Small Off-GasHt | 20 | 1.3102 | 0 | 0.83341 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.4082 | 0.00026472 | 0.0002628 | 0 | 0 | 0 | 0.16619 | 0.38405 | 0 | 0.34102 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16619 | 0.38405 | 0 | 0.34102 | 0.89127 | 0.73289 | 0.093537 | 0 | 0 | 0.82643 | 0.16619 | 4.9727 | 0.73289 | 0.11072 | 0 | 0 | 0.84361 | 0.38405 | 2.1966 | 0.73289 | 0.20426 | 0 | 0 | 0.93715 | 0.55024 | 18.079 | 1.7032 | 8.6842 | 20.0679 | 0 | 17.8198 | 46.572 | 0.73289 | 0 | 0.20426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89127 |  | 0 | 0 | 0.93715 | 0.89127 | 1.0515 | 35.8988 | 0.013378 | 0 | 0.013378 | 0.00066888 | 0 | 0.00066888 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Xlarge Ret | VRF-New-Xlarge Ret-GasHt | 20 | 1.8688 | 0 | 2.7143 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 2.0086 | 0.00037758 | 0.00037486 | 0 | 0 | 0 | 0.54126 | 1.2508 | 0 | 1.1107 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54126 | 1.2508 | 0 | 1.1107 | 2.9027 | 1.0454 | 0.13342 | 0 | 0 | 1.1788 | 0.54126 | 2.1778 | 1.0454 | 0.15793 | 0 | 0 | 1.2033 | 1.2508 | 0.96204 | 1.0454 | 0.29134 | 0 | 0 | 1.3367 | 1.792 | 54.9767 | 0.74592 | 19.8287 | 45.8212 | 0 | 40.688 | 106.3379 | 1.0454 | 0 | 0.29134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9027 |  | 0 | 0 | 1.3367 | 2.9027 | 0.46051 | 95.6647 | 0.019081 | 0 | 0.019081 | 0.00095406 | 0 | 0.00095406 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Large Ret | VRF-New-Large Ret-GasHt | 20 | 2.0058 | 0 | 2.9133 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 2.1558 | 0.00040526 | 0.00040234 | 0 | 0 | 0 | 0.58094 | 1.3425 | 0 | 1.1921 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58094 | 1.3425 | 0 | 1.1921 | 3.1155 | 1.122 | 0.1432 | 0 | 0 | 1.2652 | 0.58094 | 2.1778 | 1.122 | 0.1695 | 0 | 0 | 1.2915 | 1.3425 | 0.96204 | 1.122 | 0.3127 | 0 | 0 | 1.4347 | 1.9234 | 54.9767 | 0.74592 | 19.8287 | 45.8212 | 0 | 40.688 | 106.3379 | 1.122 | 0 | 0.3127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1155 |  | 0 | 0 | 1.4347 | 3.1155 | 0.46051 | 95.6647 | 0.02048 | 0 | 0.02048 | 0.001024 | 0 | 0.001024 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Medium Ret | VRF-New-Medium Ret-GasHt | 20 | 1.6521 | 0 | 2.3996 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.7757 | 0.0003338 | 0.00033139 | 0 | 0 | 0 | 0.4785 | 1.1057 | 0 | 0.98188 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4785 | 1.1057 | 0 | 0.98188 | 2.5661 | 0.92416 | 0.11795 | 0 | 0 | 1.0421 | 0.4785 | 2.1778 | 0.92416 | 0.13962 | 0 | 0 | 1.0638 | 1.1057 | 0.96204 | 0.92416 | 0.25756 | 0 | 0 | 1.1817 | 1.5843 | 54.9767 | 0.74592 | 19.8287 | 45.8212 | 0 | 40.688 | 106.3379 | 0.92416 | 0 | 0.25756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5661 |  | 0 | 0 | 1.1817 | 2.5661 | 0.46051 | 95.6647 | 0.016869 | 0 | 0.016869 | 0.00084344 | 0 | 0.00084344 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Small Ret | VRF-New-Small Ret-GasHt | 20 | 1.157 | 0 | 1.6805 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.2436 | 0.00023377 | 0.00023209 | 0 | 0 | 0 | 0.33512 | 0.7744 | 0 | 0.68765 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33512 | 0.7744 | 0 | 0.68765 | 1.7972 | 0.64723 | 0.082604 | 0 | 0 | 0.72983 | 0.33512 | 2.1778 | 0.64723 | 0.097778 | 0 | 0 | 0.74501 | 0.7744 | 0.96204 | 0.64723 | 0.18038 | 0 | 0 | 0.82761 | 1.1095 | 54.9767 | 0.74592 | 19.8287 | 45.8212 | 0 | 40.688 | 106.3379 | 0.64723 | 0 | 0.18038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7972 |  | 0 | 0 | 0.82761 | 1.7972 | 0.46051 | 95.6647 | 0.011814 | 0 | 0.011814 | 0.0005907 | 0 | 0.0005907 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-School K-12 | VRF-New-School K-12-GasHt | 20 | 1.7295 | 0 | 2.5119 | 0 | 0 | Commercial-School-Vent |  |  | 1.8608 | 0.00017137 | 0.00017013 | 0 | 0 | 0 | 0.50091 | 1.1575 | 0 | 1.0279 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50091 | 1.1575 | 0 | 1.0279 | 2.6863 | 0.99669 | 0.060552 | 0 | 0 | 1.0572 | 0.50091 | 2.1106 | 0.99669 | 0.071676 | 0 | 0 | 1.0684 | 1.1575 | 0.92297 | 0.99669 | 0.13223 | 0 | 0 | 1.1289 | 1.6584 | 60.3501 | 0.68071 | 19.8072 | 45.7715 | 0 | 40.6439 | 106.2227 | 0.99669 | 0 | 0.13223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6863 |  | 0 | 0 | 1.1289 | 2.6863 | 0.42025 | 100.994 | 0.017678 | 0 | 0.017678 | 0.0008839 | 0 | 0.0008839 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-University | VRF-New-University-GasHt | 20 | 1.632 | 0 | 2.3704 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.7541 | 0.00032974 | 0.00032736 | 0 | 0 | 0 | 0.47268 | 1.0923 | 0 | 0.96993 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47268 | 1.0923 | 0 | 0.96993 | 2.5349 | 0.91292 | 0.11651 | 0 | 0 | 1.0294 | 0.47268 | 2.1778 | 0.91292 | 0.13792 | 0 | 0 | 1.0508 | 1.0923 | 0.96204 | 0.91292 | 0.25443 | 0 | 0 | 1.1673 | 1.565 | 54.9767 | 0.74592 | 19.8287 | 45.8212 | 0 | 40.688 | 106.3379 | 0.91292 | 0 | 0.25443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5349 |  | 0 | 0 | 1.1673 | 2.5349 | 0.46051 | 95.6647 | 0.016664 | 0 | 0.016664 | 0.00083318 | 0 | 0.00083318 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Warehouse | VRF-New-Warehouse-GasHt | 20 | 2.0135 | 0 | 2.9245 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 2.1641 | 0.00040682 | 0.00040388 | 0 | 0 | 0 | 0.58318 | 1.3476 | 0 | 1.1967 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58318 | 1.3476 | 0 | 1.1967 | 3.1275 | 1.1263 | 0.14375 | 0 | 0 | 1.2701 | 0.58318 | 2.1778 | 1.1263 | 0.17016 | 0 | 0 | 1.2965 | 1.3476 | 0.96204 | 1.1263 | 0.3139 | 0 | 0 | 1.4402 | 1.9308 | 54.9767 | 0.74592 | 19.8287 | 45.8212 | 0 | 40.688 | 106.3379 | 1.1263 | 0 | 0.3139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1275 |  | 0 | 0 | 1.4402 | 3.1275 | 0.46051 | 95.6647 | 0.020559 | 0 | 0.020559 | 0.0010279 | 0 | 0.0010279 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Supermarket | VRF-New-Supermarket-GasHt | 20 | 2.7739 | 0 | 2.5826 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 2.9814 | 0.00056046 | 0.00055642 | 0 | 0 | 0 | 0.51501 | 1.1901 | 0 | 1.0568 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51501 | 1.1901 | 0 | 1.0568 | 2.7619 | 1.5517 | 0.19804 | 0 | 0 | 1.7497 | 0.51501 | 3.3974 | 1.5517 | 0.23442 | 0 | 0 | 1.7861 | 1.1901 | 1.5008 | 1.5517 | 0.43246 | 0 | 0 | 1.9842 | 1.7051 | 31.41 | 1.1636 | 12.7107 | 29.3725 | 0 | 26.082 | 68.1652 | 1.5517 | 0 | 0.43246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7619 |  | 0 | 0 | 1.9842 | 2.7619 | 0.71839 | 57.492 | 0.028324 | 0 | 0.028324 | 0.0014162 | 0 | 0.0014162 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-MiniMart | VRF-New-MiniMart-GasHt | 20 | 5.1161 | 0 | 4.7633 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 5.4988 | 0.0010337 | 0.0010262 | 0 | 0 | 0 | 0.94987 | 2.195 | 0 | 1.9491 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94987 | 2.195 | 0 | 1.9491 | 5.094 | 2.8619 | 0.36525 | 0 | 0 | 3.2271 | 0.94987 | 3.3974 | 2.8619 | 0.43235 | 0 | 0 | 3.2942 | 2.195 | 1.5008 | 2.8619 | 0.79761 | 0 | 0 | 3.6595 | 3.1449 | 31.41 | 1.1636 | 12.7107 | 29.3725 | 0 | 26.082 | 68.1652 | 2.8619 | 0 | 0.79761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.094 |  | 0 | 0 | 3.6595 | 5.094 | 0.71839 | 57.492 | 0.052239 | 0 | 0.052239 | 0.0026119 | 0 | 0.0026119 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Restaurant | VRF-New-Restaurant-GasHt | 20 | 4.6884 | 0 | 4.3651 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 5.039 | 0.00094727 | 0.00094044 | 0 | 0 | 0 | 0.87046 | 2.0115 | 0 | 1.7862 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87046 | 2.0115 | 0 | 1.7862 | 4.6681 | 2.6226 | 0.33472 | 0 | 0 | 2.9573 | 0.87046 | 3.3974 | 2.6226 | 0.39621 | 0 | 0 | 3.0188 | 2.0115 | 1.5008 | 2.6226 | 0.73092 | 0 | 0 | 3.3535 | 2.882 | 31.41 | 1.1636 | 12.7107 | 29.3725 | 0 | 26.082 | 68.1652 | 2.6226 | 0 | 0.73092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6681 |  | 0 | 0 | 3.3535 | 4.6681 | 0.71839 | 57.492 | 0.047871 | 0 | 0.047871 | 0.0023935 | 0 | 0.0023935 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Lodging | VRF-New-Lodging-GasHt | 20 | 0.99767 | 0 | 1.0198 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.0723 | 0.00020158 | 0.00020012 | 0 | 0 | 0 | 0.20337 | 0.46996 | 0 | 0.41731 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20337 | 0.46996 | 0 | 0.41731 | 1.0906 | 0.55808 | 0.071227 | 0 | 0 | 0.62931 | 0.20337 | 3.0944 | 0.55808 | 0.084311 | 0 | 0 | 0.64239 | 0.46996 | 1.3669 | 0.55808 | 0.15554 | 0 | 0 | 0.71362 | 0.67333 | 35.5312 | 1.0598 | 13.9555 | 32.2489 | 0 | 28.6362 | 74.8406 | 0.55808 | 0 | 0.15554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0906 |  | 0 | 0 | 0.71362 | 1.0906 | 0.65432 | 64.1674 | 0.010187 | 0 | 0.010187 | 0.00050934 | 0 | 0.00050934 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Hospital | VRF-New-Hospital-GasHt | 20 | 3.5499 | 0 | 4.1759 | 0 | 0 | Commercial-Healthcare-Vent |  |  | 3.8104 | 0.00046206 | 0.00045872 | 0 | 0 | 0 | 0.83273 | 1.9243 | 0 | 1.7087 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83273 | 1.9243 | 0 | 1.7087 | 4.4658 | 1.9212 | 0.16327 | 0 | 0 | 2.0845 | 0.83273 | 2.5032 | 1.9212 | 0.19326 | 0 | 0 | 2.1145 | 1.9243 | 1.0988 | 1.9212 | 0.35653 | 0 | 0 | 2.2777 | 2.757 | 46.3559 | 0.82616 | 16.0807 | 37.1601 | 0 | 32.9972 | 86.238 | 1.9212 | 0 | 0.35653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4658 |  | 0 | 0 | 2.2777 | 4.4658 | 0.51005 | 79.3531 | 0.036199 | 0 | 0.036199 | 0.0018099 | 0 | 0.0018099 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Residential Care | VRF-New-Residential Care-GasHt | 20 | 1.5821 | 0 | 1.8611 | 0 | 0 | Commercial-Healthcare-Vent |  |  | 1.6982 | 0.00020593 | 0.00020444 | 0 | 0 | 0 | 0.37113 | 0.85762 | 0 | 0.76154 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37113 | 0.85762 | 0 | 0.76154 | 1.9903 | 0.85624 | 0.072764 | 0 | 0 | 0.92901 | 0.37113 | 2.5032 | 0.85624 | 0.086131 | 0 | 0 | 0.94238 | 0.85762 | 1.0988 | 0.85624 | 0.1589 | 0 | 0 | 1.0151 | 1.2287 | 46.3559 | 0.82616 | 16.0807 | 37.1601 | 0 | 32.9972 | 86.238 | 0.85624 | 0 | 0.1589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9903 |  | 0 | 0 | 1.0151 | 1.9903 | 0.51005 | 79.3531 | 0.016133 | 0 | 0.016133 | 0.00080664 | 0 | 0.00080664 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Assembly | VRF-New-Assembly-GasHt | 20 | 3.0356 | 0 | 2.3056 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 3.2626 | 0.00061332 | 0.0006089 | 0 | 0 | 0 | 0.45978 | 1.0625 | 0 | 0.94345 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45978 | 1.0625 | 0 | 0.94345 | 2.4657 | 1.698 | 0.21672 | 0 | 0 | 1.9148 | 0.45978 | 4.1646 | 1.698 | 0.25653 | 0 | 0 | 1.9546 | 1.0625 | 1.8397 | 1.698 | 0.47325 | 0 | 0 | 2.1713 | 1.5222 | 23.6582 | 1.4264 | 10.3694 | 23.962 | 0 | 21.2777 | 55.609 | 1.698 | 0 | 0.47325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4657 |  | 0 | 0 | 2.1713 | 2.4657 | 0.8806 | 44.9359 | 0.030995 | 0 | 0.030995 | 0.0015497 | 0 | 0.0015497 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Other | VRF-New-Other-GasHt | 20 | 2.831 | 0 | 2.1503 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 3.0427 | 0.00057199 | 0.00056787 | 0 | 0 | 0 | 0.42879 | 0.99087 | 0 | 0.87987 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42879 | 0.99087 | 0 | 0.87987 | 2.2995 | 1.5836 | 0.20211 | 0 | 0 | 1.7857 | 0.42879 | 4.1646 | 1.5836 | 0.23924 | 0 | 0 | 1.8229 | 0.99087 | 1.8397 | 1.5836 | 0.44136 | 0 | 0 | 2.025 | 1.4197 | 23.6582 | 1.4264 | 10.3694 | 23.962 | 0 | 21.2777 | 55.609 | 1.5836 | 0 | 0.44136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2995 |  | 0 | 0 | 2.025 | 2.2995 | 0.8806 | 44.9359 | 0.028906 | 0 | 0.028906 | 0.0014453 | 0 | 0.0014453 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Category Results; Sorted by TRC Levelized Cost
Total Results |  | Measure Input Data | [8 empty] | Savings | [5 empty] | PV Capital |  |  |  | PV Admin |  |  |  | PV O&M |  |  |  | PV Periodic Repl. |  |  |  | Total PV Capital, O&M and Periodic Repl Costs |  |  |  |  | PV Wholesale Electric Utility Costs & Benefits | [6 empty] | PV Retail Electric Utility Costs & Benefits | [6 empty] | PV Electric Utility System Costs & Benefits | [5 empty] | Electric Utility System Economics |  | Sponsor Levelized Cost (mills/kwh) |  |  |  |  | PV Regional Costs & Benefits | [15 empty] | TRC Economics |  | Physical CO2 | [6 empty] | Gas Inputs |  |  |  | PV Gas Utility System Costs & Benefits |  |  |  |  | Gas Utility System Economics
Category | Measure | Measure Life | Site Savings (kWh) | Site Savings (therms) | Capital Cost ($/unit) | Annual O&M Cost ($/unit) | PV Per. Repl. Cost ($/unit) | Load Shape (electric) | Diversified Load Factor (electric) | Wholesale Power Coincidence Factor (electric) | Wholesale Electric Energy (kWh) | Wholesale Electric Demand (kw) | Retail Electric Demand (kW) | Wholesale Gas Energy (therms/yr) | Wholesale Gas Demand (therms/day) | Retail Gas Demand (therms/day) | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Total | Wholesale Utility System Energy | Wholesale Utility System T&D Def. Cap. | Wholesale Utility System Act C-E Credit | Wholesale Utility System Risk Mitigation Benefit | Wholesale Utility System Total System Benefit | Wholesale Utility System Total Non-Consumer Cost | Wholesale Utility System B/C Ratio | Retail Utility System Energy | Retail Utility System T&D Def. Cap. | Retail Utility System Act C-E Credit | Retail Utility System Risk Mitigation Benefit | Retail Utility System Total System Benefit | Retail Utility System Total Non-Consumer Cost | Retail Utility System System B/C Ratio | Utility System Energy | Utility System T&D Def. Cap. | Utility System Act C-E Credit | Utility System Total Risk Mitigation Benefit | Utility System Total System Benefit | Utility System Total Non-Consumer Cost | Utility System Net Levelized Cost (Net of Elec T&D Capacity Benefits, Act Credit & Risk-Mitigation Benefit) in mills/kwh | Utility System System B/C Ratio | Wholesale Electric Levelized Cost | Retail Electric Levelized Cost | Natural Gas Levelized Cost | Customer Levelized Cost | Total Levelized Cost | PV Regional Electric Energy | PV Regional Gas Energy | PV Regional Electric T&D Def. Cap. | PV Regional Gas T&D Def. Cap. | PV Regional Electric System CO2 | PV Regional Gas System CO2 | PV Regional Electric System Risk-Mitigation Benefit | PV Regional Gas System Risk-Mitigation Benefit | PV Regional Non-E Value | PV Regional Act Credit | PV Regional Capital Cost | PV Regional Admin Cost | PV Regional Annual O&M Cost | PV Regional Periodic Replacement Cost | PV Total Regional Benefit | PV Total Regional Cost | TRC B/C Ratio | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | Electric System CO2 Avoided (Lifetime Tons) | Gas System CO2 Avoided (Lifetime Tons) | Total System CO2 Avoided (Lifetime Tons) | Electric System CO2 Avoided (Annual Tons in 2018) | Gas System CO2 Avoided (Annual Tons in 2018) | Total System CO2 Avoided (Annual Tons in 2018) |  | Gas Site Savings (therms) | Load Shape (gas) | Diversitfied Load Factor (gas) | Wholesale Coincidence Factor (gas) | Total Gas Utility System Energy | Gas Utility System T&D Def. Cap. | Gas Utility System Risk Mitigation Benefit | Gas Utility System Total System Benefit | Gas Utility System Total Non-Consumer Cost | Gas Utility System Net Levelized Cost (Net of Gas T&D Capacity Benefits & Risk-Mitigation Benefits) in cents/therm | Gas Utility System System B/C Ratio
VRF-New-Small Off |  | 20 | 2.9035 | 0 | 1.5351 | 0 | 0 |  |  |  | 3.1207 | 0.00058664 | 0.00058241 | 0 | 0 | 0 | 0.30612 | 0.70739 | 0 | 0.62814 | 0.092105 | 0.21491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39822 | 0.9223 | 0 | 0.62814 | 1.9487 | 1.6242 | 0.20729 | 0 | 0 | 1.8315 | 0.39822 | 4.5991 | 1.6242 | 0.24537 | 0 | 0 | 1.8695 | 0.9223 | 2.027 | 1.6242 | 0.45266 | 0 | 0 | 2.0768 | 1.3205 | 20.4634 | 1.5727 | 9.3896 | 21.7469 | 0 | 14.811 | 45.9475 | 1.6242 | 0 | 0.45266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6417 | 0.30702 | 0 | 0 | 2.0768 | 1.9487 | 1.0658 | 35.2743 | 0.029647 | 0 | 0.029647 | 0.0014823 | 0 | 0.0014823 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Other |  | 20 | 3.7319 | 0 | 2.602 | 0 | 0 |  |  |  | 4.0111 | 0.00075402 | 0.00074858 | 0 | 0 | 0 | 0.51887 | 1.199 | 0 | 1.0647 | 0.15612 | 0.36428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67499 | 1.5633 | 0 | 1.0647 | 3.303 | 2.0876 | 0.26643 | 0 | 0 | 2.354 | 0.67499 | 3.4875 | 2.0876 | 0.31538 | 0 | 0 | 2.403 | 1.5633 | 1.5371 | 2.0876 | 0.58181 | 0 | 0 | 2.6694 | 2.2383 | 30.388 | 1.1926 | 12.3825 | 28.6786 | 0 | 19.5319 | 60.593 | 2.0876 | 0 | 0.58181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7826 | 0.5204 | 0 | 0 | 2.6694 | 3.303 | 0.80817 | 49.9198 | 0.038105 | 0 | 0.038105 | 0.0019052 | 0 | 0.0019052 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Assembly |  | 20 | 3.6015 | 0 | 2.5894 | 0 | 0 |  |  |  | 3.8708 | 0.00072766 | 0.00072241 | 0 | 0 | 0 | 0.51636 | 1.1932 | 0 | 1.0596 | 0.15536 | 0.36251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67172 | 1.5557 | 0 | 1.0596 | 3.287 | 2.0146 | 0.25712 | 0 | 0 | 2.2717 | 0.67172 | 3.3819 | 2.0146 | 0.30435 | 0 | 0 | 2.319 | 1.5557 | 1.4906 | 2.0146 | 0.56147 | 0 | 0 | 2.5761 | 2.2275 | 31.6693 | 1.1565 | 12.7689 | 29.5735 | 0 | 20.1414 | 62.4838 | 2.0146 | 0 | 0.56147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7691 | 0.51788 | 0 | 0 | 2.5761 | 3.287 | 0.78371 | 51.8106 | 0.036773 | 0 | 0.036773 | 0.0018386 | 0 | 0.0018386 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Lodging |  | 20 | 3.321 | 0 | 2.664 | 0 | 0 |  |  |  | 3.5694 | 0.000671 | 0.00066615 | 0 | 0 | 0 | 0.53124 | 1.2276 | 0 | 1.0901 | 0.15984 | 0.37296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69109 | 1.6006 | 0 | 1.0901 | 3.3818 | 1.8577 | 0.2371 | 0 | 0 | 2.0948 | 0.69109 | 3.0312 | 1.8577 | 0.28065 | 0 | 0 | 2.1384 | 1.6006 | 1.336 | 1.8577 | 0.51775 | 0 | 0 | 2.3755 | 2.2917 | 36.569 | 1.0366 | 14.2465 | 32.9957 | 0 | 22.4721 | 69.7143 | 1.8577 | 0 | 0.51775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.849 | 0.53281 | 0 | 0 | 2.3755 | 3.3818 | 0.70243 | 59.0411 | 0.033909 | 0 | 0.033909 | 0.0016955 | 0 | 0.0016955 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Supermarket |  | 20 | 3.0609 | 0 | 2.7766 | 0 | 0 |  |  |  | 3.2899 | 0.00061845 | 0.00061399 | 0 | 0 | 0 | 0.55369 | 1.2795 | 0 | 1.1362 | 0.1666 | 0.38872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72029 | 1.6682 | 0 | 1.1362 | 3.5247 | 1.7122 | 0.21853 | 0 | 0 | 1.9308 | 0.72029 | 2.6806 | 1.7122 | 0.25867 | 0 | 0 | 1.9709 | 1.6682 | 1.1814 | 1.7122 | 0.4772 | 0 | 0 | 2.1894 | 2.3885 | 42.7485 | 0.91666 | 16.11 | 37.3117 | 0 | 25.4115 | 78.8332 | 1.7122 | 0 | 0.4772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9693 | 0.55532 | 0 | 0 | 2.1894 | 3.5247 | 0.62118 | 68.1601 | 0.031254 | 0 | 0.031254 | 0.0015627 | 0 | 0.0015627 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Large Off |  | 20 | 3.2505 | 0 | 2.9802 | 0 | 0 |  |  |  | 3.4937 | 0.00065676 | 0.00065202 | 0 | 0 | 0 | 0.5943 | 1.3733 | 0 | 1.2195 | 0.17881 | 0.41723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77311 | 1.7906 | 0 | 1.2195 | 3.7832 | 1.8183 | 0.23207 | 0 | 0 | 2.0504 | 0.77311 | 2.6521 | 1.8183 | 0.2747 | 0 | 0 | 2.093 | 1.7906 | 1.1689 | 1.8183 | 0.50676 | 0 | 0 | 2.3251 | 2.5637 | 43.3217 | 0.90693 | 16.2829 | 37.712 | 0 | 25.6842 | 79.679 | 1.8183 | 0 | 0.50676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1871 | 0.59605 | 0 | 0 | 2.3251 | 3.7832 | 0.61458 | 69.0059 | 0.03319 | 0 | 0.03319 | 0.0016595 | 0 | 0.0016595 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Restaurant |  | 20 | 4.9085 | 0 | 4.5138 | 0 | 0 |  |  |  | 5.2756 | 0.00099175 | 0.00098459 | 0 | 0 | 0 | 0.90012 | 2.08 | 0 | 1.847 | 0.27083 | 0.63194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.171 | 2.712 | 0 | 1.847 | 5.73 | 2.7457 | 0.35043 | 0 | 0 | 3.0962 | 1.171 | 2.6442 | 2.7457 | 0.41481 | 0 | 0 | 3.1606 | 2.712 | 1.1654 | 2.7457 | 0.76524 | 0 | 0 | 3.511 | 3.8829 | 43.484 | 0.90421 | 16.3318 | 37.8253 | 0 | 25.7613 | 79.9185 | 2.7457 | 0 | 0.76524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8272 | 0.90277 | 0 | 0 | 3.511 | 5.73 | 0.61274 | 69.2453 | 0.050119 | 0 | 0.050119 | 0.0025059 | 0 | 0.0025059 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Medium Off |  | 20 | 1.9635 | 0 | 1.8154 | 0 | 0 |  |  |  | 2.1104 | 0.00039672 | 0.00039385 | 0 | 0 | 0 | 0.36202 | 0.83657 | 0 | 0.74285 | 0.10892 | 0.25416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47094 | 1.0907 | 0 | 0.74285 | 2.3045 | 1.0984 | 0.14018 | 0 | 0 | 1.2385 | 0.47094 | 2.6299 | 1.0984 | 0.16593 | 0 | 0 | 1.2643 | 1.0907 | 1.1591 | 1.0984 | 0.30611 | 0 | 0 | 1.4045 | 1.5617 | 43.7775 | 0.89933 | 16.4204 | 38.0304 | 0 | 25.901 | 80.3517 | 1.0984 | 0 | 0.30611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9414 | 0.36308 | 0 | 0 | 1.4045 | 2.3045 | 0.60944 | 69.6785 | 0.020049 | 0 | 0.020049 | 0.0010024 | 0 | 0.0010024 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-MiniMart |  | 20 | 5.1886 | 0 | 4.8123 | 0 | 0 |  |  |  | 5.5767 | 0.0010483 | 0.0010408 | 0 | 0 | 0 | 0.95964 | 2.2176 | 0 | 1.9692 | 0.28874 | 0.67372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2484 | 2.8913 | 0 | 1.9692 | 6.1088 | 2.9024 | 0.37043 | 0 | 0 | 3.2729 | 1.2484 | 2.6217 | 2.9024 | 0.43848 | 0 | 0 | 3.3409 | 2.8913 | 1.1555 | 2.9024 | 0.80891 | 0 | 0 | 3.7113 | 4.1397 | 43.9481 | 0.89653 | 16.4718 | 38.1495 | 0 | 25.9821 | 80.6034 | 2.9024 | 0 | 0.80891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1464 | 0.96246 | 0 | 0 | 3.7113 | 6.1088 | 0.60754 | 69.9303 | 0.052979 | 0 | 0.052979 | 0.0026489 | 0 | 0.0026489 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Residential Care |  | 20 | 3.3896 | 0 | 3.2647 | 0 | 0 |  |  |  | 3.6384 | 0.0004412 | 0.00043801 | 0 | 0 | 0 | 0.65103 | 1.5044 | 0 | 1.3359 | 0.19588 | 0.45706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84691 | 1.9615 | 0 | 1.3359 | 4.1443 | 1.8345 | 0.1559 | 0 | 0 | 1.9904 | 0.84691 | 2.3502 | 1.8345 | 0.18453 | 0 | 0 | 2.019 | 1.9615 | 1.0293 | 1.8345 | 0.34043 | 0 | 0 | 2.1749 | 2.8084 | 49.9118 | 0.77444 | 17.1278 | 39.6688 | 0 | 27.0169 | 83.8135 | 1.8345 | 0 | 0.34043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4913 | 0.65294 | 0 | 0 | 2.1749 | 4.1443 | 0.5248 | 76.9287 | 0.034565 | 0 | 0.034565 | 0.0017282 | 0 | 0.0017282 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Small Ret |  | 20 | 1.9605 | 0 | 2.4093 | 0 | 0 |  |  |  | 2.1071 | 0.00039611 | 0.00039326 | 0 | 0 | 0 | 0.48044 | 1.1102 | 0 | 0.98586 | 0.14456 | 0.3373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.625 | 1.4475 | 0 | 0.98586 | 3.0584 | 1.0967 | 0.13997 | 0 | 0 | 1.2366 | 0.625 | 1.9786 | 1.0967 | 0.16568 | 0 | 0 | 1.2624 | 1.4475 | 0.87208 | 1.0967 | 0.30565 | 0 | 0 | 1.4023 | 2.0725 | 61.7 | 0.67662 | 21.8251 | 50.548 | 0 | 34.4263 | 106.7994 | 1.0967 | 0 | 0.30565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5765 | 0.48186 | 0 | 0 | 1.4023 | 3.0584 | 0.45852 | 96.1263 | 0.020018 | 0 | 0.020018 | 0.0010009 | 0 | 0.0010009 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Hospital |  | 20 | 3.9754 | 0 | 4.5063 | 0 | 0 |  |  |  | 4.2671 | 0.00051744 | 0.0005137 | 0 | 0 | 0 | 0.89861 | 2.0766 | 0 | 1.8439 | 0.27038 | 0.63088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.169 | 2.7074 | 0 | 1.8439 | 5.7204 | 2.1515 | 0.18284 | 0 | 0 | 2.3343 | 1.169 | 1.9969 | 2.1515 | 0.21642 | 0 | 0 | 2.3679 | 2.7074 | 0.8746 | 2.1515 | 0.39926 | 0 | 0 | 2.5508 | 3.8764 | 59.9606 | 0.65802 | 20.1582 | 46.6873 | 0 | 31.7969 | 98.6423 | 2.1515 | 0 | 0.39926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8191 | 0.90126 | 0 | 0 | 2.5508 | 5.7204 | 0.44591 | 91.7575 | 0.040538 | 0 | 0.040538 | 0.0020269 | 0 | 0.0020269 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Medium Ret |  | 20 | 2.0051 | 0 | 2.7197 | 0 | 0 |  |  |  | 2.155 | 0.00040512 | 0.0004022 | 0 | 0 | 0 | 0.54235 | 1.2533 | 0 | 1.1129 | 0.16318 | 0.38076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70553 | 1.634 | 0 | 1.1129 | 3.4525 | 1.1216 | 0.14315 | 0 | 0 | 1.2648 | 0.70553 | 1.7926 | 1.1216 | 0.16945 | 0 | 0 | 1.2911 | 1.634 | 0.7901 | 1.1216 | 0.31259 | 0 | 0 | 1.4342 | 2.3396 | 69.2092 | 0.61302 | 24.0896 | 55.7927 | 0 | 37.9983 | 117.8806 | 1.1216 | 0 | 0.31259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9085 | 0.54394 | 0 | 0 | 1.4342 | 3.4525 | 0.41542 | 107.2075 | 0.020473 | 0 | 0.020473 | 0.0010236 | 0 | 0.0010236 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-University |  | 20 | 1.926 | 0 | 2.637 | 0 | 0 |  |  |  | 2.0701 | 0.00038914 | 0.00038633 | 0 | 0 | 0 | 0.52586 | 1.2152 | 0 | 1.0791 | 0.15822 | 0.36919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68408 | 1.5844 | 0 | 1.0791 | 3.3475 | 1.0774 | 0.1375 | 0 | 0 | 1.2149 | 0.68408 | 1.7759 | 1.0774 | 0.16276 | 0 | 0 | 1.2401 | 1.5844 | 0.78273 | 1.0774 | 0.30027 | 0 | 0 | 1.3776 | 2.2685 | 69.9607 | 0.60731 | 24.3163 | 56.3176 | 0 | 38.3557 | 118.9896 | 1.0774 | 0 | 0.30027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8201 | 0.52741 | 0 | 0 | 1.3776 | 3.3475 | 0.41154 | 108.3165 | 0.019666 | 0 | 0.019666 | 0.00098328 | 0 | 0.00098328 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Xlarge Ret |  | 20 | 2.0246 | 0 | 2.8556 | 0 | 0 |  |  |  | 2.176 | 0.00040906 | 0.00040611 | 0 | 0 | 0 | 0.56944 | 1.3159 | 0 | 1.1685 | 0.17134 | 0.39978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74078 | 1.7157 | 0 | 1.1685 | 3.6249 | 1.1325 | 0.14454 | 0 | 0 | 1.2771 | 0.74078 | 1.7239 | 1.1325 | 0.17109 | 0 | 0 | 1.3036 | 1.7157 | 0.75983 | 1.1325 | 0.31563 | 0 | 0 | 1.4482 | 2.4565 | 72.3919 | 0.58953 | 25.0494 | 58.0156 | 0 | 39.5122 | 122.5772 | 1.1325 | 0 | 0.31563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0538 | 0.57112 | 0 | 0 | 1.4482 | 3.6249 | 0.3995 | 111.9041 | 0.020672 | 0 | 0.020672 | 0.0010336 | 0 | 0.0010336 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Large Ret |  | 20 | 2.0369 | 0 | 2.9415 | 0 | 0 |  |  |  | 2.1893 | 0.00041155 | 0.00040858 | 0 | 0 | 0 | 0.58657 | 1.3555 | 0 | 1.2036 | 0.17649 | 0.41181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76306 | 1.7673 | 0 | 1.2036 | 3.734 | 1.1394 | 0.14542 | 0 | 0 | 1.2848 | 0.76306 | 1.6838 | 1.1394 | 0.17214 | 0 | 0 | 1.3116 | 1.7673 | 0.74213 | 1.1394 | 0.31756 | 0 | 0 | 1.457 | 2.5304 | 74.3727 | 0.5758 | 25.6467 | 59.3991 | 0 | 40.4544 | 125.5002 | 1.1394 | 0 | 0.31756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1457 | 0.5883 | 0 | 0 | 1.457 | 3.734 | 0.39019 | 114.8271 | 0.020798 | 0 | 0.020798 | 0.0010399 | 0 | 0.0010399 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-Warehouse |  | 20 | 2.0323 | 0 | 2.9415 | 0 | 0 |  |  |  | 2.1843 | 0.00041062 | 0.00040765 | 0 | 0 | 0 | 0.58658 | 1.3555 | 0 | 1.2036 | 0.17649 | 0.41181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76307 | 1.7673 | 0 | 1.2036 | 3.734 | 1.1368 | 0.14509 | 0 | 0 | 1.2819 | 0.76307 | 1.68 | 1.1368 | 0.17174 | 0 | 0 | 1.3086 | 1.7673 | 0.74044 | 1.1368 | 0.31683 | 0 | 0 | 1.4537 | 2.5304 | 74.5667 | 0.57449 | 25.7053 | 59.5346 | 0 | 40.5467 | 125.7866 | 1.1368 | 0 | 0.31683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1457 | 0.5883 | 0 | 0 | 1.4537 | 3.734 | 0.38931 | 115.1134 | 0.020751 | 0 | 0.020751 | 0.0010375 | 0 | 0.0010375 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-New-School K-12 |  | 20 | 1.9011 | 0 | 2.6676 | 0 | 0 |  |  |  | 2.0455 | 0.00018837 | 0.00018701 | 0 | 0 | 0 | 0.53195 | 1.2293 | 0 | 1.0916 | 0.16006 | 0.37346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69201 | 1.6027 | 0 | 1.0916 | 3.3863 | 1.0956 | 0.066561 | 0 | 0 | 1.1622 | 0.69201 | 1.6794 | 1.0956 | 0.078788 | 0 | 0 | 1.1744 | 1.6027 | 0.73274 | 1.0956 | 0.14535 | 0 | 0 | 1.2409 | 2.2947 | 77.3194 | 0.54078 | 24.8935 | 57.6545 | 0 | 39.2662 | 121.8142 | 1.0956 | 0 | 0.14535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8528 | 0.53352 | 0 | 0 | 1.2409 | 3.3863 | 0.36646 | 116.5856 | 0.019432 | 0 | 0.019432 | 0.0009716 | 0 | 0.0009716 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Supply Curve Results; Categories sorted by TRC Net Levelized Cost
Totals for Categories with Benefits Exceeding Costs. Levelized cost is TRC Net Levelized Cost (Net of Benefits) | [12 empty] | Savings Allocation by Cost Bin and Month for Segments 1 | [12 empty] | Savings Allocation by Cost Bin and Month for Segments 2
| Totals Basis | Busbar Electric Savings in kWh | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Measures with B/C > 1.00 | 4.6972 | 2.2705 | 0 | 2.2705 | 2.4282 | 3.126 | 4234.4437 | 12.81 | 27.3642 | 1.3167 | 0.044624 | 0.29454 | 0.26484 | 0.30476 | 0.28352 | 0.28946 | 0.28653 | 0.27221 | 0.28363 | 0.265 | 0.30215 | 0.26739 | 0.29111 |  | 0.12505 | 0.10744 | 0.10306 | 0.10761 | 0.10558 | 0.092641 | 0.10877 | 0.089205 | 0.10982 | 0.098636 | 0.11834 | 0.12591
| Categories with B/C > 1.00 | 3.1207 | 1.5351 | 0.30702 | 1.8421 | 1.9487 | 2.0768 | 5170.9703 | 20.4634 | 35.2743 | 1.0658 | 0.029647 | 0.32801 | 0.29494 | 0.3394 | 0.31575 | 0.32236 | 0.31909 | 0.30314 | 0.31586 | 0.29512 | 0.33649 | 0.29777 | 0.3242 |  | 0.13926 | 0.11965 | 0.11477 | 0.11984 | 0.11758 | 0.10317 | 0.12113 | 0.099343 | 0.1223 | 0.10985 | 0.13179 | 0.14022
Supply Curve Results: By TRC Net Levelized Cost - Net of Benefits
| Block 1: <= 0 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 2: <= 10 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 3: 10-20 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 4: 20-30 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 5: 30-40 mills/kWh | 3.1207 | 1.5351 | 0.30702 | 1.8421 | 1.9487 | 2.0768 | 5170.9703 | 20.4634 | 35.2743 | 1.0658 | 0.029647 | 0.19568 | 0.17595 | 0.20247 | 0.18836 | 0.19231 | 0.19036 | 0.18085 | 0.18843 | 0.17606 | 0.20074 | 0.17764 | 0.19341 |  | 0.083079 | 0.071379 | 0.068467 | 0.071491 | 0.070142 | 0.061548 | 0.072265 | 0.059265 | 0.072961 | 0.065531 | 0.078623 | 0.08365
| Block 6: 40-50 mills/kWh | 4.0111 | 2.602 | 0.5204 | 3.1224 | 3.303 | 2.6694 | 6819.1906 | 30.388 | 49.9198 | 0.80817 | 0.038105 | 0.25151 | 0.22615 | 0.26024 | 0.24211 | 0.24718 | 0.24467 | 0.23244 | 0.2422 | 0.22629 | 0.25801 | 0.22833 | 0.24859 |  | 0.10678 | 0.091744 | 0.088002 | 0.091889 | 0.090155 | 0.079109 | 0.092884 | 0.076174 | 0.093779 | 0.084228 | 0.10106 | 0.10752
| Block 7: 50-60 mills/kWh | 7.4402 | 5.2534 | 1.0507 | 6.3041 | 6.6688 | 4.9515 | 7422.361 | 34.0199 | 55.2794 | 0.74472 | 0.070683 | 0.46654 | 0.41949 | 0.48273 | 0.44909 | 0.4585 | 0.45385 | 0.43117 | 0.44926 | 0.41975 | 0.4786 | 0.42353 | 0.46112 |  | 0.19807 | 0.17018 | 0.16324 | 0.17045 | 0.16723 | 0.14674 | 0.17229 | 0.1413 | 0.17395 | 0.15624 | 0.18745 | 0.19944
| Block 8: 60-70 mills/kWh | 19.7462 | 16.8984 | 3.3797 | 20.2781 | 21.4511 | 13.1413 | 8995.9631 | 43.4952 | 69.2619 | 0.61265 | 0.18759 | 1.2382 | 1.1133 | 1.2812 | 1.1919 | 1.2168 | 1.2045 | 1.1443 | 1.1923 | 1.114 | 1.2702 | 1.124 | 1.2238 |  | 0.52568 | 0.45165 | 0.43323 | 0.45236 | 0.44383 | 0.38945 | 0.45726 | 0.375 | 0.46167 | 0.41465 | 0.49749 | 0.5293
| Block 9: 70-80 mills/kWh | 3.6384 | 3.2647 | 0.65294 | 3.9176 | 4.1443 | 2.1749 | 9432.4469 | 49.9118 | 76.9287 | 0.5248 | 0.034565 | 0.17244 | 0.1584 | 0.1849 | 0.17131 | 0.18005 | 0.18274 | 0.1786 | 0.19328 | 0.16945 | 0.18707 | 0.16447 | 0.17176 |  | 0.1349 | 0.11874 | 0.12089 | 0.12403 | 0.12746 | 0.11903 | 0.13635 | 0.12368 | 0.13258 | 0.12118 | 0.1306 | 0.13446
| Block 10: 80-90 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 11: 90-100 mills/kWh | 6.3742 | 6.9156 | 1.3831 | 8.2987 | 8.7788 | 3.9531 | 11404.7661 | 60.5356 | 93.2017 | 0.45008 | 0.060556 | 0.33437 | 0.30458 | 0.35356 | 0.32811 | 0.34101 | 0.34286 | 0.33157 | 0.35391 | 0.31761 | 0.35494 | 0.31284 | 0.33203 |  | 0.21431 | 0.18745 | 0.18802 | 0.19374 | 0.19685 | 0.18116 | 0.2087 | 0.18507 | 0.20475 | 0.18637 | 0.20625 | 0.21418
| Block 12: 100-110 mills/kWh | 4.2251 | 5.3568 | 1.0714 | 6.4281 | 6.8 | 2.8118 | 13327.5431 | 69.5774 | 107.7508 | 0.41352 | 0.040139 | 0.26494 | 0.23822 | 0.27413 | 0.25503 | 0.26037 | 0.25773 | 0.24485 | 0.25512 | 0.23837 | 0.27178 | 0.24051 | 0.26186 |  | 0.11248 | 0.09664 | 0.092698 | 0.096793 | 0.094967 | 0.083331 | 0.097841 | 0.080239 | 0.098783 | 0.088723 | 0.10645 | 0.11325
| Block 13: 110-120 mills/kWh | 8.5951 | 11.4062 | 2.2812 | 13.6874 | 14.4792 | 5.5997 | 13950.0968 | 74.6218 | 114.5783 | 0.38668 | 0.081654 | 0.56404 | 0.50995 | 0.57977 | 0.54251 | 0.5542 | 0.54368 | 0.50711 | 0.54558 | 0.52432 | 0.57936 | 0.50519 | 0.54215 |  | 0.21827 | 0.18223 | 0.1703 | 0.17153 | 0.16572 | 0.14536 | 0.16754 | 0.14098 | 0.17449 | 0.1539 | 0.19163 | 0.21524
| Block 14: 120-130 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 15: 130-140 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 16: 140-150 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 17: 150-160 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 18: 160-170 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 19: 170-180 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 20: 180-190 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 21: 190-200 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 22: > 200 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Shaped Savings Results; By Category and sorted by TRC BC ratio
[13 empty] | Savings Allocation by Cost Bin and Month for Segments 1 Feb: Savings Allocation by Category and Month for Segments 1 |  |  | Savings Allocation by Category and Month for Segments 2
Category | Measure | Busbar Savings | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Wholesale KW | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
VRF-New-Small Off |  | 3.1207 | 1.5351 | 0.30702 | 1.8421 | 1.9487 | 2.0768 | 5170.9703 | 20.4634 | 35.2743 | 1.0658 | 0.029647 | 0.00058664 | 0.19568 | 0.17595 | 0.20247 | 0.18836 | 0.19231 | 0.19036 | 0.18085 | 0.18843 | 0.17606 | 0.20074 | 0.17764 | 0.19341 |  | 0.083079 | 0.071379 | 0.068467 | 0.071491 | 0.070142 | 0.061548 | 0.072265 | 0.059265 | 0.072961 | 0.065531 | 0.078623 | 0.08365
VRF-New-Other |  | 4.0111 | 2.602 | 0.5204 | 3.1224 | 3.303 | 2.6694 | 6819.1906 | 30.388 | 49.9198 | 0.80817 | 0.038105 | 0.00075402 | 0.25151 | 0.22615 | 0.26024 | 0.24211 | 0.24718 | 0.24467 | 0.23244 | 0.2422 | 0.22629 | 0.25801 | 0.22833 | 0.24859 |  | 0.10678 | 0.091744 | 0.088002 | 0.091889 | 0.090155 | 0.079109 | 0.092884 | 0.076174 | 0.093779 | 0.084228 | 0.10106 | 0.10752
VRF-New-Assembly |  | 3.8708 | 2.5894 | 0.51788 | 3.1073 | 3.287 | 2.5761 | 7031.9817 | 31.6693 | 51.8106 | 0.78371 | 0.036773 | 0.00072766 | 0.24272 | 0.21825 | 0.25114 | 0.23364 | 0.23854 | 0.23612 | 0.22432 | 0.23373 | 0.21838 | 0.24899 | 0.22035 | 0.2399 |  | 0.10305 | 0.088537 | 0.084926 | 0.088676 | 0.087004 | 0.076343 | 0.089637 | 0.073511 | 0.0905 | 0.081283 | 0.097523 | 0.10376
VRF-New-Lodging |  | 3.5694 | 2.664 | 0.53281 | 3.1968 | 3.3818 | 2.3755 | 7845.7085 | 36.569 | 59.0411 | 0.70243 | 0.033909 | 0.000671 | 0.22382 | 0.20125 | 0.23159 | 0.21545 | 0.21996 | 0.21773 | 0.20685 | 0.21553 | 0.20137 | 0.2296 | 0.20319 | 0.22122 |  | 0.095024 | 0.081642 | 0.078312 | 0.081771 | 0.080228 | 0.070398 | 0.082656 | 0.067786 | 0.083452 | 0.074953 | 0.089928 | 0.095678
VRF-New-Supermarket |  | 3.2899 | 2.7766 | 0.55532 | 3.3319 | 3.5247 | 2.1894 | 8871.9635 | 42.7485 | 68.1601 | 0.62118 | 0.031254 | 0.00061845 | 0.20629 | 0.18549 | 0.21345 | 0.19858 | 0.20274 | 0.20068 | 0.19065 | 0.19865 | 0.1856 | 0.21162 | 0.18728 | 0.20389 |  | 0.087583 | 0.075249 | 0.07218 | 0.075367 | 0.073946 | 0.064885 | 0.076183 | 0.062478 | 0.076917 | 0.069084 | 0.082886 | 0.088186
VRF-New-Large Off |  | 3.4937 | 2.9802 | 0.59605 | 3.5763 | 3.7832 | 2.3251 | 8967.1516 | 43.3217 | 69.0059 | 0.61458 | 0.03319 | 0.00065676 | 0.21907 | 0.19698 | 0.22667 | 0.21088 | 0.21529 | 0.21311 | 0.20246 | 0.21096 | 0.1971 | 0.22473 | 0.19888 | 0.21652 |  | 0.093008 | 0.07991 | 0.076651 | 0.080036 | 0.078526 | 0.068904 | 0.080903 | 0.066348 | 0.081682 | 0.073363 | 0.088021 | 0.093648
VRF-New-Restaurant |  | 5.2756 | 4.5138 | 0.90277 | 5.4166 | 5.73 | 3.511 | 8994.0983 | 43.484 | 69.2453 | 0.61274 | 0.050119 | 0.00099175 | 0.33081 | 0.29745 | 0.34229 | 0.31844 | 0.32511 | 0.32181 | 0.30573 | 0.31856 | 0.29763 | 0.33936 | 0.30031 | 0.32696 |  | 0.14045 | 0.12067 | 0.11575 | 0.12086 | 0.11858 | 0.10405 | 0.12217 | 0.10019 | 0.12334 | 0.11078 | 0.13292 | 0.14141
VRF-New-Medium Off |  | 2.1104 | 1.8154 | 0.36308 | 2.1785 | 2.3045 | 1.4045 | 9042.8549 | 43.7775 | 69.6785 | 0.60944 | 0.020049 | 0.00039672 | 0.13233 | 0.11899 | 0.13692 | 0.12738 | 0.13005 | 0.12873 | 0.1223 | 0.12743 | 0.11906 | 0.13575 | 0.12013 | 0.13079 |  | 0.056182 | 0.04827 | 0.046301 | 0.048346 | 0.047434 | 0.041622 | 0.048869 | 0.040078 | 0.04934 | 0.044315 | 0.053169 | 0.056568
VRF-New-MiniMart |  | 5.5767 | 4.8123 | 0.96246 | 5.7748 | 6.1088 | 3.7113 | 9071.1834 | 43.9481 | 69.9303 | 0.60754 | 0.052979 | 0.0010483 | 0.34969 | 0.31442 | 0.36182 | 0.33661 | 0.34366 | 0.34018 | 0.32317 | 0.33673 | 0.31462 | 0.35872 | 0.31745 | 0.34562 |  | 0.14846 | 0.12755 | 0.12235 | 0.12776 | 0.12535 | 0.10999 | 0.12914 | 0.10591 | 0.13038 | 0.1171 | 0.1405 | 0.14948
VRF-New-Residential Care |  | 3.6384 | 3.2647 | 0.65294 | 3.9176 | 4.1443 | 2.1749 | 9432.4469 | 49.9118 | 76.9287 | 0.5248 | 0.034565 | 0.0004412 | 0.17244 | 0.1584 | 0.1849 | 0.17131 | 0.18005 | 0.18274 | 0.1786 | 0.19328 | 0.16945 | 0.18707 | 0.16447 | 0.17176 |  | 0.1349 | 0.11874 | 0.12089 | 0.12403 | 0.12746 | 0.11903 | 0.13635 | 0.12368 | 0.13258 | 0.12118 | 0.1306 | 0.13446
VRF-New-Small Ret |  | 2.1071 | 2.4093 | 0.48186 | 2.8911 | 3.0584 | 1.4023 | 12019.3081 | 61.7 | 96.1263 | 0.45852 | 0.020018 | 0.00039611 | 0.13213 | 0.11881 | 0.13671 | 0.12719 | 0.12985 | 0.12854 | 0.12211 | 0.12723 | 0.11888 | 0.13554 | 0.11995 | 0.13059 |  | 0.056097 | 0.048197 | 0.046231 | 0.048272 | 0.047362 | 0.041559 | 0.048795 | 0.040017 | 0.049265 | 0.044248 | 0.053088 | 0.056482
VRF-New-Hospital |  | 4.2671 | 4.5063 | 0.90126 | 5.4075 | 5.7204 | 2.5508 | 11101.2964 | 59.9606 | 91.7575 | 0.44591 | 0.040538 | 0.00051744 | 0.20224 | 0.18577 | 0.21685 | 0.20092 | 0.21116 | 0.21432 | 0.20946 | 0.22667 | 0.19873 | 0.2194 | 0.19289 | 0.20144 |  | 0.15821 | 0.13925 | 0.14178 | 0.14547 | 0.14949 | 0.1396 | 0.15991 | 0.14505 | 0.15549 | 0.14212 | 0.15317 | 0.1577
VRF-New-Medium Ret |  | 2.155 | 2.7197 | 0.54394 | 3.2637 | 3.4525 | 1.4342 | 13266.3956 | 69.2092 | 107.2075 | 0.41542 | 0.020473 | 0.00040512 | 0.13513 | 0.12151 | 0.13982 | 0.13008 | 0.1328 | 0.13146 | 0.12489 | 0.13013 | 0.12158 | 0.13863 | 0.12268 | 0.13356 |  | 0.057372 | 0.049292 | 0.047282 | 0.04937 | 0.048438 | 0.042503 | 0.049904 | 0.040927 | 0.050385 | 0.045254 | 0.054295 | 0.057767
VRF-New-University |  | 2.0701 | 2.637 | 0.52741 | 3.1644 | 3.3475 | 1.3776 | 13391.2012 | 69.9607 | 108.3165 | 0.41154 | 0.019666 | 0.00038914 | 0.1298 | 0.11671 | 0.13431 | 0.12495 | 0.12757 | 0.12627 | 0.11996 | 0.125 | 0.11679 | 0.13316 | 0.11784 | 0.12829 |  | 0.055109 | 0.047348 | 0.045417 | 0.047423 | 0.046528 | 0.040827 | 0.047936 | 0.039313 | 0.048398 | 0.043469 | 0.052154 | 0.055488
VRF-New-Xlarge Ret |  | 2.176 | 2.8556 | 0.57112 | 3.4267 | 3.6249 | 1.4482 | 13794.9546 | 72.3919 | 111.9041 | 0.3995 | 0.020672 | 0.00040906 | 0.13645 | 0.12269 | 0.14118 | 0.13135 | 0.1341 | 0.13274 | 0.1261 | 0.13139 | 0.12276 | 0.13997 | 0.12387 | 0.13486 |  | 0.05793 | 0.049772 | 0.047742 | 0.04985 | 0.04891 | 0.042917 | 0.05039 | 0.041325 | 0.050875 | 0.045694 | 0.054823 | 0.058329
VRF-New-Large Ret |  | 2.1893 | 2.9415 | 0.5883 | 3.5298 | 3.734 | 1.457 | 14123.9118 | 74.3727 | 114.8271 | 0.39019 | 0.020798 | 0.00041155 | 0.13728 | 0.12344 | 0.14204 | 0.13215 | 0.13491 | 0.13355 | 0.12687 | 0.13219 | 0.12351 | 0.14083 | 0.12462 | 0.13568 |  | 0.058283 | 0.050075 | 0.048032 | 0.050154 | 0.049208 | 0.043178 | 0.050697 | 0.041577 | 0.051185 | 0.045972 | 0.055157 | 0.058684
VRF-New-Warehouse |  | 2.1843 | 2.9415 | 0.5883 | 3.5298 | 3.734 | 1.4537 | 14156.138 | 74.5667 | 115.1134 | 0.38931 | 0.020751 | 0.00041062 | 0.13697 | 0.12315 | 0.14172 | 0.13184 | 0.13461 | 0.13324 | 0.12658 | 0.13189 | 0.12323 | 0.14051 | 0.12434 | 0.13537 |  | 0.05815 | 0.049961 | 0.047923 | 0.05004 | 0.049096 | 0.04308 | 0.050582 | 0.041482 | 0.051069 | 0.045868 | 0.055032 | 0.05855
VRF-New-School K-12 |  | 2.0455 | 2.6676 | 0.53352 | 3.2011 | 3.3863 | 1.2409 | 13709.0826 | 77.3194 | 116.5856 | 0.36646 | 0.019432 | 0.00018837 | 0.15335 | 0.14067 | 0.15482 | 0.14717 | 0.15059 | 0.14416 | 0.12755 | 0.1501 | 0.15482 | 0.15806 | 0.13236 | 0.13623 |  | 0.043903 | 0.032425 | 0.026602 | 0.021484 | 0.01851 | 0.016189 | 0.015869 | 0.0166 | 0.021359 | 0.016362 | 0.026613 | 0.039677
Note on I6: :ProCost Perioodic replacement costs and savinsg of the measure. These are costs and savings that occur periodicially, but at different periods than annually. Can be positive or negative. Periodic replacement costs for both the measure and the baseline measure should be included if applicable. ProCost can analysze these costs in two ways dependent on the 'Repeat Periodic Replacemetn' switch in the ProData page. When set to 'On', ProCost repeats replacement costs for multiple times over the life of a measure depending on the input period and measure life. For example fluorescent lamps may have a 4-year replacement cycle that repeats 3 times in a 15-year measure life. When set to 'Off', ProCost reads the period as the year after installation that the replacement cost occurs and does not subsequently reinstall or repeat the replacement costs. For example a compressor may be replaced only once in the life of a heat-pump system. Example: A new fluorescent lighting systems may have a measure life of 15 years, and a lamp life of five years. Two lamps lamps per fixture must be replaced at years 6 and 11. Lamp and labor costs, expressed as positive costs, are entered as a cost and the period would be enetered as 5. The baseline measure may have a four year lamp life and would have required a three-lamp replacement at years 5, 9 and 13. Lamp and labor replacement costs would be entered as annual savings in dollars with a 4-year period. ProCost determines the net present value of the two cost streams.
Note on O6: :ProCost If the measure has gas savings for incfreases, enter the annual savings and shape of the savings here. Example: Clothes washer saves electric motor and dryer energy and gas water heat.
Note on A7: :Procost Category for the measure. Individual measures can be grouped into categories. Procost output is reported by measure and by category. All measures must belong to at least one category. Category name can be the same as measure name. Example: Measures can be combined into one category if they have components with different load shapes or measure lives. On wash machines there may be one load shape for the electric motor savings component, a second load shape for the electric water heat savings component and a third shape for electric dryer savings component.
Note on B7: :ProCost Name of Measure. User-defined. For PTR measures, defined naming conventions apply.
Note on C7: :ProCost Annual electric savings for the measure in kWh at the site. May be positive, negative or zero. Savings are incremental to the baseline alternative.
Note on D7: :ProCost Physical life of the measure in years. Must be >=1.
Note on E7: :ProCost Initial cost to install the measure in dollars. Costs are incremental to the baseline alternative. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on F7: :ProCost Annaul opperations and maintenace cost for the measure in dollars. Must be incremental cost over the baseline alternative. May be positive, negative or zero. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page. O&M costs are enetered as positive values. Negative values represent O&M savings compared to the baseline alternative. Example: Annualized maintenace cost for a heat pump heating system compared to a baseline electric resistance heating system.
Note on G7: :ProCost Name of the pointer to the shape of the savings. The shapes represent the daily and monthly shape of the savings in four time segments for each month of the year. Shape of the savings is relative to the baseline alternative. These shaps are in the MC_AND_Loadshape file.
Note on H7: :ProCost Annual value of any non-energy benefits of the measure, relative to the baseline alternative. Expressed in dollars per year and denominated in dollars of the 'Cost Reference Year'. Positive value represents dollar savings. Negative value represents dollar cost. Example: Water, detergent and sewer savings from efficient clothes washer.
Note on I7: : Cost in dollars that is incurred for Period 1. Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on J7: :ProCost Duration of Period1. The time at which Period 1 costs, or savings, occur. In years.
Note on K7: : Cost in dollars that is incurred for Period 2 Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on L7: :ProCost Duration of Period 2. The time at which Period 2 costs, or savings, occur. In years.
Note on M7: : Cost in dollars that is incurred for Period 3. Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on N7: :ProCost Duration of Period 3. The time at which Period 3 costs, or savings, occur. In years.
Note on O7: : Annual gas savings, or increases, in therms.
Note on P7: :ProCost Name of the pointer to the shape of the savings. The shapes represent the daily and monthly shape of the savings in four time segments for each month of the year. Shape of the savings is relative to the baseline alternative. These shaps are in the MC_AND_Loadshape file.
Note on BH70: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BM70: Direct and program administrative costs of the measure to sponsor. Separate costs for each sponsor. Depends on share of costs incurred by sponsor, sponsor cost of capital, and financing term which are user-defined inputs. Includes applicable Capital, O&M, Periodic Replacement and Program Administrative costs. Sponsor costs are levelized over program life. Does not include any adjustments for benefit. NOTE: Units are per kWh for 'Electric' runs and per therm for 'Gas' runs for all sponsors.
Note on CE70: All costs minus all benefits regardless of which sponsor incurs the cost or accrues the benefits. TRC Net Levelized Cost includes all applicable costs and all benefits. In addition to energy system costs and benefits, TRC Net Levelized Cost includes non-energy, other-fuel, O&M, periodic-replacement and risk-mitigation benefits and costs. TRC Net Levelized Cost corresponds to TRC B/C ratios with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure. The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the TRC B/C ratio and the TRC Net Levelized Cost. If Risk-Mitigation credit is non-zero, TRC Levelized Cost will be reduced by the risk-mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on CW70: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BH111: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BM111: Direct and program administrative costs of the measure to sponsor. Separate costs for each sponsor. Depends on share of costs incurred by sponsor, sponsor cost of capital, and financing term which are user-defined inputs. Includes applicable Capital, O&M, Periodic Replacement and Program Administrative costs. Sponsor costs are levelized over program life. Does not include any adjustments for benefit. NOTE: Units are per kWh for 'Electric' runs and per therm for 'Gas' runs for all sponsors.
Note on CE111: All costs minus all benefits regardless of which sponsor incurs the cost or accrues the benefits. TRC Net Levelized Cost includes all applicable costs and all benefits. In addition to energy system costs and benefits, TRC Net Levelized Cost includes non-energy, other-fuel, O&M, periodic-replacement and risk-mitigation benefits and costs. TRC Net Levelized Cost corresponds to TRC B/C ratios with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure. The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the TRC B/C ratio and the TRC Net Levelized Cost. If Risk-Mitigation credit is non-zero, TRC Levelized Cost will be reduced by the risk-mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on CW111: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.

## M_Input_Retro_Out
Shaped Savings Results; By Category and sorted by TRC BC ratio
[14 empty] | Savings Allocation by Category and Month for Segments 1 | [11 empty] | Savings Allocation by Category and Month for Segments 2
Category | Measure | Busbar Savings | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Wholesale KW | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
VRF-Retro-Small Off |  | 3.5602 | 1.773 | 0.35461 | 2.1276 | 2.2507 | 2.3693 | 5235.1868 | 20.85 | 35.8449 | 1.0527 | 0.033822 | 0.00066926 | 0.22324 | 0.20073 | 0.23099 | 0.21489 | 0.21939 | 0.21717 | 0.20632 | 0.21497 | 0.20085 | 0.22901 | 0.20266 | 0.22065 | 0.094779 | 0.081432 | 0.07811 | 0.08156 | 0.080021 | 0.070216 | 0.082443 | 0.067612 | 0.083237 | 0.07476 | 0.089697 | 0.095431
VRF-Retro-Other |  | 4.3115 | 3.0053 | 0.60106 | 3.6064 | 3.815 | 2.8693 | 7327.3906 | 33.448 | 54.4355 | 0.75212 | 0.040959 | 0.0008105 | 0.27035 | 0.24309 | 0.27973 | 0.26024 | 0.26569 | 0.263 | 0.24985 | 0.26034 | 0.24324 | 0.27734 | 0.24543 | 0.26721 | 0.11478 | 0.098616 | 0.094594 | 0.098771 | 0.096908 | 0.085034 | 0.099841 | 0.08188 | 0.1008 | 0.090537 | 0.10863 | 0.11557
VRF-Retro-Lodging |  | 3.7783 | 3.077 | 0.6154 | 3.6924 | 3.906 | 2.5145 | 8560.7383 | 40.8745 | 65.3946 | 0.64376 | 0.035894 | 0.00071027 | 0.23692 | 0.21303 | 0.24514 | 0.22806 | 0.23284 | 0.23048 | 0.21896 | 0.22814 | 0.21316 | 0.24304 | 0.21508 | 0.23417 | 0.10059 | 0.086421 | 0.082896 | 0.086557 | 0.084924 | 0.074519 | 0.087494 | 0.071754 | 0.088337 | 0.079341 | 0.095193 | 0.10128
VRF-Retro-Large Off |  | 3.9857 | 3.4422 | 0.68844 | 4.1306 | 4.3696 | 2.6525 | 9078.5117 | 43.9923 | 69.9954 | 0.60704 | 0.037865 | 0.00074926 | 0.24992 | 0.22472 | 0.2586 | 0.24058 | 0.24562 | 0.24313 | 0.23097 | 0.24067 | 0.22486 | 0.25638 | 0.22689 | 0.24702 | 0.10611 | 0.091165 | 0.087446 | 0.091308 | 0.089586 | 0.078609 | 0.092297 | 0.075693 | 0.093186 | 0.083696 | 0.10042 | 0.10684
VRF-Retro-Medium Off |  | 2.4076 | 2.0968 | 0.41936 | 2.5162 | 2.6617 | 1.6023 | 9155.155 | 44.4538 | 70.6764 | 0.60196 | 0.022872 | 0.00045259 | 0.15097 | 0.13574 | 0.15621 | 0.14532 | 0.14837 | 0.14686 | 0.13952 | 0.14538 | 0.13583 | 0.15487 | 0.13705 | 0.14921 | 0.064095 | 0.055068 | 0.052822 | 0.055155 | 0.054114 | 0.047484 | 0.055752 | 0.045722 | 0.056289 | 0.050557 | 0.060657 | 0.064536
VRF-Retro-Restaurant |  | 5.8389 | 5.2135 | 1.0427 | 6.2562 | 6.6181 | 3.8859 | 9386.0805 | 45.8442 | 72.7283 | 0.58715 | 0.05547 | 0.0010976 | 0.36613 | 0.32921 | 0.37884 | 0.35244 | 0.35982 | 0.35617 | 0.33837 | 0.35257 | 0.32941 | 0.37559 | 0.33238 | 0.36187 | 0.15544 | 0.13355 | 0.12811 | 0.13376 | 0.13124 | 0.11516 | 0.13521 | 0.11089 | 0.13651 | 0.12261 | 0.14711 | 0.15651
VRF-Retro-Assembly |  | 3.2062 | 2.9908 | 0.59815 | 3.5889 | 3.7965 | 2.1338 | 9805.5803 | 48.3702 | 76.4559 | 0.56203 | 0.030459 | 0.00060272 | 0.20105 | 0.18077 | 0.20802 | 0.19353 | 0.19758 | 0.19558 | 0.1858 | 0.1936 | 0.18088 | 0.20624 | 0.18251 | 0.19871 | 0.085356 | 0.073335 | 0.070344 | 0.073451 | 0.072065 | 0.063235 | 0.074246 | 0.060889 | 0.074961 | 0.067327 | 0.080779 | 0.085943
VRF-Retro-Supermarket |  | 3.3204 | 3.207 | 0.6414 | 3.8484 | 4.071 | 2.2098 | 10152.9961 | 50.4622 | 79.5429 | 0.5428 | 0.031544 | 0.00062419 | 0.20821 | 0.18721 | 0.21543 | 0.20042 | 0.20462 | 0.20254 | 0.19242 | 0.20049 | 0.18733 | 0.21359 | 0.18901 | 0.20579 | 0.088396 | 0.075947 | 0.072849 | 0.076067 | 0.074632 | 0.065487 | 0.07689 | 0.063058 | 0.077631 | 0.069725 | 0.083655 | 0.089004
VRF-Retro-MiniMart |  | 5.6284 | 5.5583 | 1.1117 | 6.6699 | 7.0558 | 3.7458 | 10380.9815 | 51.835 | 81.5687 | 0.53088 | 0.05347 | 0.0010581 | 0.35293 | 0.31734 | 0.36518 | 0.33973 | 0.34685 | 0.34333 | 0.32617 | 0.33986 | 0.31754 | 0.36205 | 0.3204 | 0.34883 | 0.14984 | 0.12874 | 0.12349 | 0.12894 | 0.12651 | 0.11101 | 0.13034 | 0.10689 | 0.13159 | 0.11819 | 0.1418 | 0.15087
VRF-Retro-Residential Care |  | 3.9867 | 3.7708 | 0.75415 | 4.5249 | 4.7867 | 2.3832 | 9942.4973 | 52.983 | 81.4608 | 0.49788 | 0.037874 | 0.00048344 | 0.18895 | 0.17357 | 0.2026 | 0.18772 | 0.19729 | 0.20024 | 0.1957 | 0.21178 | 0.18567 | 0.20499 | 0.18021 | 0.1882 | 0.14782 | 0.13011 | 0.13247 | 0.13591 | 0.13967 | 0.13043 | 0.1494 | 0.13552 | 0.14527 | 0.13279 | 0.1431 | 0.14734
VRF-Retro-Warehouse |  | 2.9829 | 3.3975 | 0.67949 | 4.0769 | 4.3128 | 1.9851 | 11973.0293 | 61.4213 | 95.7151 | 0.46029 | 0.028338 | 0.00056074 | 0.18704 | 0.16818 | 0.19353 | 0.18005 | 0.18382 | 0.18195 | 0.17286 | 0.18011 | 0.16828 | 0.19188 | 0.1698 | 0.18487 | 0.07941 | 0.068227 | 0.065444 | 0.068335 | 0.067045 | 0.05883 | 0.069074 | 0.056648 | 0.06974 | 0.062637 | 0.075152 | 0.079957
VRF-Retro-Small Ret |  | 2.0845 | 2.7827 | 0.55655 | 3.3393 | 3.5325 | 1.3872 | 14033.33 | 73.8272 | 114.0222 | 0.39271 | 0.019803 | 0.00039185 | 0.13071 | 0.11753 | 0.13524 | 0.12582 | 0.12845 | 0.12715 | 0.1208 | 0.12587 | 0.1176 | 0.13409 | 0.11866 | 0.12919 | 0.055493 | 0.047678 | 0.045733 | 0.047753 | 0.046852 | 0.041112 | 0.04827 | 0.039587 | 0.048735 | 0.043772 | 0.052517 | 0.055875
VRF-Retro-Hospital |  | 4.2671 | 5.2048 | 1.041 | 6.2458 | 6.6071 | 2.5508 | 12822.0771 | 70.3221 | 107.0478 | 0.38606 | 0.040538 | 0.00051744 | 0.20224 | 0.18577 | 0.21685 | 0.20092 | 0.21116 | 0.21432 | 0.20946 | 0.22667 | 0.19873 | 0.2194 | 0.19289 | 0.20144 | 0.15821 | 0.13925 | 0.14178 | 0.14547 | 0.14949 | 0.1396 | 0.15991 | 0.14505 | 0.15549 | 0.14212 | 0.15317 | 0.1577
VRF-Retro-University |  | 2.0701 | 3.0458 | 0.60916 | 3.655 | 3.8664 | 1.3776 | 15466.9336 | 82.4595 | 126.7607 | 0.35631 | 0.019666 | 0.00038914 | 0.1298 | 0.11671 | 0.13431 | 0.12495 | 0.12757 | 0.12627 | 0.11996 | 0.125 | 0.11679 | 0.13316 | 0.11784 | 0.12829 | 0.055109 | 0.047348 | 0.045417 | 0.047423 | 0.046528 | 0.040827 | 0.047936 | 0.039313 | 0.048398 | 0.043469 | 0.052154 | 0.055488
VRF-Retro-Medium Ret |  | 2.1319 | 3.1413 | 0.62826 | 3.7696 | 3.9876 | 1.4188 | 15489.3864 | 82.5947 | 126.9602 | 0.3558 | 0.020253 | 0.00040076 | 0.13368 | 0.1202 | 0.13832 | 0.12868 | 0.13138 | 0.13004 | 0.12354 | 0.12873 | 0.12027 | 0.13713 | 0.12136 | 0.13213 | 0.056755 | 0.048762 | 0.046773 | 0.048839 | 0.047917 | 0.042046 | 0.049368 | 0.040486 | 0.049843 | 0.044767 | 0.053711 | 0.057145
VRF-Retro-Xlarge Ret |  | 2.1526 | 3.2982 | 0.65965 | 3.9579 | 4.1868 | 1.4326 | 16106.5136 | 86.3107 | 132.4438 | 0.34216 | 0.02045 | 0.00040466 | 0.13498 | 0.12137 | 0.13966 | 0.12993 | 0.13265 | 0.13131 | 0.12475 | 0.12998 | 0.12144 | 0.13847 | 0.12254 | 0.13341 | 0.057307 | 0.049236 | 0.047228 | 0.049314 | 0.048384 | 0.042455 | 0.049848 | 0.04088 | 0.050328 | 0.045203 | 0.054234 | 0.057701
VRF-Retro-Large Ret |  | 2.1657 | 3.3975 | 0.67949 | 4.0769 | 4.3128 | 1.4413 | 16490.5927 | 88.6234 | 135.8566 | 0.33419 | 0.020575 | 0.00040713 | 0.1358 | 0.12211 | 0.14051 | 0.13072 | 0.13346 | 0.13211 | 0.12551 | 0.13077 | 0.12218 | 0.13931 | 0.12328 | 0.13422 | 0.057656 | 0.049536 | 0.047516 | 0.049614 | 0.048678 | 0.042714 | 0.050152 | 0.041129 | 0.050635 | 0.045478 | 0.054564 | 0.058053
VRF-Retro-School K-12 |  | 1.9865 | 3.0811 | 0.61622 | 3.6973 | 3.9112 | 1.2052 | 16303.8163 | 92.9433 | 139.6415 | 0.30814 | 0.018872 | 0.00018294 | 0.14893 | 0.13662 | 0.15036 | 0.14293 | 0.14625 | 0.14001 | 0.12388 | 0.14578 | 0.15036 | 0.1535 | 0.12855 | 0.13231 | 0.042638 | 0.031491 | 0.025835 | 0.020865 | 0.017977 | 0.015723 | 0.015412 | 0.016122 | 0.020744 | 0.015891 | 0.025846 | 0.038533

## M_Input_Retro
Data Set Name
Measure Index Name | VRF
Costs must be denominated in the same year as 'Input Cost Reference Year' = |  | 2012
| Cost inflator 2006 to 2012 | 1.1074
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105
Input Data | [7 empty] | Periodic Replacement Costs and Savings and Replacement Period | [5 empty] | Gas Inputs |  | Retro or LO | Early Retrofit Parameters
Category Name | Measure Name | Savings (kwh/yr) | Life (yrs) | Capital Cost | Annual O&M | Shape Pointer | Non-E Val ($/yr) | Cost 1 ($) | Period 1 | Cost 2 ($) | Period 2 | Cost 3 ($) | Period 3 | Savings (therms/yr) | Shape Pointer | R or L | Savings 2 (kWh) | Remaining Life (yrs) | Salvage Value ($)
VRF-Retro-Large Off | VRF-Retro-Large Off-ElecHt | 1.2424 | 20 | 0.89018 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Medium Off | VRF-Retro-Medium Off-ElecHt | 0.71452 | 20 | 0.58536 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Small Off | VRF-Retro-Small Off-ElecHt | 1.8177 | 20 | 0.81044 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Xlarge Ret | VRF-Retro-Xlarge Ret-ElecHt | 0.15413 | 20 | 0.16323 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Large Ret | VRF-Retro-Large Ret-ElecHt | 0.030809 | 20 | 0.032627 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Medium Ret | VRF-Retro-Medium Ret-ElecHt | 0.34919 | 20 | 0.36979 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Small Ret | VRF-Retro-Small Ret-ElecHt | 0.79484 | 20 | 0.84174 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-School K-12 | VRF-Retro-School K-12-ElecHt | 0.16666 | 20 | 0.17978 |  | Commercial-School-Vent | [9 empty] | L
VRF-Retro-University | VRF-Retro-University-ElecHt | 0.294 | 20 | 0.308 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Warehouse | VRF-Retro-Warehouse-ElecHt | 0.025667 | 20 | 0.01969 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Supermarket | VRF-Retro-Supermarket-ElecHt | 0.28967 | 20 | 0.22402 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-MiniMart | VRF-Retro-MiniMart-ElecHt | 0.073145 | 20 | 0.056567 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Restaurant | VRF-Retro-Restaurant-ElecHt | 0.24362 | 20 | 0.17181 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Lodging | VRF-Retro-Lodging-ElecHt | 2.4593 | 20 | 1.8991 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Hospital | VRF-Retro-Hospital-ElecHt | 0.42548 | 20 | 0.38161 |  | Commercial-Healthcare-Vent | [9 empty] | L
VRF-Retro-Residential Care | VRF-Retro-Residential Care-ElecHt | 1.9806 | 20 | 1.6212 |  | Commercial-Healthcare-Vent | [9 empty] | L
VRF-Retro-Assembly | VRF-Retro-Assembly-ElecHt | 0.46873 | 20 | 0.32772 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Other | VRF-Retro-Other-ElecHt | 0.9684 | 20 | 0.52174 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Large Off | VRF-Retro-Large Off-GasHt | 2.4659 | 20 | 2.552 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Medium Off | VRF-Retro-Medium Off-GasHt | 1.5255 | 20 | 1.5115 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Small Off | VRF-Retro-Small Off-GasHt | 1.4947 | 20 | 0.9626 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Xlarge Ret | VRF-Retro-Xlarge Ret-GasHt | 1.8487 | 20 | 3.135 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Large Ret | VRF-Retro-Large Ret-GasHt | 1.9842 | 20 | 3.3648 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Medium Ret | VRF-Retro-Medium Ret-GasHt | 1.6343 | 20 | 2.7715 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Small Ret | VRF-Retro-Small Ret-GasHt | 1.1446 | 20 | 1.941 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-School K-12 | VRF-Retro-School K-12-GasHt | 1.6796 | 20 | 2.9013 |  | Commercial-School-Vent | [9 empty] | L
VRF-Retro-University | VRF-Retro-University-GasHt | 1.632 | 20 | 2.7378 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Warehouse | VRF-Retro-Warehouse-GasHt | 2.7496 | 20 | 3.3778 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Supermarket | VRF-Retro-Supermarket-GasHt | 2.7997 | 20 | 2.983 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-MiniMart | VRF-Retro-MiniMart-GasHt | 5.1636 | 20 | 5.5017 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Restaurant | VRF-Retro-Restaurant-GasHt | 5.189 | 20 | 5.0417 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Lodging | VRF-Retro-Lodging-GasHt | 1.0561 | 20 | 1.1779 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-Retro-Hospital | VRF-Retro-Hospital-GasHt | 3.5499 | 20 | 4.8232 |  | Commercial-Healthcare-Vent | [9 empty] | L
VRF-Retro-Residential Care | VRF-Retro-Residential Care-GasHt | 1.7336 | 20 | 2.1496 |  | Commercial-Healthcare-Vent | [9 empty] | L
VRF-Retro-Assembly | VRF-Retro-Assembly-GasHt | 2.5144 | 20 | 2.663 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | l
VRF-Retro-Other | VRF-Retro-Other-GasHt | 3.043 | 20 | 2.4836 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | l
ProCost Results
Version: | ProCost 3.0 - Beta04
Run Time: | Thursday, 19 March , 2015 at 9:19 AM
Regurgitation of ProData input parameters which were used for this run
| Run Parameters |  | Run Parameters |  |  | Marginal Cost & Conservation Load Shape Parameters | [9 empty] | Sponsor Parameters | [5 empty] | Program Parameters |  |  | Utility System Parameters
| Run Type | Electric | Run Type | Electric |  | Marginal Costs and Savings Shape File | Q:\SeventhPlan\Conservation Analysis\Global EE Inputs\MC Files\MC_AND_LOADSHAPE_v3.0_24segment-7P-D9 - NewSegValues.xlsx |  |  | 6P MidC Final (with carbon) | [6 empty] | Customer | Wholesale Elec | Retail Elec | Nat Gas |  | Program Life (yrs) | 20 |  |  | Electric | Gas
| Negative B/C Ratios | Off | Negative B/C Ratios | Off |  | Marginal Elec Avoided Cost Input Worksheet | 7P Mid |  |  | Conservation Load Shapes | [5 empty] | Real After-Tax Cost of Capital | 0.068013 | 0.043878 | 0.053289 | 0.054479 |  | Program Start Date | 2016 |  | Bulk System T&D Loss Factor | 0.0040389 | 0.01
| Admin Cost @ Category Level | On | Admin Cost @ Category Level | On |  | Elec Savings Shape Input Worksheet | GLSShapes |  |  | 6P_Gas_Final | [5 empty] | Financial Life (years) | 12 | 12 | 1 | 1 |  | Present Value Time Zero | 2016 |  | Bulk System T&D Credit ($/kw-yr)($/dailytherm-yr) | 26 | 0
| Repeat Periodic Replacement | On | Repeat Periodic Replacement | On |  | Marginal Gas Avoided Cost Input Worksheet | 7P Gas |  |  | Conservation Load Shapes | [6 empty] | Customer | Wholesale Elec | Retail Elec | Nat Gas |  | Input Cost Reference Year | 2012 |  | Bulk System T&D I2R Loss Component (%) | 0.9 | N/A
[6 empty] | Gas Savings Shape Input Worksheet | GLSShapes | [8 empty] | Sponsor Share of Initial Capital Cost | 0.35 | 0.195 | 0.455 | 0 |  | Real Discount Rate | 0.04 |  | Local System Dist Loss Factor | 0.047399 | 0
| Run Type: | Electric |  |  |  | Marginal Elec CO2 per kWh Input Worksheet | CO2 lbs per kWh .95 |  |  | CO2 lbs per therm | [5 empty] | Sponsor Share of Annual O&M | 1 | 0 | 0 | 0 |  | Capital Real Escalation Rate | 0 |  | Local System Dist Credit ($/kw-yr)($/dailytherm-yr) | 31 | 0
| Negative B/C Ratios: | False: (Converts Negative B/C Ratios) |  |  |  | Marginal Gas CO2 per therm Input Worksheet | CO2 lbs per therm |  |  | Zero Dollars per ton CO2 | [5 empty] | Sponsor Share of Periodic Replacement Cost | 1 | 0 | 0 | 0 |  | Admin Cost (as % of Initial Capital Cost) | 0.2 |  | Local System Dist I2R Loss Component (%) | 0.7 | N/A
| Admin Cost / Category Level: | True: Admin Costs added at Category Results |  |  |  | Marginal Avoided Cost CO2 Input Worksheet | Zero Dollars per ton CO2 |  |  | LineLossShapes | [5 empty] | Sponsor Share of Admin Cost |  | 0.3 | 0.7 | 0 |  | Regional Act Conservation Credit (%) | 0 |  | Risk-Mitigation Credit (mills/kWh)(mills/therm) - Retro. | 0 | 0
| Periodic O&M Treatment: | True: (Periodic O&M Repeats over measure life) |  |  |  | Line Loss Shape Input Worksheet | LineLossShapes | [8 empty] | Last Year of Non-Customer O&M & Period Replacement |  | 20 |  |  |  | Report Annual Carbon Saved for Year | 2018 |  | Risk-Mitigation Credit (mills/kWh)(mills/therm) - Lost Op. | 0 | 0
Measure Results; Sorted in same order as input
Total Results |  | Measure Input Data | [8 empty] | Savings | [5 empty] | PV Capital |  |  |  | PV Admin |  |  |  | PV O&M |  |  |  | PV Periodic Repl. |  |  |  | Total PV Capital, O&M and Periodic Repl Costs |  |  |  |  | PV Wholesale Electric Utility Costs & Benefits | [6 empty] | PV Retail Electric Utility Costs & Benefits | [6 empty] | PV Electric Utility System Costs & Benefits | [5 empty] | Electric Utility System Economics |  | Sponsor Levelized Cost (mills/kwh) |  |  |  |  | PV Regional Costs & Benefits | [15 empty] | TRC Economics |  | Physical CO2 | [6 empty] | Gas Inputs |  |  |  | PV Gas Utility System Costs & Benefits |  |  |  |  | Gas Utility System Economics
Category | Measure | Measure Life | Site Savings (kWh) | Site Savings (therms) | Capital Cost ($/unit) | Annual O&M Cost ($/unit) | PV Per. Repl. Cost ($/unit) | Load Shape (electric) | Diversified Load Factor (electric) | Wholesale Power Coincidence Factor (electric) | Wholesale Electric Energy (kWh) | Wholesale Electric Demand (kw) | Retail Electric Demand (kW) | Wholesale Gas Energy (therms/yr) | Wholesale Gas Demand (therms/day) | Retail Gas Demand (therms/day) | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Total | Wholesale Utility System Energy | Wholesale Utility System T&D Def. Cap. | Wholesale Utility System Act C-E Credit | Wholesale Utility System Risk Mitigation Benefit | Wholesale Utility System Total System Benefit | Wholesale Utility System Total Non-Consumer Cost | Wholesale Utility System B/C Ratio | Retail Utility System Energy | Retail Utility System T&D Def. Cap. | Retail Utility System Act C-E Credit | Retail Utility System Risk Mitigation Benefit | Retail Utility System Total System Benefit | Retail Utility System Total Non-Consumer Cost | Retail Utility System System B/C Ratio | Utility System Energy | Utility System T&D Def. Cap. | Utility System Act C-E Credit | Utility System Total Risk Mitigation Benefit | Utility System Total System Benefit | Utility System Total Non-Consumer Cost | Utility System Net Levelized Cost (Net of Elec T&D Capacity Benefits, Act Credit & Risk-Mitigation Benefit) in mills/kwh | Utility System System B/C Ratio | Wholesale Electric Levelized Cost | Retail Electric Levelized Cost | Natural Gas Levelized Cost | Customer Levelized Cost | Total Levelized Cost | PV Regional Electric Energy | PV Regional Gas Energy | PV Regional Electric T&D Def. Cap. | PV Regional Gas T&D Def. Cap. | PV Regional Electric System CO2 | PV Regional Gas System CO2 | PV Regional Electric System Risk-Mitigation Benefit | PV Regional Gas System Risk-Mitigation Benefit | PV Regional Non-E Value | PV Regional Act Credit | PV Regional Capital Cost | PV Regional Admin Cost | PV Regional Annual O&M Cost | PV Regional Periodic Replacement Cost | PV Total Regional Benefit | PV Total Regional Cost | TRC B/C Ratio | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | Electric System CO2 Avoided (Lifetime Tons) | Gas System CO2 Avoided (Lifetime Tons) | Total System CO2 Avoided (Lifetime Tons) | Electric System CO2 Avoided (Annual Tons in 2018) | Gas System CO2 Avoided (Annual Tons in 2018) | Total System CO2 Avoided (Annual Tons in 2018) |  | Gas Site Savings (therms) | Load Shape (gas) | Diversitfied Load Factor (gas) | Wholesale Coincidence Factor (gas) | Total Gas Utility System Energy | Gas Utility System T&D Def. Cap. | Gas Utility System Risk Mitigation Benefit | Gas Utility System Total System Benefit | Gas Utility System Total Non-Consumer Cost | Gas Utility System Net Levelized Cost (Net of Gas T&D Capacity Benefits & Risk-Mitigation Benefits) in cents/therm | Gas Utility System System B/C Ratio
VRF-Retro-Large Off | VRF-Retro-Large Off-ElecHt | 20 | 1.2424 | 0 | 0.89018 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.3354 | 0.00025103 | 0.00024922 | 0 | 0 | 0 | 0.17751 | 0.41021 | 0 | 0.36425 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17751 | 0.41021 | 0 | 0.36425 | 0.95197 | 0.695 | 0.088701 | 0 | 0 | 0.7837 | 0.17751 | 4.4149 | 0.695 | 0.105 | 0 | 0 | 0.79999 | 0.41021 | 1.9502 | 0.695 | 0.1937 | 0 | 0 | 0.8887 | 0.58772 | 21.7117 | 1.5121 | 9.7814 | 22.6034 | 0 | 20.0713 | 52.4562 | 0.695 | 0 | 0.1937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95197 |  | 0 | 0 | 0.8887 | 0.95197 | 0.93353 | 41.783 | 0.012686 | 0 | 0.012686 | 0.0006343 | 0 | 0.0006343 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Medium Off | VRF-Retro-Medium Off-ElecHt | 20 | 0.71452 | 0 | 0.58536 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.76796 | 0.00014437 | 0.00014332 | 0 | 0 | 0 | 0.11673 | 0.26974 | 0 | 0.23952 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11673 | 0.26974 | 0 | 0.23952 | 0.626 | 0.39969 | 0.051012 | 0 | 0 | 0.45071 | 0.11673 | 3.8611 | 0.39969 | 0.060383 | 0 | 0 | 0.46008 | 0.26974 | 1.7056 | 0.39969 | 0.11139 | 0 | 0 | 0.51109 | 0.38647 | 26.3563 | 1.3224 | 11.1843 | 25.8452 | 0 | 22.9498 | 59.9793 | 0.39969 | 0 | 0.11139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.626 |  | 0 | 0 | 0.51109 | 0.626 | 0.81644 | 49.3061 | 0.0072957 | 0 | 0.0072957 | 0.00036478 | 0 | 0.00036478 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Small Off | VRF-Retro-Small Off-ElecHt | 20 | 1.8177 | 0 | 0.81044 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.9537 | 0.00036727 | 0.00036462 | 0 | 0 | 0 | 0.16161 | 0.37346 | 0 | 0.33163 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16161 | 0.37346 | 0 | 0.33163 | 0.8667 | 1.0168 | 0.12977 | 0 | 0 | 1.1466 | 0.16161 | 7.0946 | 1.0168 | 0.15361 | 0 | 0 | 1.1704 | 0.37346 | 3.134 | 1.0168 | 0.28339 | 0 | 0 | 1.3002 | 0.53508 | 9.4794 | 2.4299 | 6.0868 | 14.0657 | 0 | 12.49 | 32.6426 | 1.0168 | 0 | 0.28339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8667 |  | 0 | 0 | 1.3002 | 0.8667 | 1.5002 | 21.9694 | 0.01856 | 0 | 0.01856 | 0.000928 | 0 | 0.000928 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Xlarge Ret | VRF-Retro-Xlarge Ret-ElecHt | 20 | 0.15413 | 0 | 0.16323 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.16566 | 3.1142e-05 | 3.0917e-05 | 0 | 0 | 0 | 0.03255 | 0.075218 | 0 | 0.066792 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03255 | 0.075218 | 0 | 0.066792 | 0.17456 | 0.086219 | 0.011004 | 0 | 0 | 0.097223 | 0.03255 | 2.9869 | 0.086219 | 0.013025 | 0 | 0 | 0.099245 | 0.075218 | 1.3194 | 0.086219 | 0.024029 | 0 | 0 | 0.11025 | 0.10777 | 37.1943 | 1.023 | 14.4578 | 33.4097 | 0 | 29.667 | 77.5344 | 0.086219 | 0 | 0.024029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17456 |  | 0 | 0 | 0.11025 | 0.17456 | 0.63158 | 66.8613 | 0.0015738 | 0 | 0.0015738 | 7.8689e-05 | 0 | 7.8689e-05 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Large Ret | VRF-Retro-Large Ret-ElecHt | 20 | 0.030809 | 0 | 0.032627 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.033113 | 6.2248e-06 | 6.1799e-06 | 0 | 0 | 0 | 0.0065063 | 0.015035 | 0 | 0.013351 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0065063 | 0.015035 | 0 | 0.013351 | 0.034892 | 0.017234 | 0.0021995 | 0 | 0 | 0.019434 | 0.0065063 | 2.9869 | 0.017234 | 0.0026036 | 0 | 0 | 0.019838 | 0.015035 | 1.3194 | 0.017234 | 0.0048031 | 0 | 0 | 0.022037 | 0.021541 | 37.1943 | 1.023 | 14.4578 | 33.4097 | 0 | 29.667 | 77.5344 | 0.017234 | 0 | 0.0048031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034892 |  | 0 | 0 | 0.022037 | 0.034892 | 0.63158 | 66.8613 | 0.00031458 | 0 | 0.00031458 | 1.5729e-05 | 0 | 1.5729e-05 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Medium Ret | VRF-Retro-Medium Ret-ElecHt | 20 | 0.34919 | 0 | 0.36979 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.3753 | 7.0552e-05 | 7.0043e-05 | 0 | 0 | 0 | 0.073742 | 0.17041 | 0 | 0.15132 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073742 | 0.17041 | 0 | 0.15132 | 0.39547 | 0.19533 | 0.024929 | 0 | 0 | 0.22026 | 0.073742 | 2.9869 | 0.19533 | 0.029509 | 0 | 0 | 0.22484 | 0.17041 | 1.3194 | 0.19533 | 0.054439 | 0 | 0 | 0.24977 | 0.24415 | 37.1943 | 1.023 | 14.4578 | 33.4097 | 0 | 29.667 | 77.5344 | 0.19533 | 0 | 0.054439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39547 |  | 0 | 0 | 0.24977 | 0.39547 | 0.63158 | 66.8613 | 0.0035654 | 0 | 0.0035654 | 0.00017827 | 0 | 0.00017827 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Small Ret | VRF-Retro-Small Ret-ElecHt | 20 | 0.79484 | 0 | 0.84174 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.85429 | 0.00016059 | 0.00015943 | 0 | 0 | 0 | 0.16785 | 0.38789 | 0 | 0.34443 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16785 | 0.38789 | 0 | 0.34443 | 0.90018 | 0.44462 | 0.056746 | 0 | 0 | 0.50137 | 0.16785 | 2.9869 | 0.44462 | 0.06717 | 0 | 0 | 0.51179 | 0.38789 | 1.3194 | 0.44462 | 0.12392 | 0 | 0 | 0.56854 | 0.55574 | 37.1943 | 1.023 | 14.4578 | 33.4097 | 0 | 29.667 | 77.5344 | 0.44462 | 0 | 0.12392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90018 |  | 0 | 0 | 0.56854 | 0.90018 | 0.63158 | 66.8613 | 0.0081158 | 0 | 0.0081158 | 0.00040579 | 0 | 0.00040579 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-School K-12 | VRF-Retro-School K-12-ElecHt | 20 | 0.16666 | 0 | 0.17978 | 0 | 0 | Commercial-School-Vent |  |  | 0.17932 | 1.6514e-05 | 1.6395e-05 | 0 | 0 | 0 | 0.03585 | 0.082845 | 0 | 0.073564 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03585 | 0.082845 | 0 | 0.073564 | 0.19226 | 0.096047 | 0.0058352 | 0 | 0 | 0.10188 | 0.03585 | 2.8419 | 0.096047 | 0.0069071 | 0 | 0 | 0.10295 | 0.082845 | 1.2427 | 0.096047 | 0.012742 | 0 | 0 | 0.10879 | 0.11869 | 43.4759 | 0.91655 | 14.7106 | 33.9939 | 0 | 30.1857 | 78.8903 | 0.096047 | 0 | 0.012742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19226 |  | 0 | 0 | 0.10879 | 0.19226 | 0.56585 | 73.6616 | 0.0017036 | 0 | 0.0017036 | 8.5178e-05 | 0 | 8.5178e-05 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-University | VRF-Retro-University-ElecHt | 20 | 0.294 | 0 | 0.308 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.31599 | 5.9402e-05 | 5.8973e-05 | 0 | 0 | 0 | 0.06142 | 0.14193 | 0 | 0.12603 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06142 | 0.14193 | 0 | 0.12603 | 0.32938 | 0.16446 | 0.02099 | 0 | 0 | 0.18545 | 0.06142 | 3.0194 | 0.16446 | 0.024845 | 0 | 0 | 0.1893 | 0.14193 | 1.3338 | 0.16446 | 0.045835 | 0 | 0 | 0.21029 | 0.20335 | 36.6794 | 1.0341 | 14.3023 | 33.0503 | 0 | 29.3479 | 76.7005 | 0.16446 | 0 | 0.045835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32938 |  | 0 | 0 | 0.21029 | 0.32938 | 0.63845 | 66.0273 | 0.0030019 | 0 | 0.0030019 | 0.0001501 | 0 | 0.0001501 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Warehouse | VRF-Retro-Warehouse-ElecHt | 20 | 0.025667 | 0 | 0.01969 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.027587 | 5.1859e-06 | 5.1485e-06 | 0 | 0 | 0 | 0.0039265 | 0.0090736 | 0 | 0.0080571 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0039265 | 0.0090736 | 0 | 0.0080571 | 0.021057 | 0.014358 | 0.0018324 | 0 | 0 | 0.01619 | 0.0039265 | 4.1233 | 0.014358 | 0.002169 | 0 | 0 | 0.016527 | 0.0090736 | 1.8214 | 0.014358 | 0.0040015 | 0 | 0 | 0.018359 | 0.013 | 24.002 | 1.4122 | 10.4732 | 24.202 | 0 | 21.4907 | 56.1659 | 0.014358 | 0 | 0.0040015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021057 |  | 0 | 0 | 0.018359 | 0.021057 | 0.87187 | 45.4927 | 0.00026207 | 0 | 0.00026207 | 1.3104e-05 | 0 | 1.3104e-05 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Supermarket | VRF-Retro-Supermarket-ElecHt | 20 | 0.28967 | 0 | 0.22402 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.31133 | 5.8527e-05 | 5.8104e-05 | 0 | 0 | 0 | 0.044672 | 0.10323 | 0 | 0.091666 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044672 | 0.10323 | 0 | 0.091666 | 0.23957 | 0.16204 | 0.02068 | 0 | 0 | 0.18272 | 0.044672 | 4.0902 | 0.16204 | 0.024479 | 0 | 0 | 0.18652 | 0.10323 | 1.8068 | 0.16204 | 0.04516 | 0 | 0 | 0.2072 | 0.1479 | 24.2826 | 1.4009 | 10.558 | 24.3978 | 0 | 21.6647 | 56.6205 | 0.16204 | 0 | 0.04516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23957 |  | 0 | 0 | 0.2072 | 0.23957 | 0.86487 | 45.9473 | 0.0029577 | 0 | 0.0029577 | 0.00014788 | 0 | 0.00014788 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-MiniMart | VRF-Retro-MiniMart-ElecHt | 20 | 0.073145 | 0 | 0.056567 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.078615 | 1.4779e-05 | 1.4672e-05 | 0 | 0 | 0 | 0.01128 | 0.026067 | 0 | 0.023147 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01128 | 0.026067 | 0 | 0.023147 | 0.060494 | 0.040916 | 0.005222 | 0 | 0 | 0.046138 | 0.01128 | 4.0902 | 0.040916 | 0.0061813 | 0 | 0 | 0.047097 | 0.026067 | 1.8068 | 0.040916 | 0.011403 | 0 | 0 | 0.052319 | 0.037347 | 24.2826 | 1.4009 | 10.558 | 24.3978 | 0 | 21.6647 | 56.6205 | 0.040916 | 0 | 0.011403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.060494 |  | 0 | 0 | 0.052319 | 0.060494 | 0.86487 | 45.9473 | 0.00074685 | 0 | 0.00074685 | 3.7342e-05 | 0 | 3.7342e-05 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Restaurant | VRF-Retro-Restaurant-ElecHt | 20 | 0.24362 | 0 | 0.17181 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.26184 | 4.9222e-05 | 4.8867e-05 | 0 | 0 | 0 | 0.034261 | 0.079171 | 0 | 0.070302 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034261 | 0.079171 | 0 | 0.070302 | 0.18373 | 0.13628 | 0.017393 | 0 | 0 | 0.15367 | 0.034261 | 4.4853 | 0.13628 | 0.020588 | 0 | 0 | 0.15686 | 0.079171 | 1.9813 | 0.13628 | 0.03798 | 0 | 0 | 0.17426 | 0.11343 | 21.2034 | 1.5362 | 9.6279 | 22.2486 | 0 | 19.7562 | 51.6328 | 0.13628 | 0 | 0.03798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18373 |  | 0 | 0 | 0.17426 | 0.18373 | 0.94842 | 40.9596 | 0.0024875 | 0 | 0.0024875 | 0.00012437 | 0 | 0.00012437 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Lodging | VRF-Retro-Lodging-ElecHt | 20 | 2.4593 | 0 | 1.8991 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 2.6433 | 0.0004969 | 0.00049331 | 0 | 0 | 0 | 0.3787 | 0.87511 | 0 | 0.77708 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3787 | 0.87511 | 0 | 0.77708 | 2.0309 | 1.3757 | 0.17558 | 0 | 0 | 1.5513 | 0.3787 | 4.0964 | 1.3757 | 0.20783 | 0 | 0 | 1.5835 | 0.87511 | 1.8095 | 1.3757 | 0.38341 | 0 | 0 | 1.7591 | 1.2538 | 24.2297 | 1.403 | 10.542 | 24.3609 | 0 | 21.6319 | 56.5348 | 1.3757 | 0 | 0.38341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0309 |  | 0 | 0 | 1.7591 | 2.0309 | 0.86618 | 45.8616 | 0.025111 | 0 | 0.025111 | 0.0012555 | 0 | 0.0012555 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Hospital | VRF-Retro-Hospital-ElecHt | 20 | 0.42548 | 0 | 0.38161 | 0 | 0 | Commercial-Healthcare-Vent |  |  | 0.4567 | 5.5381e-05 | 5.4981e-05 | 0 | 0 | 0 | 0.076099 | 0.17585 | 0 | 0.15615 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076099 | 0.17585 | 0 | 0.15615 | 0.40811 | 0.23027 | 0.019569 | 0 | 0 | 0.24984 | 0.076099 | 3.2831 | 0.23027 | 0.023163 | 0 | 0 | 0.25343 | 0.17585 | 1.4412 | 0.23027 | 0.042732 | 0 | 0 | 0.273 | 0.25195 | 33.7088 | 1.0836 | 12.2608 | 28.3328 | 0 | 25.1588 | 65.7524 | 0.23027 | 0 | 0.042732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40811 |  | 0 | 0 | 0.273 | 0.40811 | 0.66895 | 58.8676 | 0.0043387 | 0 | 0.0043387 | 0.00021693 | 0 | 0.00021693 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Residential Care | VRF-Retro-Residential Care-ElecHt | 20 | 1.9806 | 0 | 1.6212 | 0 | 0 | Commercial-Healthcare-Vent |  |  | 2.1259 | 0.0002578 | 0.00025594 | 0 | 0 | 0 | 0.32328 | 0.74706 | 0 | 0.66337 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32328 | 0.74706 | 0 | 0.66337 | 1.7337 | 1.0719 | 0.091092 | 0 | 0 | 1.163 | 0.32328 | 3.5975 | 1.0719 | 0.10783 | 0 | 0 | 1.1797 | 0.74706 | 1.5792 | 1.0719 | 0.19892 | 0 | 0 | 1.2708 | 1.0703 | 30.1614 | 1.1873 | 11.1893 | 25.8569 | 0 | 22.9602 | 60.0065 | 1.0719 | 0 | 0.19892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7337 |  | 0 | 0 | 1.2708 | 1.7337 | 0.73301 | 53.1216 | 0.020197 | 0 | 0.020197 | 0.0010098 | 0 | 0.0010098 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Assembly | VRF-Retro-Assembly-ElecHt | 20 | 0.46873 | 0 | 0.32772 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 0.50379 | 9.4706e-05 | 9.4022e-05 | 0 | 0 | 0 | 0.065352 | 0.15102 | 0 | 0.1341 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065352 | 0.15102 | 0 | 0.1341 | 0.35047 | 0.2622 | 0.033464 | 0 | 0 | 0.29567 | 0.065352 | 4.5242 | 0.2622 | 0.039612 | 0 | 0 | 0.30181 | 0.15102 | 1.9985 | 0.2622 | 0.073076 | 0 | 0 | 0.33528 | 0.21637 | 20.9289 | 1.5496 | 9.545 | 22.0571 | 0 | 19.5861 | 51.1882 | 0.2622 | 0 | 0.073076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35047 |  | 0 | 0 | 0.33528 | 0.35047 | 0.95666 | 40.515 | 0.0047861 | 0 | 0.0047861 | 0.0002393 | 0 | 0.0002393 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Other | VRF-Retro-Other-ElecHt | 20 | 0.9684 | 0 | 0.52174 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.0408 | 0.00019566 | 0.00019425 | 0 | 0 | 0 | 0.10404 | 0.24043 | 0 | 0.21349 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10404 | 0.24043 | 0 | 0.21349 | 0.55796 | 0.54171 | 0.069137 | 0 | 0 | 0.61085 | 0.10404 | 5.8712 | 0.54171 | 0.081838 | 0 | 0 | 0.62355 | 0.24043 | 2.5935 | 0.54171 | 0.15097 | 0 | 0 | 0.69269 | 0.34447 | 13.6789 | 2.0109 | 7.3552 | 16.9968 | 0 | 15.0928 | 39.4449 | 0.54171 | 0 | 0.15097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55796 |  | 0 | 0 | 0.69269 | 0.55796 | 1.2415 | 28.7717 | 0.009888 | 0 | 0.009888 | 0.0004944 | 0 | 0.0004944 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Large Off | VRF-Retro-Large Off-GasHt | 20 | 2.4659 | 0 | 2.552 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 2.6503 | 0.00049823 | 0.00049463 | 0 | 0 | 0 | 0.5089 | 1.176 | 0 | 1.0443 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5089 | 1.176 | 0 | 1.0443 | 2.7292 | 1.3794 | 0.17605 | 0 | 0 | 1.5554 | 0.5089 | 3.0565 | 1.3794 | 0.20839 | 0 | 0 | 1.5878 | 1.176 | 1.3502 | 1.3794 | 0.38444 | 0 | 0 | 1.7638 | 1.6849 | 36.105 | 1.0468 | 14.1288 | 32.6494 | 0 | 28.9919 | 75.77 | 1.3794 | 0 | 0.38444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7292 |  | 0 | 0 | 1.7638 | 2.7292 | 0.64629 | 65.0969 | 0.025178 | 0 | 0.025178 | 0.0012589 | 0 | 0.0012589 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Medium Off | VRF-Retro-Medium Off-GasHt | 20 | 1.5255 | 0 | 1.5115 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.6396 | 0.00030822 | 0.000306 | 0 | 0 | 0 | 0.3014 | 0.6965 | 0 | 0.61847 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3014 | 0.6965 | 0 | 0.61847 | 1.6164 | 0.85335 | 0.10891 | 0 | 0 | 0.96226 | 0.3014 | 3.1926 | 0.85335 | 0.12892 | 0 | 0 | 0.98227 | 0.6965 | 1.4103 | 0.85335 | 0.23783 | 0 | 0 | 1.0912 | 0.9979 | 34.1103 | 1.0935 | 13.5263 | 31.2572 | 0 | 27.7556 | 72.539 | 0.85335 | 0 | 0.23783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6164 |  | 0 | 0 | 1.0912 | 1.6164 | 0.67508 | 61.8659 | 0.015576 | 0 | 0.015576 | 0.00077882 | 0 | 0.00077882 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Small Off | VRF-Retro-Small Off-GasHt | 20 | 1.4947 | 0 | 0.9626 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.6065 | 0.000302 | 0.00029982 | 0 | 0 | 0 | 0.19195 | 0.44358 | 0 | 0.39389 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19195 | 0.44358 | 0 | 0.39389 | 1.0294 | 0.83611 | 0.10671 | 0 | 0 | 0.94282 | 0.19195 | 4.9117 | 0.83611 | 0.12631 | 0 | 0 | 0.96242 | 0.44358 | 2.1697 | 0.83611 | 0.23302 | 0 | 0 | 1.0691 | 0.63553 | 18.4361 | 1.6823 | 8.7921 | 20.3172 | 0 | 18.0411 | 47.1504 | 0.83611 | 0 | 0.23302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0294 |  | 0 | 0 | 1.0691 | 1.0294 | 1.0386 | 36.4772 | 0.015262 | 0 | 0.015262 | 0.00076308 | 0 | 0.00076308 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Xlarge Ret | VRF-Retro-Xlarge Ret-GasHt | 20 | 1.8487 | 0 | 3.135 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.9869 | 0.00037352 | 0.00037082 | 0 | 0 | 0 | 0.62516 | 1.4447 | 0 | 1.2828 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62516 | 1.4447 | 0 | 1.2828 | 3.3526 | 1.0341 | 0.13198 | 0 | 0 | 1.1661 | 0.62516 | 1.8653 | 1.0341 | 0.15623 | 0 | 0 | 1.1904 | 1.4447 | 0.82397 | 1.0341 | 0.28821 | 0 | 0 | 1.3223 | 2.0698 | 65.9774 | 0.63887 | 23.1513 | 53.4992 | 0 | 47.5059 | 124.1565 | 1.0341 | 0 | 0.28821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3526 |  | 0 | 0 | 1.3223 | 3.3526 | 0.39442 | 113.4833 | 0.018876 | 0 | 0.018876 | 0.0009438 | 0 | 0.0009438 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Large Ret | VRF-Retro-Large Ret-GasHt | 20 | 1.9842 | 0 | 3.3648 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 2.1326 | 0.0004009 | 0.00039801 | 0 | 0 | 0 | 0.67099 | 1.5506 | 0 | 1.3769 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67099 | 1.5506 | 0 | 1.3769 | 3.5984 | 1.1099 | 0.14166 | 0 | 0 | 1.2516 | 0.67099 | 1.8653 | 1.1099 | 0.16768 | 0 | 0 | 1.2776 | 1.5506 | 0.82397 | 1.1099 | 0.30934 | 0 | 0 | 1.4193 | 2.2216 | 65.9774 | 0.63887 | 23.1513 | 53.4992 | 0 | 47.5059 | 124.1565 | 1.1099 | 0 | 0.30934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5984 |  | 0 | 0 | 1.4193 | 3.5984 | 0.39442 | 113.4833 | 0.02026 | 0 | 0.02026 | 0.001013 | 0 | 0.001013 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Medium Ret | VRF-Retro-Medium Ret-GasHt | 20 | 1.6343 | 0 | 2.7715 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.7566 | 0.00033021 | 0.00032783 | 0 | 0 | 0 | 0.55267 | 1.2771 | 0 | 1.1341 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55267 | 1.2771 | 0 | 1.1341 | 2.9639 | 0.91422 | 0.11668 | 0 | 0 | 1.0309 | 0.55267 | 1.8653 | 0.91422 | 0.13811 | 0 | 0 | 1.0523 | 1.2771 | 0.82397 | 0.91422 | 0.25479 | 0 | 0 | 1.169 | 1.8298 | 65.9774 | 0.63887 | 23.1513 | 53.4992 | 0 | 47.5059 | 124.1565 | 0.91422 | 0 | 0.25479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9639 |  | 0 | 0 | 1.169 | 2.9639 | 0.39442 | 113.4833 | 0.016688 | 0 | 0.016688 | 0.00083437 | 0 | 0.00083437 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Small Ret | VRF-Retro-Small Ret-GasHt | 20 | 1.1446 | 0 | 1.941 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.2302 | 0.00023126 | 0.00022959 | 0 | 0 | 0 | 0.38706 | 0.89444 | 0 | 0.79424 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38706 | 0.89444 | 0 | 0.79424 | 2.0757 | 0.64027 | 0.081715 | 0 | 0 | 0.72198 | 0.38706 | 1.8653 | 0.64027 | 0.096727 | 0 | 0 | 0.73699 | 0.89444 | 0.82397 | 0.64027 | 0.17844 | 0 | 0 | 0.81871 | 1.2815 | 65.9774 | 0.63887 | 23.1513 | 53.4992 | 0 | 47.5059 | 124.1565 | 0.64027 | 0 | 0.17844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0757 |  | 0 | 0 | 0.81871 | 2.0757 | 0.39442 | 113.4833 | 0.011687 | 0 | 0.011687 | 0.00058434 | 0 | 0.00058434 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-School K-12 | VRF-Retro-School K-12-GasHt | 20 | 1.6796 | 0 | 2.9013 | 0 | 0 | Commercial-School-Vent |  |  | 1.8072 | 0.00016643 | 0.00016523 | 0 | 0 | 0 | 0.57856 | 1.337 | 0 | 1.1872 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57856 | 1.337 | 0 | 1.1872 | 3.1027 | 0.96798 | 0.058808 | 0 | 0 | 1.0268 | 0.57856 | 1.7747 | 0.96798 | 0.069611 | 0 | 0 | 1.0376 | 1.337 | 0.77608 | 0.96798 | 0.12842 | 0 | 0 | 1.0964 | 1.9155 | 72.7623 | 0.57238 | 23.5562 | 54.4347 | 0 | 48.3366 | 126.3275 | 0.96798 | 0 | 0.12842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1027 |  | 0 | 0 | 1.0964 | 3.1027 | 0.35337 | 121.0989 | 0.017169 | 0 | 0.017169 | 0.00085843 | 0 | 0.00085843 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-University | VRF-Retro-University-GasHt | 20 | 1.632 | 0 | 2.7378 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.7541 | 0.00032974 | 0.00032736 | 0 | 0 | 0 | 0.54595 | 1.2616 | 0 | 1.1203 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54595 | 1.2616 | 0 | 1.1203 | 2.9278 | 0.91292 | 0.11651 | 0 | 0 | 1.0294 | 0.54595 | 1.8856 | 0.91292 | 0.13792 | 0 | 0 | 1.0508 | 1.2616 | 0.83293 | 0.91292 | 0.25443 | 0 | 0 | 1.1673 | 1.8076 | 65.1529 | 0.64581 | 22.9023 | 52.9238 | 0 | 46.995 | 122.821 | 0.91292 | 0 | 0.25443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9278 |  | 0 | 0 | 1.1673 | 2.9278 | 0.39871 | 112.1479 | 0.016664 | 0 | 0.016664 | 0.00083318 | 0 | 0.00083318 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Warehouse | VRF-Retro-Warehouse-GasHt | 20 | 2.7496 | 0 | 3.3778 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 2.9553 | 0.00055555 | 0.00055154 | 0 | 0 | 0 | 0.67357 | 1.5565 | 0 | 1.3822 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67357 | 1.5565 | 0 | 1.3822 | 3.6122 | 1.5381 | 0.1963 | 0 | 0 | 1.7344 | 0.67357 | 2.5749 | 1.5381 | 0.23237 | 0 | 0 | 1.7705 | 1.5565 | 1.1375 | 1.5381 | 0.42867 | 0 | 0 | 1.9668 | 2.2301 | 44.8524 | 0.88193 | 16.7708 | 38.7548 | 0 | 34.4133 | 89.9388 | 1.5381 | 0 | 0.42867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6122 |  | 0 | 0 | 1.9668 | 3.6122 | 0.54447 | 79.2657 | 0.028076 | 0 | 0.028076 | 0.0014038 | 0 | 0.0014038 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Supermarket | VRF-Retro-Supermarket-GasHt | 20 | 2.7997 | 0 | 2.983 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 3.0091 | 0.00056566 | 0.00056158 | 0 | 0 | 0 | 0.59484 | 1.3746 | 0 | 1.2206 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59484 | 1.3746 | 0 | 1.2206 | 3.19 | 1.5661 | 0.19988 | 0 | 0 | 1.766 | 0.59484 | 2.9688 | 1.5661 | 0.23659 | 0 | 0 | 1.8027 | 1.3746 | 1.3114 | 1.5661 | 0.43647 | 0 | 0 | 2.0026 | 1.9694 | 37.4864 | 1.0168 | 14.546 | 33.6136 | 0 | 29.848 | 78.0076 | 1.5661 | 0 | 0.43647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.19 |  | 0 | 0 | 2.0026 | 3.19 | 0.62775 | 67.3345 | 0.028586 | 0 | 0.028586 | 0.0014293 | 0 | 0.0014293 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-MiniMart | VRF-Retro-MiniMart-GasHt | 20 | 5.1636 | 0 | 5.5017 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 5.5498 | 0.0010433 | 0.0010358 | 0 | 0 | 0 | 1.0971 | 2.5353 | 0 | 2.2512 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 2.5353 | 0 | 2.2512 | 5.8836 | 2.8884 | 0.36864 | 0 | 0 | 3.2571 | 1.0971 | 2.9688 | 2.8884 | 0.43636 | 0 | 0 | 3.3248 | 2.5353 | 1.3114 | 2.8884 | 0.80501 | 0 | 0 | 3.6934 | 3.6324 | 37.4864 | 1.0168 | 14.546 | 33.6136 | 0 | 29.848 | 78.0076 | 2.8884 | 0 | 0.80501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8836 |  | 0 | 0 | 3.6934 | 5.8836 | 0.62775 | 67.3345 | 0.052724 | 0 | 0.052724 | 0.0026362 | 0 | 0.0026362 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Restaurant | VRF-Retro-Restaurant-GasHt | 20 | 5.189 | 0 | 5.0417 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 5.5771 | 0.0010484 | 0.0010408 | 0 | 0 | 0 | 1.0054 | 2.3233 | 0 | 2.063 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0054 | 2.3233 | 0 | 2.063 | 5.3917 | 2.9026 | 0.37046 | 0 | 0 | 3.2731 | 1.0054 | 3.2556 | 2.9026 | 0.43851 | 0 | 0 | 3.3411 | 2.3233 | 1.4381 | 2.9026 | 0.80896 | 0 | 0 | 3.7116 | 3.3287 | 33.2441 | 1.115 | 13.2647 | 30.6526 | 0 | 27.2187 | 71.136 | 2.9026 | 0 | 0.80896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3917 |  | 0 | 0 | 3.7116 | 5.3917 | 0.68839 | 60.4628 | 0.052983 | 0 | 0.052983 | 0.0026491 | 0 | 0.0026491 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Lodging | VRF-Retro-Lodging-GasHt | 20 | 1.0561 | 0 | 1.1779 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 1.1351 | 0.00021338 | 0.00021184 | 0 | 0 | 0 | 0.23489 | 0.5428 | 0 | 0.482 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23489 | 0.5428 | 0 | 0.482 | 1.2597 | 0.59075 | 0.075396 | 0 | 0 | 0.66615 | 0.23489 | 2.836 | 0.59075 | 0.089246 | 0 | 0 | 0.68 | 0.5428 | 1.2528 | 0.59075 | 0.16464 | 0 | 0 | 0.75539 | 0.7777 | 39.7421 | 0.97132 | 15.2273 | 35.188 | 0 | 31.246 | 81.6613 | 0.59075 | 0 | 0.16464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2597 |  | 0 | 0 | 0.75539 | 1.2597 | 0.59966 | 70.9881 | 0.010783 | 0 | 0.010783 | 0.00053915 | 0 | 0.00053915 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Hospital | VRF-Retro-Hospital-GasHt | 20 | 3.5499 | 0 | 4.8232 | 0 | 0 | Commercial-Healthcare-Vent |  |  | 3.8104 | 0.00046206 | 0.00045872 | 0 | 0 | 0 | 0.96181 | 2.2226 | 0 | 1.9736 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96181 | 2.2226 | 0 | 1.9736 | 5.158 | 1.9212 | 0.16327 | 0 | 0 | 2.0845 | 0.96181 | 2.1673 | 1.9212 | 0.19326 | 0 | 0 | 2.1145 | 2.2226 | 0.95136 | 1.9212 | 0.35653 | 0 | 0 | 2.2777 | 3.1844 | 54.6086 | 0.71528 | 18.5733 | 42.9201 | 0 | 38.112 | 99.6055 | 1.9212 | 0 | 0.35653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.158 |  | 0 | 0 | 2.2777 | 5.158 | 0.4416 | 92.7206 | 0.036199 | 0 | 0.036199 | 0.0018099 | 0 | 0.0018099 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Residential Care | VRF-Retro-Residential Care-GasHt | 20 | 1.7336 | 0 | 2.1496 | 0 | 0 | Commercial-Healthcare-Vent |  |  | 1.8608 | 0.00022565 | 0.00022402 | 0 | 0 | 0 | 0.42866 | 0.99056 | 0 | 0.87959 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42866 | 0.99056 | 0 | 0.87959 | 2.2988 | 0.93823 | 0.079732 | 0 | 0 | 1.018 | 0.42866 | 2.3748 | 0.93823 | 0.094379 | 0 | 0 | 1.0326 | 0.99056 | 1.0425 | 0.93823 | 0.17411 | 0 | 0 | 1.1123 | 1.4192 | 49.2349 | 0.78378 | 16.9503 | 39.1695 | 0 | 34.7815 | 90.9012 | 0.93823 | 0 | 0.17411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2988 |  | 0 | 0 | 1.1123 | 2.2988 | 0.48388 | 84.0164 | 0.017678 | 0 | 0.017678 | 0.00088388 | 0 | 0.00088388 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Assembly | VRF-Retro-Assembly-GasHt | 20 | 2.5144 | 0 | 2.663 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 2.7024 | 0.00050802 | 0.00050435 | 0 | 0 | 0 | 0.53104 | 1.2272 | 0 | 1.0897 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53104 | 1.2272 | 0 | 1.0897 | 2.8479 | 1.4065 | 0.17951 | 0 | 0 | 1.586 | 0.53104 | 2.9866 | 1.4065 | 0.21248 | 0 | 0 | 1.619 | 1.2272 | 1.3193 | 1.4065 | 0.39199 | 0 | 0 | 1.7985 | 1.7582 | 37.1994 | 1.0229 | 14.4593 | 33.4133 | 0 | 29.6701 | 77.5427 | 1.4065 | 0 | 0.39199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8479 |  | 0 | 0 | 1.7985 | 2.8479 | 0.63152 | 66.8696 | 0.025673 | 0 | 0.025673 | 0.0012837 | 0 | 0.0012837 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Other | VRF-Retro-Other-GasHt | 20 | 3.043 | 0 | 2.4836 | 0 | 0 | C-All-HVAC-Vent-All-All-E |  |  | 3.2706 | 0.00061484 | 0.0006104 | 0 | 0 | 0 | 0.49526 | 1.1445 | 0 | 1.0163 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49526 | 1.1445 | 0 | 1.0163 | 2.656 | 1.7022 | 0.21725 | 0 | 0 | 1.9195 | 0.49526 | 3.8757 | 1.7022 | 0.25716 | 0 | 0 | 1.9594 | 1.1445 | 1.7121 | 1.7022 | 0.47441 | 0 | 0 | 2.1766 | 1.6397 | 26.2168 | 1.3274 | 11.1421 | 25.7478 | 0 | 22.8634 | 59.7533 | 1.7022 | 0 | 0.47441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.656 |  | 0 | 0 | 2.1766 | 2.656 | 0.81953 | 49.0801 | 0.031071 | 0 | 0.031071 | 0.0015536 | 0 | 0.0015536 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Category Results; Sorted by TRC Levelized Cost
Total Results |  | Measure Input Data | [8 empty] | Savings | [5 empty] | PV Capital |  |  |  | PV Admin |  |  |  | PV O&M |  |  |  | PV Periodic Repl. |  |  |  | Total PV Capital, O&M and Periodic Repl Costs |  |  |  |  | PV Wholesale Electric Utility Costs & Benefits | [6 empty] | PV Retail Electric Utility Costs & Benefits | [6 empty] | PV Electric Utility System Costs & Benefits | [5 empty] | Electric Utility System Economics |  | Sponsor Levelized Cost (mills/kwh) |  |  |  |  | PV Regional Costs & Benefits | [15 empty] | TRC Economics |  | Physical CO2 | [6 empty] | Gas Inputs |  |  |  | PV Gas Utility System Costs & Benefits |  |  |  |  | Gas Utility System Economics
Category | Measure | Measure Life | Site Savings (kWh) | Site Savings (therms) | Capital Cost ($/unit) | Annual O&M Cost ($/unit) | PV Per. Repl. Cost ($/unit) | Load Shape (electric) | Diversified Load Factor (electric) | Wholesale Power Coincidence Factor (electric) | Wholesale Electric Energy (kWh) | Wholesale Electric Demand (kw) | Retail Electric Demand (kW) | Wholesale Gas Energy (therms/yr) | Wholesale Gas Demand (therms/day) | Retail Gas Demand (therms/day) | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Total | Wholesale Utility System Energy | Wholesale Utility System T&D Def. Cap. | Wholesale Utility System Act C-E Credit | Wholesale Utility System Risk Mitigation Benefit | Wholesale Utility System Total System Benefit | Wholesale Utility System Total Non-Consumer Cost | Wholesale Utility System B/C Ratio | Retail Utility System Energy | Retail Utility System T&D Def. Cap. | Retail Utility System Act C-E Credit | Retail Utility System Risk Mitigation Benefit | Retail Utility System Total System Benefit | Retail Utility System Total Non-Consumer Cost | Retail Utility System System B/C Ratio | Utility System Energy | Utility System T&D Def. Cap. | Utility System Act C-E Credit | Utility System Total Risk Mitigation Benefit | Utility System Total System Benefit | Utility System Total Non-Consumer Cost | Utility System Net Levelized Cost (Net of Elec T&D Capacity Benefits, Act Credit & Risk-Mitigation Benefit) in mills/kwh | Utility System System B/C Ratio | Wholesale Electric Levelized Cost | Retail Electric Levelized Cost | Natural Gas Levelized Cost | Customer Levelized Cost | Total Levelized Cost | PV Regional Electric Energy | PV Regional Gas Energy | PV Regional Electric T&D Def. Cap. | PV Regional Gas T&D Def. Cap. | PV Regional Electric System CO2 | PV Regional Gas System CO2 | PV Regional Electric System Risk-Mitigation Benefit | PV Regional Gas System Risk-Mitigation Benefit | PV Regional Non-E Value | PV Regional Act Credit | PV Regional Capital Cost | PV Regional Admin Cost | PV Regional Annual O&M Cost | PV Regional Periodic Replacement Cost | PV Total Regional Benefit | PV Total Regional Cost | TRC B/C Ratio | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | Electric System CO2 Avoided (Lifetime Tons) | Gas System CO2 Avoided (Lifetime Tons) | Total System CO2 Avoided (Lifetime Tons) | Electric System CO2 Avoided (Annual Tons in 2018) | Gas System CO2 Avoided (Annual Tons in 2018) | Total System CO2 Avoided (Annual Tons in 2018) |  | Gas Site Savings (therms) | Load Shape (gas) | Diversitfied Load Factor (gas) | Wholesale Coincidence Factor (gas) | Total Gas Utility System Energy | Gas Utility System T&D Def. Cap. | Gas Utility System Risk Mitigation Benefit | Gas Utility System Total System Benefit | Gas Utility System Total Non-Consumer Cost | Gas Utility System Net Levelized Cost (Net of Gas T&D Capacity Benefits & Risk-Mitigation Benefits) in cents/therm | Gas Utility System System B/C Ratio
VRF-Retro-Small Off |  | 20 | 3.3124 | 0 | 1.773 | 0 | 0 |  |  |  | 3.5602 | 0.00066926 | 0.00066443 | 0 | 0 | 0 | 0.35357 | 0.81704 | 0 | 0.72551 | 0.10638 | 0.24823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45995 | 1.0653 | 0 | 0.72551 | 2.2507 | 1.8529 | 0.23648 | 0 | 0 | 2.0894 | 0.45995 | 4.5427 | 1.8529 | 0.27993 | 0 | 0 | 2.1329 | 1.0653 | 2.0022 | 1.8529 | 0.51641 | 0 | 0 | 2.3693 | 1.5252 | 20.85 | 1.5534 | 9.5063 | 22.0169 | 0 | 14.9949 | 46.5181 | 1.8529 | 0 | 0.51641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8961 | 0.35461 | 0 | 0 | 2.3693 | 2.2507 | 1.0527 | 35.8449 | 0.033822 | 0 | 0.033822 | 0.0016911 | 0 | 0.0016911 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Other |  | 20 | 4.0114 | 0 | 3.0053 | 0 | 0 |  |  |  | 4.3115 | 0.0008105 | 0.00080465 | 0 | 0 | 0 | 0.5993 | 1.3849 | 0 | 1.2297 | 0.18032 | 0.42074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77962 | 1.8056 | 0 | 1.2297 | 3.815 | 2.2439 | 0.28639 | 0 | 0 | 2.5303 | 0.77962 | 3.2456 | 2.2439 | 0.339 | 0 | 0 | 2.5829 | 1.8056 | 1.4305 | 2.2439 | 0.62539 | 0 | 0 | 2.8693 | 2.5853 | 33.448 | 1.1099 | 13.3054 | 30.8158 | 0 | 20.9875 | 65.1087 | 2.2439 | 0 | 0.62539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2139 | 0.60106 | 0 | 0 | 2.8693 | 3.815 | 0.75212 | 54.4355 | 0.040959 | 0 | 0.040959 | 0.002048 | 0 | 0.002048 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Lodging |  | 20 | 3.5154 | 0 | 3.077 | 0 | 0 |  |  |  | 3.7783 | 0.00071027 | 0.00070515 | 0 | 0 | 0 | 0.61359 | 1.4179 | 0 | 1.2591 | 0.18462 | 0.43078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79821 | 1.8487 | 0 | 1.2591 | 3.906 | 1.9665 | 0.25097 | 0 | 0 | 2.2174 | 0.79821 | 2.778 | 1.9665 | 0.29708 | 0 | 0 | 2.2635 | 1.8487 | 1.2244 | 1.9665 | 0.54805 | 0 | 0 | 2.5145 | 2.6469 | 40.8745 | 0.94998 | 15.5449 | 36.0028 | 0 | 24.5201 | 76.0678 | 1.9665 | 0 | 0.54805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2906 | 0.6154 | 0 | 0 | 2.5145 | 3.906 | 0.64376 | 65.3946 | 0.035894 | 0 | 0.035894 | 0.0017947 | 0 | 0.0017947 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Large Off |  | 20 | 3.7083 | 0 | 3.4422 | 0 | 0 |  |  |  | 3.9857 | 0.00074926 | 0.00074385 | 0 | 0 | 0 | 0.68642 | 1.5862 | 0 | 1.4085 | 0.20653 | 0.48191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89295 | 2.0681 | 0 | 1.4085 | 4.3696 | 2.0744 | 0.26475 | 0 | 0 | 2.3391 | 0.89295 | 2.6196 | 2.0744 | 0.31338 | 0 | 0 | 2.3878 | 2.0681 | 1.1546 | 2.0744 | 0.57813 | 0 | 0 | 2.6525 | 2.9611 | 43.9923 | 0.8958 | 16.4851 | 38.1803 | 0 | 26.0031 | 80.6685 | 2.0744 | 0 | 0.57813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6811 | 0.68844 | 0 | 0 | 2.6525 | 4.3696 | 0.60704 | 69.9954 | 0.037865 | 0 | 0.037865 | 0.0018932 | 0 | 0.0018932 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Medium Off |  | 20 | 2.24 | 0 | 2.0968 | 0 | 0 |  |  |  | 2.4076 | 0.00045259 | 0.00044932 | 0 | 0 | 0 | 0.41813 | 0.96624 | 0 | 0.858 | 0.12581 | 0.29355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54394 | 1.2598 | 0 | 0.858 | 2.6617 | 1.253 | 0.15992 | 0 | 0 | 1.413 | 0.54394 | 2.5976 | 1.253 | 0.1893 | 0 | 0 | 1.4423 | 1.2598 | 1.1449 | 1.253 | 0.34922 | 0 | 0 | 1.6023 | 1.8037 | 44.4538 | 0.8883 | 16.6243 | 38.5026 | 0 | 26.2227 | 81.3496 | 1.253 | 0 | 0.34922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2424 | 0.41936 | 0 | 0 | 1.6023 | 2.6617 | 0.60196 | 70.6764 | 0.022872 | 0 | 0.022872 | 0.0011436 | 0 | 0.0011436 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Restaurant |  | 20 | 5.4326 | 0 | 5.2135 | 0 | 0 |  |  |  | 5.8389 | 0.0010976 | 0.0010897 | 0 | 0 | 0 | 1.0396 | 2.4025 | 0 | 2.1333 | 0.31281 | 0.72989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3525 | 3.1324 | 0 | 2.1333 | 6.6181 | 3.0389 | 0.38785 | 0 | 0 | 3.4268 | 1.3525 | 2.5337 | 3.0389 | 0.4591 | 0 | 0 | 3.498 | 3.1324 | 1.1167 | 3.0389 | 0.84694 | 0 | 0 | 3.8859 | 4.4848 | 45.8442 | 0.86645 | 17.0436 | 39.4738 | 0 | 26.8841 | 83.4015 | 3.0389 | 0 | 0.84694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5754 | 1.0427 | 0 | 0 | 3.8859 | 6.6181 | 0.58715 | 72.7283 | 0.05547 | 0 | 0.05547 | 0.0027735 | 0 | 0.0027735 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Assembly |  | 20 | 2.9831 | 0 | 2.9908 | 0 | 0 |  |  |  | 3.2062 | 0.00060272 | 0.00059837 | 0 | 0 | 0 | 0.5964 | 1.3782 | 0 | 1.2238 | 0.17945 | 0.41871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77584 | 1.7969 | 0 | 1.2238 | 3.7965 | 1.6687 | 0.21297 | 0 | 0 | 1.8817 | 0.77584 | 2.4253 | 1.6687 | 0.2521 | 0 | 0 | 1.9208 | 1.7969 | 1.069 | 1.6687 | 0.46507 | 0 | 0 | 2.1338 | 2.5727 | 48.3702 | 0.82938 | 17.8053 | 41.238 | 0 | 28.0856 | 87.129 | 1.6687 | 0 | 0.46507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1984 | 0.59815 | 0 | 0 | 2.1338 | 3.7965 | 0.56203 | 76.4559 | 0.030459 | 0 | 0.030459 | 0.001523 | 0 | 0.001523 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Supermarket |  | 20 | 3.0893 | 0 | 3.207 | 0 | 0 |  |  |  | 3.3204 | 0.00062419 | 0.00061968 | 0 | 0 | 0 | 0.63952 | 1.4778 | 0 | 1.3123 | 0.19242 | 0.44898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83194 | 1.9268 | 0 | 1.3123 | 4.071 | 1.7281 | 0.22056 | 0 | 0 | 1.9487 | 0.83194 | 2.3423 | 1.7281 | 0.26107 | 0 | 0 | 1.9892 | 1.9268 | 1.0324 | 1.7281 | 0.48163 | 0 | 0 | 2.2098 | 2.7587 | 50.4622 | 0.801 | 18.4362 | 42.6991 | 0 | 29.0807 | 90.216 | 1.7281 | 0 | 0.48163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4296 | 0.6414 | 0 | 0 | 2.2098 | 4.071 | 0.5428 | 79.5429 | 0.031544 | 0 | 0.031544 | 0.0015772 | 0 | 0.0015772 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-MiniMart |  | 20 | 5.2367 | 0 | 5.5583 | 0 | 0 |  |  |  | 5.6284 | 0.0010581 | 0.0010504 | 0 | 0 | 0 | 1.1084 | 2.5613 | 0 | 2.2744 | 0.3335 | 0.77816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4419 | 3.3395 | 0 | 2.2744 | 7.0558 | 2.9294 | 0.37387 | 0 | 0 | 3.3032 | 1.4419 | 2.2909 | 2.9294 | 0.44254 | 0 | 0 | 3.3719 | 3.3395 | 1.0097 | 2.9294 | 0.81641 | 0 | 0 | 3.7458 | 4.7814 | 51.835 | 0.78341 | 18.8502 | 43.6579 | 0 | 29.7337 | 92.2418 | 2.9294 | 0 | 0.81641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9441 | 1.1117 | 0 | 0 | 3.7458 | 7.0558 | 0.53088 | 81.5687 | 0.05347 | 0 | 0.05347 | 0.0026735 | 0 | 0.0026735 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Residential Care |  | 20 | 3.7142 | 0 | 3.7708 | 0 | 0 |  |  |  | 3.9867 | 0.00048344 | 0.00047995 | 0 | 0 | 0 | 0.75194 | 1.7376 | 0 | 1.543 | 0.22625 | 0.52791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97819 | 2.2655 | 0 | 1.543 | 4.7867 | 2.0101 | 0.17082 | 0 | 0 | 2.181 | 0.97819 | 2.2296 | 2.0101 | 0.2022 | 0 | 0 | 2.2124 | 2.2655 | 0.97653 | 2.0101 | 0.37303 | 0 | 0 | 2.3832 | 3.2437 | 52.983 | 0.73471 | 18.054 | 41.8139 | 0 | 28.4778 | 88.3456 | 2.0101 | 0 | 0.37303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0325 | 0.75415 | 0 | 0 | 2.3832 | 4.7867 | 0.49788 | 81.4608 | 0.037874 | 0 | 0.037874 | 0.0018937 | 0 | 0.0018937 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Warehouse |  | 20 | 2.7753 | 0 | 3.3975 | 0 | 0 |  |  |  | 2.9829 | 0.00056074 | 0.00055669 | 0 | 0 | 0 | 0.6775 | 1.5656 | 0 | 1.3902 | 0.20385 | 0.47564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88135 | 2.0412 | 0 | 1.3902 | 4.3128 | 1.5525 | 0.19814 | 0 | 0 | 1.7506 | 0.88135 | 1.9863 | 1.5525 | 0.23453 | 0 | 0 | 1.787 | 2.0412 | 0.87545 | 1.5525 | 0.43267 | 0 | 0 | 1.9851 | 2.9226 | 61.4213 | 0.67924 | 21.7411 | 50.3534 | 0 | 34.2937 | 106.3882 | 1.5525 | 0 | 0.43267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0.67949 | 0 | 0 | 1.9851 | 4.3128 | 0.46029 | 95.7151 | 0.028338 | 0 | 0.028338 | 0.0014169 | 0 | 0.0014169 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Small Ret |  | 20 | 1.9394 | 0 | 2.7827 | 0 | 0 |  |  |  | 2.0845 | 0.00039185 | 0.00038903 | 0 | 0 | 0 | 0.55492 | 1.2823 | 0 | 1.1387 | 0.16696 | 0.38958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72188 | 1.6719 | 0 | 1.1387 | 3.5325 | 1.0849 | 0.13846 | 0 | 0 | 1.2233 | 0.72188 | 1.6947 | 1.0849 | 0.1639 | 0 | 0 | 1.2488 | 1.6719 | 0.74692 | 1.0849 | 0.30236 | 0 | 0 | 1.3872 | 2.3938 | 73.8272 | 0.57952 | 25.4823 | 59.0181 | 0 | 40.195 | 124.6954 | 1.0849 | 0 | 0.30236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9759 | 0.55655 | 0 | 0 | 1.3872 | 3.5325 | 0.39271 | 114.0222 | 0.019803 | 0 | 0.019803 | 0.00099013 | 0 | 0.00099013 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Hospital |  | 20 | 3.9754 | 0 | 5.2048 | 0 | 0 |  |  |  | 4.2671 | 0.00051744 | 0.0005137 | 0 | 0 | 0 | 1.0379 | 2.3984 | 0 | 2.1298 | 0.31229 | 0.72867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3502 | 3.1271 | 0 | 2.1298 | 6.6071 | 2.1515 | 0.18284 | 0 | 0 | 2.3343 | 1.3502 | 1.7289 | 2.1515 | 0.21642 | 0 | 0 | 2.3679 | 3.1271 | 0.75722 | 2.1515 | 0.39926 | 0 | 0 | 2.5508 | 4.4773 | 70.3221 | 0.56971 | 23.2828 | 53.9241 | 0 | 36.7256 | 113.9326 | 2.1515 | 0 | 0.39926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5661 | 1.041 | 0 | 0 | 2.5508 | 6.6071 | 0.38606 | 107.0478 | 0.040538 | 0 | 0.040538 | 0.0020269 | 0 | 0.0020269 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-University |  | 20 | 1.926 | 0 | 3.0458 | 0 | 0 |  |  |  | 2.0701 | 0.00038914 | 0.00038633 | 0 | 0 | 0 | 0.60737 | 1.4035 | 0 | 1.2463 | 0.18275 | 0.42641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79012 | 1.83 | 0 | 1.2463 | 3.8664 | 1.0774 | 0.1375 | 0 | 0 | 1.2149 | 0.79012 | 1.5376 | 1.0774 | 0.16276 | 0 | 0 | 1.2401 | 1.83 | 0.67769 | 1.0774 | 0.30027 | 0 | 0 | 1.3776 | 2.6201 | 82.4595 | 0.5258 | 28.0854 | 65.0473 | 0 | 44.3012 | 137.4339 | 1.0774 | 0 | 0.30027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2572 | 0.60916 | 0 | 0 | 1.3776 | 3.8664 | 0.35631 | 126.7607 | 0.019666 | 0 | 0.019666 | 0.00098328 | 0 | 0.00098328 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Medium Ret |  | 20 | 1.9835 | 0 | 3.1413 | 0 | 0 |  |  |  | 2.1319 | 0.00040076 | 0.00039787 | 0 | 0 | 0 | 0.62642 | 1.4476 | 0 | 1.2854 | 0.18848 | 0.43978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81489 | 1.8873 | 0 | 1.2854 | 3.9876 | 1.1095 | 0.14161 | 0 | 0 | 1.2512 | 0.81489 | 1.5354 | 1.1095 | 0.16762 | 0 | 0 | 1.2772 | 1.8873 | 0.67671 | 1.1095 | 0.30923 | 0 | 0 | 1.4188 | 2.7022 | 82.5947 | 0.52504 | 28.1262 | 65.1417 | 0 | 44.3655 | 137.6334 | 1.1095 | 0 | 0.30923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3594 | 0.62826 | 0 | 0 | 1.4188 | 3.9876 | 0.3558 | 126.9602 | 0.020253 | 0 | 0.020253 | 0.0010126 | 0 | 0.0010126 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Xlarge Ret |  | 20 | 2.0028 | 0 | 3.2982 | 0 | 0 |  |  |  | 2.1526 | 0.00040466 | 0.00040174 | 0 | 0 | 0 | 0.65771 | 1.5199 | 0 | 1.3496 | 0.19789 | 0.46175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85561 | 1.9816 | 0 | 1.3496 | 4.1868 | 1.1203 | 0.14299 | 0 | 0 | 1.2633 | 0.85561 | 1.4765 | 1.1203 | 0.16925 | 0 | 0 | 1.2896 | 1.9816 | 0.65078 | 1.1203 | 0.31224 | 0 | 0 | 1.4326 | 2.8372 | 86.3107 | 0.50492 | 29.2468 | 67.7371 | 0 | 46.1331 | 143.117 | 1.1203 | 0 | 0.31224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5272 | 0.65965 | 0 | 0 | 1.4326 | 4.1868 | 0.34216 | 132.4438 | 0.02045 | 0 | 0.02045 | 0.0010225 | 0 | 0.0010225 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-Large Ret |  | 20 | 2.015 | 0 | 3.3975 | 0 | 0 |  |  |  | 2.1657 | 0.00040713 | 0.00040419 | 0 | 0 | 0 | 0.6775 | 1.5656 | 0 | 1.3902 | 0.20385 | 0.47564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88135 | 2.0412 | 0 | 1.3902 | 4.3128 | 1.1272 | 0.14386 | 0 | 0 | 1.271 | 0.88135 | 1.4421 | 1.1272 | 0.17028 | 0 | 0 | 1.2975 | 2.0412 | 0.63562 | 1.1272 | 0.31414 | 0 | 0 | 1.4413 | 2.9226 | 88.6234 | 0.49316 | 29.9442 | 69.3523 | 0 | 47.2332 | 146.5297 | 1.1272 | 0 | 0.31414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0.67949 | 0 | 0 | 1.4413 | 4.3128 | 0.33419 | 135.8566 | 0.020575 | 0 | 0.020575 | 0.0010287 | 0 | 0.0010287 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
VRF-Retro-School K-12 |  | 20 | 1.8463 | 0 | 3.0811 | 0 | 0 |  |  |  | 1.9865 | 0.00018294 | 0.00018162 | 0 | 0 | 0 | 0.61441 | 1.4198 | 0 | 1.2608 | 0.18486 | 0.43135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79927 | 1.8512 | 0 | 1.2608 | 3.9112 | 1.064 | 0.064643 | 0 | 0 | 1.1287 | 0.79927 | 1.4121 | 1.064 | 0.076518 | 0 | 0 | 1.1405 | 1.8512 | 0.61613 | 1.064 | 0.14116 | 0 | 0 | 1.2052 | 2.6504 | 92.9433 | 0.45471 | 29.6051 | 68.5668 | 0 | 46.6982 | 144.8701 | 1.064 | 0 | 0.14116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.295 | 0.61622 | 0 | 0 | 1.2052 | 3.9112 | 0.30814 | 139.6415 | 0.018872 | 0 | 0.018872 | 0.00094361 | 0 | 0.00094361 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9999 | 9999
Supply Curve Results; Categories sorted by TRC Net Levelized Cost
Totals for Categories with Benefits Exceeding Costs. Levelized cost is TRC Net Levelized Cost (Net of Benefits) | [12 empty] | Savings Allocation by Cost Bin and Month for Segments 1 | [12 empty] | Savings Allocation by Cost Bin and Month for Segments 2
| Totals Basis | Busbar Electric Savings in kWh | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Measures with B/C > 1.00 | 4.601 | 2.2948 | 0 | 2.2948 | 2.4541 | 3.062 | 4369.0982 | 13.5567 | 28.5737 | 1.2805 | 0.04371 | 0.28851 | 0.25941 | 0.29852 | 0.27772 | 0.28353 | 0.28066 | 0.26663 | 0.27782 | 0.25957 | 0.29596 | 0.26191 | 0.28515 |  | 0.12249 | 0.10524 | 0.10095 | 0.1054 | 0.10342 | 0.090744 | 0.10655 | 0.087378 | 0.10757 | 0.096616 | 0.11592 | 0.12333
| Categories with B/C > 1.00 | 3.5602 | 1.773 | 0.35461 | 2.1276 | 2.2507 | 2.3693 | 5235.1868 | 20.85 | 35.8449 | 1.0527 | 0.033822 | 0.37421 | 0.33647 | 0.3872 | 0.36022 | 0.36776 | 0.36403 | 0.34584 | 0.36035 | 0.33668 | 0.38388 | 0.33971 | 0.36986 |  | 0.15887 | 0.1365 | 0.13093 | 0.13671 | 0.13414 | 0.1177 | 0.1382 | 0.11333 | 0.13953 | 0.12532 | 0.15035 | 0.15997
Supply Curve Results: By TRC Net Levelized Cost - Net of Benefits
| Block 1: <= 0 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 2: <= 10 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 3: 10-20 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 4: 20-30 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 5: 30-40 mills/kWh | 3.5602 | 1.773 | 0.35461 | 2.1276 | 2.2507 | 2.3693 | 5235.1868 | 20.85 | 35.8449 | 1.0527 | 0.033822 | 0.22324 | 0.20073 | 0.23099 | 0.21489 | 0.21939 | 0.21717 | 0.20632 | 0.21497 | 0.20085 | 0.22901 | 0.20266 | 0.22065 |  | 0.094779 | 0.081432 | 0.07811 | 0.08156 | 0.080021 | 0.070216 | 0.082443 | 0.067612 | 0.083237 | 0.07476 | 0.089697 | 0.095431
| Block 6: 40-50 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 7: 50-60 mills/kWh | 4.3115 | 3.0053 | 0.60106 | 3.6064 | 3.815 | 2.8693 | 7327.3906 | 33.448 | 54.4355 | 0.75212 | 0.040959 | 0.27035 | 0.24309 | 0.27973 | 0.26024 | 0.26569 | 0.263 | 0.24985 | 0.26034 | 0.24324 | 0.27734 | 0.24543 | 0.26721 |  | 0.11478 | 0.098616 | 0.094594 | 0.098771 | 0.096908 | 0.085034 | 0.099841 | 0.08188 | 0.1008 | 0.090537 | 0.10863 | 0.11557
| Block 8: 60-70 mills/kWh | 7.764 | 6.5192 | 1.3038 | 7.823 | 8.2755 | 5.167 | 8826.5401 | 42.475 | 67.7564 | 0.62491 | 0.073759 | 0.48684 | 0.43775 | 0.50374 | 0.46864 | 0.47845 | 0.4736 | 0.44993 | 0.46881 | 0.43802 | 0.49943 | 0.44197 | 0.48118 |  | 0.20669 | 0.17759 | 0.17034 | 0.17787 | 0.17451 | 0.15313 | 0.17979 | 0.14745 | 0.18152 | 0.16304 | 0.19561 | 0.20812
| Block 9: 70-80 mills/kWh | 14.7731 | 13.5081 | 2.7016 | 16.2097 | 17.1474 | 9.8316 | 9611.8622 | 47.2038 | 74.7345 | 0.57415 | 0.14035 | 0.92635 | 0.83294 | 0.9585 | 0.89171 | 0.91038 | 0.90116 | 0.85611 | 0.89204 | 0.83345 | 0.95029 | 0.84095 | 0.91558 |  | 0.39329 | 0.3379 | 0.32412 | 0.33844 | 0.33205 | 0.29137 | 0.3421 | 0.28056 | 0.3454 | 0.31022 | 0.3722 | 0.396
| Block 10: 80-90 mills/kWh | 9.6152 | 9.329 | 1.8658 | 11.1948 | 11.8424 | 6.1289 | 10199.172 | 52.311 | 81.5239 | 0.5172 | 0.091345 | 0.54188 | 0.49091 | 0.56778 | 0.52745 | 0.54413 | 0.54358 | 0.52187 | 0.55164 | 0.50321 | 0.56704 | 0.50061 | 0.53703 |  | 0.29766 | 0.25884 | 0.25596 | 0.26485 | 0.26617 | 0.24144 | 0.27974 | 0.24241 | 0.27686 | 0.25098 | 0.28491 | 0.29821
| Block 11: 90-100 mills/kWh | 2.9829 | 3.3975 | 0.67949 | 4.0769 | 4.3128 | 1.9851 | 11973.0293 | 61.4213 | 95.7151 | 0.46029 | 0.028338 | 0.18704 | 0.16818 | 0.19353 | 0.18005 | 0.18382 | 0.18195 | 0.17286 | 0.18011 | 0.16828 | 0.19188 | 0.1698 | 0.18487 |  | 0.07941 | 0.068227 | 0.065444 | 0.068335 | 0.067045 | 0.05883 | 0.069074 | 0.056648 | 0.06974 | 0.062637 | 0.075152 | 0.079957
| Block 12: 100-110 mills/kWh | 4.2671 | 5.2048 | 1.041 | 6.2458 | 6.6071 | 2.5508 | 12822.0771 | 70.3221 | 107.0478 | 0.38606 | 0.040538 | 0.20224 | 0.18577 | 0.21685 | 0.20092 | 0.21116 | 0.21432 | 0.20946 | 0.22667 | 0.19873 | 0.2194 | 0.19289 | 0.20144 |  | 0.15821 | 0.13925 | 0.14178 | 0.14547 | 0.14949 | 0.1396 | 0.15991 | 0.14505 | 0.15549 | 0.14212 | 0.15317 | 0.1577
| Block 13: 110-120 mills/kWh | 2.0845 | 2.7827 | 0.55655 | 3.3393 | 3.5325 | 1.3872 | 14033.33 | 73.8272 | 114.0222 | 0.39271 | 0.019803 | 0.13071 | 0.11753 | 0.13524 | 0.12582 | 0.12845 | 0.12715 | 0.1208 | 0.12587 | 0.1176 | 0.13409 | 0.11866 | 0.12919 |  | 0.055493 | 0.047678 | 0.045733 | 0.047753 | 0.046852 | 0.041112 | 0.04827 | 0.039587 | 0.048735 | 0.043772 | 0.052517 | 0.055875
| Block 14: 120-130 mills/kWh | 4.2019 | 6.1871 | 1.2374 | 7.4245 | 7.854 | 2.7964 | 15478.3251 | 82.5281 | 126.8619 | 0.35605 | 0.039919 | 0.26348 | 0.23691 | 0.27263 | 0.25363 | 0.25894 | 0.25632 | 0.24351 | 0.25372 | 0.23706 | 0.27029 | 0.23919 | 0.26042 |  | 0.11186 | 0.09611 | 0.09219 | 0.096262 | 0.094446 | 0.082873 | 0.097304 | 0.079799 | 0.098241 | 0.088236 | 0.10587 | 0.11263
| Block 15: 130-140 mills/kWh | 6.3049 | 9.7768 | 1.9554 | 11.7321 | 12.4108 | 4.0791 | 16300.6109 | 89.1949 | 135.8839 | 0.32871 | 0.059897 | 0.41972 | 0.3801 | 0.43054 | 0.40359 | 0.41236 | 0.40342 | 0.37413 | 0.40653 | 0.39398 | 0.43128 | 0.37437 | 0.39994 |  | 0.1576 | 0.13026 | 0.12058 | 0.11979 | 0.11504 | 0.10089 | 0.11541 | 0.098132 | 0.12171 | 0.10657 | 0.13464 | 0.15429
| Block 16: 140-150 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 17: 150-160 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 18: 160-170 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 19: 170-180 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 20: 180-190 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 21: 190-200 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 22: > 200 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Shaped Savings Results; By Category and sorted by TRC BC ratio
[13 empty] | Savings Allocation by Cost Bin and Month for Segments 1 Feb: Savings Allocation by Category and Month for Segments 1 |  |  | Savings Allocation by Category and Month for Segments 2
Category | Measure | Busbar Savings | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Wholesale KW | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
VRF-Retro-Small Off |  | 3.5602 | 1.773 | 0.35461 | 2.1276 | 2.2507 | 2.3693 | 5235.1868 | 20.85 | 35.8449 | 1.0527 | 0.033822 | 0.00066926 | 0.22324 | 0.20073 | 0.23099 | 0.21489 | 0.21939 | 0.21717 | 0.20632 | 0.21497 | 0.20085 | 0.22901 | 0.20266 | 0.22065 |  | 0.094779 | 0.081432 | 0.07811 | 0.08156 | 0.080021 | 0.070216 | 0.082443 | 0.067612 | 0.083237 | 0.07476 | 0.089697 | 0.095431
VRF-Retro-Other |  | 4.3115 | 3.0053 | 0.60106 | 3.6064 | 3.815 | 2.8693 | 7327.3906 | 33.448 | 54.4355 | 0.75212 | 0.040959 | 0.0008105 | 0.27035 | 0.24309 | 0.27973 | 0.26024 | 0.26569 | 0.263 | 0.24985 | 0.26034 | 0.24324 | 0.27734 | 0.24543 | 0.26721 |  | 0.11478 | 0.098616 | 0.094594 | 0.098771 | 0.096908 | 0.085034 | 0.099841 | 0.08188 | 0.1008 | 0.090537 | 0.10863 | 0.11557
VRF-Retro-Lodging |  | 3.7783 | 3.077 | 0.6154 | 3.6924 | 3.906 | 2.5145 | 8560.7383 | 40.8745 | 65.3946 | 0.64376 | 0.035894 | 0.00071027 | 0.23692 | 0.21303 | 0.24514 | 0.22806 | 0.23284 | 0.23048 | 0.21896 | 0.22814 | 0.21316 | 0.24304 | 0.21508 | 0.23417 |  | 0.10059 | 0.086421 | 0.082896 | 0.086557 | 0.084924 | 0.074519 | 0.087494 | 0.071754 | 0.088337 | 0.079341 | 0.095193 | 0.10128
VRF-Retro-Large Off |  | 3.9857 | 3.4422 | 0.68844 | 4.1306 | 4.3696 | 2.6525 | 9078.5117 | 43.9923 | 69.9954 | 0.60704 | 0.037865 | 0.00074926 | 0.24992 | 0.22472 | 0.2586 | 0.24058 | 0.24562 | 0.24313 | 0.23097 | 0.24067 | 0.22486 | 0.25638 | 0.22689 | 0.24702 |  | 0.10611 | 0.091165 | 0.087446 | 0.091308 | 0.089586 | 0.078609 | 0.092297 | 0.075693 | 0.093186 | 0.083696 | 0.10042 | 0.10684
VRF-Retro-Medium Off |  | 2.4076 | 2.0968 | 0.41936 | 2.5162 | 2.6617 | 1.6023 | 9155.155 | 44.4538 | 70.6764 | 0.60196 | 0.022872 | 0.00045259 | 0.15097 | 0.13574 | 0.15621 | 0.14532 | 0.14837 | 0.14686 | 0.13952 | 0.14538 | 0.13583 | 0.15487 | 0.13705 | 0.14921 |  | 0.064095 | 0.055068 | 0.052822 | 0.055155 | 0.054114 | 0.047484 | 0.055752 | 0.045722 | 0.056289 | 0.050557 | 0.060657 | 0.064536
VRF-Retro-Restaurant |  | 5.8389 | 5.2135 | 1.0427 | 6.2562 | 6.6181 | 3.8859 | 9386.0805 | 45.8442 | 72.7283 | 0.58715 | 0.05547 | 0.0010976 | 0.36613 | 0.32921 | 0.37884 | 0.35244 | 0.35982 | 0.35617 | 0.33837 | 0.35257 | 0.32941 | 0.37559 | 0.33238 | 0.36187 |  | 0.15544 | 0.13355 | 0.12811 | 0.13376 | 0.13124 | 0.11516 | 0.13521 | 0.11089 | 0.13651 | 0.12261 | 0.14711 | 0.15651
VRF-Retro-Assembly |  | 3.2062 | 2.9908 | 0.59815 | 3.5889 | 3.7965 | 2.1338 | 9805.5803 | 48.3702 | 76.4559 | 0.56203 | 0.030459 | 0.00060272 | 0.20105 | 0.18077 | 0.20802 | 0.19353 | 0.19758 | 0.19558 | 0.1858 | 0.1936 | 0.18088 | 0.20624 | 0.18251 | 0.19871 |  | 0.085356 | 0.073335 | 0.070344 | 0.073451 | 0.072065 | 0.063235 | 0.074246 | 0.060889 | 0.074961 | 0.067327 | 0.080779 | 0.085943
VRF-Retro-Supermarket |  | 3.3204 | 3.207 | 0.6414 | 3.8484 | 4.071 | 2.2098 | 10152.9961 | 50.4622 | 79.5429 | 0.5428 | 0.031544 | 0.00062419 | 0.20821 | 0.18721 | 0.21543 | 0.20042 | 0.20462 | 0.20254 | 0.19242 | 0.20049 | 0.18733 | 0.21359 | 0.18901 | 0.20579 |  | 0.088396 | 0.075947 | 0.072849 | 0.076067 | 0.074632 | 0.065487 | 0.07689 | 0.063058 | 0.077631 | 0.069725 | 0.083655 | 0.089004
VRF-Retro-MiniMart |  | 5.6284 | 5.5583 | 1.1117 | 6.6699 | 7.0558 | 3.7458 | 10380.9815 | 51.835 | 81.5687 | 0.53088 | 0.05347 | 0.0010581 | 0.35293 | 0.31734 | 0.36518 | 0.33973 | 0.34685 | 0.34333 | 0.32617 | 0.33986 | 0.31754 | 0.36205 | 0.3204 | 0.34883 |  | 0.14984 | 0.12874 | 0.12349 | 0.12894 | 0.12651 | 0.11101 | 0.13034 | 0.10689 | 0.13159 | 0.11819 | 0.1418 | 0.15087
VRF-Retro-Residential Care |  | 3.9867 | 3.7708 | 0.75415 | 4.5249 | 4.7867 | 2.3832 | 9942.4973 | 52.983 | 81.4608 | 0.49788 | 0.037874 | 0.00048344 | 0.18895 | 0.17357 | 0.2026 | 0.18772 | 0.19729 | 0.20024 | 0.1957 | 0.21178 | 0.18567 | 0.20499 | 0.18021 | 0.1882 |  | 0.14782 | 0.13011 | 0.13247 | 0.13591 | 0.13967 | 0.13043 | 0.1494 | 0.13552 | 0.14527 | 0.13279 | 0.1431 | 0.14734
VRF-Retro-Warehouse |  | 2.9829 | 3.3975 | 0.67949 | 4.0769 | 4.3128 | 1.9851 | 11973.0293 | 61.4213 | 95.7151 | 0.46029 | 0.028338 | 0.00056074 | 0.18704 | 0.16818 | 0.19353 | 0.18005 | 0.18382 | 0.18195 | 0.17286 | 0.18011 | 0.16828 | 0.19188 | 0.1698 | 0.18487 |  | 0.07941 | 0.068227 | 0.065444 | 0.068335 | 0.067045 | 0.05883 | 0.069074 | 0.056648 | 0.06974 | 0.062637 | 0.075152 | 0.079957
VRF-Retro-Small Ret |  | 2.0845 | 2.7827 | 0.55655 | 3.3393 | 3.5325 | 1.3872 | 14033.33 | 73.8272 | 114.0222 | 0.39271 | 0.019803 | 0.00039185 | 0.13071 | 0.11753 | 0.13524 | 0.12582 | 0.12845 | 0.12715 | 0.1208 | 0.12587 | 0.1176 | 0.13409 | 0.11866 | 0.12919 |  | 0.055493 | 0.047678 | 0.045733 | 0.047753 | 0.046852 | 0.041112 | 0.04827 | 0.039587 | 0.048735 | 0.043772 | 0.052517 | 0.055875
VRF-Retro-Hospital |  | 4.2671 | 5.2048 | 1.041 | 6.2458 | 6.6071 | 2.5508 | 12822.0771 | 70.3221 | 107.0478 | 0.38606 | 0.040538 | 0.00051744 | 0.20224 | 0.18577 | 0.21685 | 0.20092 | 0.21116 | 0.21432 | 0.20946 | 0.22667 | 0.19873 | 0.2194 | 0.19289 | 0.20144 |  | 0.15821 | 0.13925 | 0.14178 | 0.14547 | 0.14949 | 0.1396 | 0.15991 | 0.14505 | 0.15549 | 0.14212 | 0.15317 | 0.1577
VRF-Retro-University |  | 2.0701 | 3.0458 | 0.60916 | 3.655 | 3.8664 | 1.3776 | 15466.9336 | 82.4595 | 126.7607 | 0.35631 | 0.019666 | 0.00038914 | 0.1298 | 0.11671 | 0.13431 | 0.12495 | 0.12757 | 0.12627 | 0.11996 | 0.125 | 0.11679 | 0.13316 | 0.11784 | 0.12829 |  | 0.055109 | 0.047348 | 0.045417 | 0.047423 | 0.046528 | 0.040827 | 0.047936 | 0.039313 | 0.048398 | 0.043469 | 0.052154 | 0.055488
VRF-Retro-Medium Ret |  | 2.1319 | 3.1413 | 0.62826 | 3.7696 | 3.9876 | 1.4188 | 15489.3864 | 82.5947 | 126.9602 | 0.3558 | 0.020253 | 0.00040076 | 0.13368 | 0.1202 | 0.13832 | 0.12868 | 0.13138 | 0.13004 | 0.12354 | 0.12873 | 0.12027 | 0.13713 | 0.12136 | 0.13213 |  | 0.056755 | 0.048762 | 0.046773 | 0.048839 | 0.047917 | 0.042046 | 0.049368 | 0.040486 | 0.049843 | 0.044767 | 0.053711 | 0.057145
VRF-Retro-Xlarge Ret |  | 2.1526 | 3.2982 | 0.65965 | 3.9579 | 4.1868 | 1.4326 | 16106.5136 | 86.3107 | 132.4438 | 0.34216 | 0.02045 | 0.00040466 | 0.13498 | 0.12137 | 0.13966 | 0.12993 | 0.13265 | 0.13131 | 0.12475 | 0.12998 | 0.12144 | 0.13847 | 0.12254 | 0.13341 |  | 0.057307 | 0.049236 | 0.047228 | 0.049314 | 0.048384 | 0.042455 | 0.049848 | 0.04088 | 0.050328 | 0.045203 | 0.054234 | 0.057701
VRF-Retro-Large Ret |  | 2.1657 | 3.3975 | 0.67949 | 4.0769 | 4.3128 | 1.4413 | 16490.5927 | 88.6234 | 135.8566 | 0.33419 | 0.020575 | 0.00040713 | 0.1358 | 0.12211 | 0.14051 | 0.13072 | 0.13346 | 0.13211 | 0.12551 | 0.13077 | 0.12218 | 0.13931 | 0.12328 | 0.13422 |  | 0.057656 | 0.049536 | 0.047516 | 0.049614 | 0.048678 | 0.042714 | 0.050152 | 0.041129 | 0.050635 | 0.045478 | 0.054564 | 0.058053
VRF-Retro-School K-12 |  | 1.9865 | 3.0811 | 0.61622 | 3.6973 | 3.9112 | 1.2052 | 16303.8163 | 92.9433 | 139.6415 | 0.30814 | 0.018872 | 0.00018294 | 0.14893 | 0.13662 | 0.15036 | 0.14293 | 0.14625 | 0.14001 | 0.12388 | 0.14578 | 0.15036 | 0.1535 | 0.12855 | 0.13231 |  | 0.042638 | 0.031491 | 0.025835 | 0.020865 | 0.017977 | 0.015723 | 0.015412 | 0.016122 | 0.020744 | 0.015891 | 0.025846 | 0.038533
Note on I6: :ProCost Perioodic replacement costs and savinsg of the measure. These are costs and savings that occur periodicially, but at different periods than annually. Can be positive or negative. Periodic replacement costs for both the measure and the baseline measure should be included if applicable. ProCost can analysze these costs in two ways dependent on the 'Repeat Periodic Replacemetn' switch in the ProData page. When set to 'On', ProCost repeats replacement costs for multiple times over the life of a measure depending on the input period and measure life. For example fluorescent lamps may have a 4-year replacement cycle that repeats 3 times in a 15-year measure life. When set to 'Off', ProCost reads the period as the year after installation that the replacement cost occurs and does not subsequently reinstall or repeat the replacement costs. For example a compressor may be replaced only once in the life of a heat-pump system. Example: A new fluorescent lighting systems may have a measure life of 15 years, and a lamp life of five years. Two lamps lamps per fixture must be replaced at years 6 and 11. Lamp and labor costs, expressed as positive costs, are entered as a cost and the period would be enetered as 5. The baseline measure may have a four year lamp life and would have required a three-lamp replacement at years 5, 9 and 13. Lamp and labor replacement costs would be entered as annual savings in dollars with a 4-year period. ProCost determines the net present value of the two cost streams.
Note on O6: :ProCost If the measure has gas savings for incfreases, enter the annual savings and shape of the savings here. Example: Clothes washer saves electric motor and dryer energy and gas water heat.
Note on A7: :Procost Category for the measure. Individual measures can be grouped into categories. Procost output is reported by measure and by category. All measures must belong to at least one category. Category name can be the same as measure name. Example: Measures can be combined into one category if they have components with different load shapes or measure lives. On wash machines there may be one load shape for the electric motor savings component, a second load shape for the electric water heat savings component and a third shape for electric dryer savings component.
Note on B7: :ProCost Name of Measure. User-defined. For PTR measures, defined naming conventions apply.
Note on C7: :ProCost Annual electric savings for the measure in kWh at the site. May be positive, negative or zero. Savings are incremental to the baseline alternative.
Note on D7: :ProCost Physical life of the measure in years. Must be >=1.
Note on E7: :ProCost Initial cost to install the measure in dollars. Costs are incremental to the baseline alternative. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on F7: :ProCost Annaul opperations and maintenace cost for the measure in dollars. Must be incremental cost over the baseline alternative. May be positive, negative or zero. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page. O&M costs are enetered as positive values. Negative values represent O&M savings compared to the baseline alternative. Example: Annualized maintenace cost for a heat pump heating system compared to a baseline electric resistance heating system.
Note on G7: :ProCost Name of the pointer to the shape of the savings. The shapes represent the daily and monthly shape of the savings in four time segments for each month of the year. Shape of the savings is relative to the baseline alternative. These shaps are in the MC_AND_Loadshape file.
Note on H7: :ProCost Annual value of any non-energy benefits of the measure, relative to the baseline alternative. Expressed in dollars per year and denominated in dollars of the 'Cost Reference Year'. Positive value represents dollar savings. Negative value represents dollar cost. Example: Water, detergent and sewer savings from efficient clothes washer.
Note on I7: : Cost in dollars that is incurred for Period 1. Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on J7: :ProCost Duration of Period1. The time at which Period 1 costs, or savings, occur. In years.
Note on K7: : Cost in dollars that is incurred for Period 2 Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on L7: :ProCost Duration of Period 2. The time at which Period 2 costs, or savings, occur. In years.
Note on M7: : Cost in dollars that is incurred for Period 3. Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on N7: :ProCost Duration of Period 3. The time at which Period 3 costs, or savings, occur. In years.
Note on O7: : Annual gas savings, or increases, in therms.
Note on P7: :ProCost Name of the pointer to the shape of the savings. The shapes represent the daily and monthly shape of the savings in four time segments for each month of the year. Shape of the savings is relative to the baseline alternative. These shaps are in the MC_AND_Loadshape file.
Note on BH70: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BM70: Direct and program administrative costs of the measure to sponsor. Separate costs for each sponsor. Depends on share of costs incurred by sponsor, sponsor cost of capital, and financing term which are user-defined inputs. Includes applicable Capital, O&M, Periodic Replacement and Program Administrative costs. Sponsor costs are levelized over program life. Does not include any adjustments for benefit. NOTE: Units are per kWh for 'Electric' runs and per therm for 'Gas' runs for all sponsors.
Note on CE70: All costs minus all benefits regardless of which sponsor incurs the cost or accrues the benefits. TRC Net Levelized Cost includes all applicable costs and all benefits. In addition to energy system costs and benefits, TRC Net Levelized Cost includes non-energy, other-fuel, O&M, periodic-replacement and risk-mitigation benefits and costs. TRC Net Levelized Cost corresponds to TRC B/C ratios with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure. The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the TRC B/C ratio and the TRC Net Levelized Cost. If Risk-Mitigation credit is non-zero, TRC Levelized Cost will be reduced by the risk-mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on CW70: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BH111: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BM111: Direct and program administrative costs of the measure to sponsor. Separate costs for each sponsor. Depends on share of costs incurred by sponsor, sponsor cost of capital, and financing term which are user-defined inputs. Includes applicable Capital, O&M, Periodic Replacement and Program Administrative costs. Sponsor costs are levelized over program life. Does not include any adjustments for benefit. NOTE: Units are per kWh for 'Electric' runs and per therm for 'Gas' runs for all sponsors.
Note on CE111: All costs minus all benefits regardless of which sponsor incurs the cost or accrues the benefits. TRC Net Levelized Cost includes all applicable costs and all benefits. In addition to energy system costs and benefits, TRC Net Levelized Cost includes non-energy, other-fuel, O&M, periodic-replacement and risk-mitigation benefits and costs. TRC Net Levelized Cost corresponds to TRC B/C ratios with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure. The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the TRC B/C ratio and the TRC Net Levelized Cost. If Risk-Mitigation credit is non-zero, TRC Levelized Cost will be reduced by the risk-mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on CW111: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.

## M_Input_Raw_Out
Shaped Savings Results; By Category and sorted by TRC BC ratio
[14 empty] | Savings Allocation by Category and Month for Segments 1 | [11 empty] | Savings Allocation by Category and Month for Segments 2
Category | Measure | Busbar Savings | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Wholesale KW | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
VRF-New-University |  | 10.3009 | 4 | 0.8 | 4.8 | 5.0795 | 6.2037 | 4081.9747 | 2.4047 | 29.4375 | 1.2213 | 0.097861 | 0.00051131 | 0.17125 | 0.12557 | 0.22773 | 0.22081 | 0.51016 | 0.88248 | 1.6115 | 1.7598 | 0.8277 | 0.379 | 0.16996 | 0.14276 | 0.1695 | 0.1257 | 0.17373 | 0.17378 | 0.30522 | 0.33381 | 0.58623 | 0.46175 | 0.39614 | 0.22328 | 0.16955 | 0.15345
VRF-New-Residential Care |  | 10.3009 | 4 | 0.8 | 4.8 | 5.0795 | 6.2037 | 4081.9747 | 2.4047 | 29.4375 | 1.2213 | 0.097861 | 0.00051131 | 0.17125 | 0.12557 | 0.22773 | 0.22081 | 0.51016 | 0.88248 | 1.6115 | 1.7598 | 0.8277 | 0.379 | 0.16996 | 0.14276 | 0.1695 | 0.1257 | 0.17373 | 0.17378 | 0.30522 | 0.33381 | 0.58623 | 0.46175 | 0.39614 | 0.22328 | 0.16955 | 0.15345
VRF-New-Large Off |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Medium Off |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Xlarge Ret |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Large Ret |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Medium Ret |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Small Ret |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-School K-12 |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Warehouse |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Hospital |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Other |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Small Off |  | 10.3009 | 6 | 1.2 | 7.2 | 7.6193 | 6.2037 | 6122.962 | 7.0305 | 47.5796 | 0.81421 | 0.097861 | 0.00051131 | 0.17125 | 0.12557 | 0.22773 | 0.22081 | 0.51016 | 0.88248 | 1.6115 | 1.7598 | 0.8277 | 0.379 | 0.16996 | 0.14276 | 0.1695 | 0.1257 | 0.17373 | 0.17378 | 0.30522 | 0.33381 | 0.58623 | 0.46175 | 0.39614 | 0.22328 | 0.16955 | 0.15345
VRF-New-Supermarket |  | 10.3009 | 6 | 1.2 | 7.2 | 7.6193 | 6.2037 | 6122.962 | 7.0305 | 47.5796 | 0.81421 | 0.097861 | 0.00051131 | 0.17125 | 0.12557 | 0.22773 | 0.22081 | 0.51016 | 0.88248 | 1.6115 | 1.7598 | 0.8277 | 0.379 | 0.16996 | 0.14276 | 0.1695 | 0.1257 | 0.17373 | 0.17378 | 0.30522 | 0.33381 | 0.58623 | 0.46175 | 0.39614 | 0.22328 | 0.16955 | 0.15345
VRF-New-MiniMart |  | 10.3009 | 6 | 1.2 | 7.2 | 7.6193 | 6.2037 | 6122.962 | 7.0305 | 47.5796 | 0.81421 | 0.097861 | 0.00051131 | 0.17125 | 0.12557 | 0.22773 | 0.22081 | 0.51016 | 0.88248 | 1.6115 | 1.7598 | 0.8277 | 0.379 | 0.16996 | 0.14276 | 0.1695 | 0.1257 | 0.17373 | 0.17378 | 0.30522 | 0.33381 | 0.58623 | 0.46175 | 0.39614 | 0.22328 | 0.16955 | 0.15345
VRF-New-Restaurant |  | 10.3009 | 6 | 1.2 | 7.2 | 7.6193 | 6.2037 | 6122.962 | 7.0305 | 47.5796 | 0.81421 | 0.097861 | 0.00051131 | 0.17125 | 0.12557 | 0.22773 | 0.22081 | 0.51016 | 0.88248 | 1.6115 | 1.7598 | 0.8277 | 0.379 | 0.16996 | 0.14276 | 0.1695 | 0.1257 | 0.17373 | 0.17378 | 0.30522 | 0.33381 | 0.58623 | 0.46175 | 0.39614 | 0.22328 | 0.16955 | 0.15345
VRF-New-Assembly |  | 9.6703 | 6 | 1.2 | 7.2 | 7.6193 | 5.8239 | 6522.2687 | 7.9355 | 51.129 | 0.76437 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Lodging |  | 9.6703 | 8 | 1.6 | 9.6 | 10.1591 | 5.8239 | 8696.3583 | 12.8629 | 70.4543 | 0.57327 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405

## M_Input_Raw
Data Set Name
Measure Index Name | VRF
Costs must be denominated in the same year as 'Input Cost Reference Year' = |  | 2012
| Cost inflator 2006 to 2012 | 1.1074
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105
Input Data | [7 empty] | Periodic Replacement Costs and Savings and Replacement Period | [5 empty] | Gas Inputs |  | Retro or LO | Early Retrofit Parameters
Category Name | Measure Name | Savings (kwh/yr) | Life (yrs) | Capital Cost | Annual O&M | Shape Pointer | Non-E Val ($/yr) | Cost 1 ($) | Period 1 | Cost 2 ($) | Period 2 | Cost 3 ($) | Period 3 | Savings (therms/yr) | Shape Pointer | R or L | Savings 2 (kWh) | Remaining Life (yrs) | Salvage Value ($)
VRF-New-Large Off | VRF-New-Large Off-ElecHt | 5.2 | 20 | 3.68 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Medium Off | VRF-New-Medium Off-ElecHt | 2.83 | 20 | 2.29 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Small Off | VRF-New-Small Off-ElecHt | 5.2 | 20 | 2.29 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Xlarge Ret | VRF-New-Xlarge Ret-ElecHt | 2.94 | 20 | 2.6667 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Large Ret | VRF-New-Large Ret-ElecHt | 2.94 | 20 | 2.6667 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Medium Ret | VRF-New-Medium Ret-ElecHt | 2.94 | 20 | 2.6667 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Small Ret | VRF-New-Small Ret-ElecHt | 2.94 | 20 | 2.6667 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-School K-12 | VRF-New-School K-12-ElecHt | 2.94 | 20 | 2.6667 |  | Commercial-School-Vent | [9 empty] | L
VRF-New-University | VRF-New-University-ElecHt | 2.94 | 20 | 2.6667 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Warehouse | VRF-New-Warehouse-ElecHt | 2.94 | 20 | 2.6667 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Supermarket | VRF-New-Supermarket-ElecHt | 7.3248 | 20 | 4.95 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-MiniMart | VRF-New-MiniMart-ElecHt | 7.3248 | 20 | 4.95 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Restaurant | VRF-New-Restaurant-ElecHt | 7.3248 | 20 | 4.95 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Lodging | VRF-New-Lodging-ElecHt | 5.2 | 20 | 3.68 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Hospital | VRF-New-Hospital-ElecHt | 5.3185 | 20 | 4.13 |  | Commercial-Healthcare-Vent | [9 empty] | L
VRF-New-Residential Care | VRF-New-Residential Care-ElecHt | 5.3185 | 20 | 4.13 |  | Commercial-Healthcare-Vent | [9 empty] | L
VRF-New-Assembly | VRF-New-Assembly-ElecHt | 5.3185 | 20 | 2.6667 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Other | VRF-New-Other-ElecHt | 5.3185 | 20 | 2.6667 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Large Off | VRF-New-Large Off-GasHt | 4 | 20 | 4.0889 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Medium Off | VRF-New-Medium Off-GasHt | 2.6 | 20 | 2.5444 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Small Off | VRF-New-Small Off-GasHt | 4 | 20 | 2.5444 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Xlarge Ret | VRF-New-Xlarge Ret-GasHt | 2.04 | 20 | 2.963 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Large Ret | VRF-New-Large Ret-GasHt | 2.04 | 20 | 2.963 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Medium Ret | VRF-New-Medium Ret-GasHt | 2.04 | 20 | 2.963 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Small Ret | VRF-New-Small Ret-GasHt | 2.04 | 20 | 2.963 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-School K-12 | VRF-New-School K-12-GasHt | 2.04 | 20 | 2.963 |  | Commercial-School-Vent | [9 empty] | L
VRF-New-University | VRF-New-University-GasHt | 2.04 | 20 | 2.963 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Warehouse | VRF-New-Warehouse-GasHt | 2.04 | 20 | 2.963 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Supermarket | VRF-New-Supermarket-GasHt | 5.9073 | 20 | 5.5 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-MiniMart | VRF-New-MiniMart-GasHt | 5.9073 | 20 | 5.5 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Restaurant | VRF-New-Restaurant-GasHt | 5.9073 | 20 | 5.5 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Lodging | VRF-New-Lodging-GasHt | 4 | 20 | 4.0889 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | L
VRF-New-Hospital | VRF-New-Hospital-GasHt | 3.901 | 20 | 4.5889 |  | Commercial-Healthcare-Vent | [9 empty] | L
VRF-New-Residential Care | VRF-New-Residential Care-GasHt | 3.901 | 20 | 4.5889 |  | Commercial-Healthcare-Vent | [9 empty] | L
VRF-New-Assembly | VRF-New-Assembly-GasHt | 3.901 | 20 | 2.963 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | l
VRF-New-Other | VRF-New-Other-GasHt | 3.901 | 20 | 2.963 |  | C-All-HVAC-Vent-All-All-E | [9 empty] | l
ProCost Results
Version: | ProCost 3.0 - Beta04
Run Time: | Thursday, 5 February , 2015 at 9:43 AM
Regurgitation of ProData input parameters which were used for this run
| Run Parameters |  | Run Parameters |  |  | Marginal Cost & Conservation Load Shape Parameters | [9 empty] | Sponsor Parameters | [5 empty] | Program Parameters |  |  | Utility System Parameters
| Run Type | Electric | Run Type | Electric |  | Marginal Costs and Savings Shape File | \\nas2\Q\SeventhPlan\Conservation Analysis\Global EE Inputs\MC Files\MC_AND_LOADSHAPE_v3.0_24segment-7P-D9 - NewSegValues.xlsx |  |  | 6P MidC Final (with carbon) | [6 empty] | Customer | Wholesale Elec | Retail Elec | Nat Gas |  | Program Life (yrs) | 20 |  |  | Electric | Gas
| Negative B/C Ratios | Off | Negative B/C Ratios | Off |  | Marginal Elec Avoided Cost Input Worksheet | 7P Mid |  |  | Conservation Load Shapes | [5 empty] | Real After-Tax Cost of Capital | 0.068013 | 0.043878 | 0.053289 | 0.054479 |  | Program Start Date | 2016 |  | Bulk System T&D Loss Factor | 0.0040389 | 0.01
| Admin Cost @ Category Level | On | Admin Cost @ Category Level | On |  | Elec Savings Shape Input Worksheet | GLSShapes |  |  | 6P_Gas_Final | [5 empty] | Financial Life (years) | 12 | 12 | 1 | 1 |  | Present Value Time Zero | 2016 |  | Bulk System T&D Credit ($/kw-yr)($/dailytherm-yr) | 26 | 0
| Repeat Periodic Replacement | On | Repeat Periodic Replacement | On |  | Marginal Gas Avoided Cost Input Worksheet | 7P Gas |  |  | Conservation Load Shapes | [6 empty] | Customer | Wholesale Elec | Retail Elec | Nat Gas |  | Input Cost Reference Year | 2012 |  | Bulk System T&D I2R Loss Component (%) | 0.9 | N/A
[6 empty] | Gas Savings Shape Input Worksheet | GLSShapes | [8 empty] | Sponsor Share of Initial Capital Cost | 0.35 | 0.195 | 0.04875 | 0.40625 |  | Real Discount Rate | 0.04 |  | Local System Dist Loss Factor | 0.047399 | 0
| Run Type: | Electric |  |  |  | Marginal Elec CO2 per kWh Input Worksheet | CO2 lbs per kWh .95 |  |  | CO2 lbs per therm | [5 empty] | Sponsor Share of Annual O&M | 1 | 0 | 0 | 0 |  | Capital Real Escalation Rate | 0 |  | Local System Dist Credit ($/kw-yr)($/dailytherm-yr) | 31 | 0
| Negative B/C Ratios: | False: (Converts Negative B/C Ratios) |  |  |  | Marginal Gas CO2 per therm Input Worksheet | CO2 lbs per therm |  |  | Zero Dollars per ton CO2 | [5 empty] | Sponsor Share of Periodic Replacement Cost | 1 | 0 | 0 | 0 |  | Admin Cost (as % of Initial Capital Cost) | 0.2 |  | Local System Dist I2R Loss Component (%) | 0.7 | N/A
| Admin Cost / Category Level: | True: Admin Costs added at Category Results |  |  |  | Marginal Avoided Cost CO2 Input Worksheet | Zero Dollars per ton CO2 |  |  | LineLossShapes | [5 empty] | Sponsor Share of Admin Cost |  | 0.3 | 0.075 | 0.625 |  | Regional Act Conservation Credit (%) | 0.1 |  | Risk-Mitigation Credit (mills/kWh)(mills/therm) - Retro. | 0 | 0
| Periodic O&M Treatment: | True: (Periodic O&M Repeats over measure life) |  |  |  | Line Loss Shape Input Worksheet | LineLossShapes | [8 empty] | Last Year of Non-Customer O&M & Period Replacement |  | 20 |  |  |  | Report Annual Carbon Saved for Year | 2018 |  | Risk-Mitigation Credit (mills/kWh)(mills/therm) - Lost Op. | 0 | 0
Measure Results; Sorted in same order as input
Total Results |  | Measure Input Data | [8 empty] | Savings | [5 empty] | PV Capital |  |  |  | PV Admin |  |  |  | PV O&M |  |  |  | PV Periodic Repl. |  |  |  | Total PV Capital, O&M and Periodic Repl Costs |  |  |  |  | PV Wholesale Electric Utility Costs & Benefits | [6 empty] | PV Retail Electric Utility Costs & Benefits | [6 empty] | PV Electric Utility System Costs & Benefits | [5 empty] | Electric Utility System Economics |  | Sponsor Levelized Cost (mills/kwh) |  |  |  |  | PV Regional Costs & Benefits | [15 empty] | TRC Economics |  | Physical CO2 | [6 empty] | Gas Inputs |  |  |  | PV Gas Utility System Costs & Benefits |  |  |  |  | Gas Utility System Economics
Category | Measure | Measure Life | Site Savings (kWh) | Site Savings (therms) | Capital Cost ($/unit) | Annual O&M Cost ($/unit) | PV Per. Repl. Cost ($/unit) | Load Shape (electric) | Diversified Load Factor (electric) | Wholesale Power Coincidence Factor (electric) | Wholesale Electric Energy (kWh) | Wholesale Electric Demand (kw) | Retail Electric Demand (kW) | Wholesale Gas Energy (therms/yr) | Wholesale Gas Demand (therms/day) | Retail Gas Demand (therms/day) | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Total | Wholesale Utility System Energy | Wholesale Utility System T&D Def. Cap. | Wholesale Utility System Act C-E Credit | Wholesale Utility System Risk Mitigation Benefit | Wholesale Utility System Total System Benefit | Wholesale Utility System Total Non-Consumer Cost | Wholesale Utility System B/C Ratio | Retail Utility System Energy | Retail Utility System T&D Def. Cap. | Retail Utility System Act C-E Credit | Retail Utility System Risk Mitigation Benefit | Retail Utility System Total System Benefit | Retail Utility System Total Non-Consumer Cost | Retail Utility System System B/C Ratio | Utility System Energy | Utility System T&D Def. Cap. | Utility System Act C-E Credit | Utility System Total Risk Mitigation Benefit | Utility System Total System Benefit | Utility System Total Non-Consumer Cost | Utility System Net Levelized Cost (Net of Elec T&D Capacity Benefits, Act Credit & Risk-Mitigation Benefit) in mills/kwh | Utility System System B/C Ratio | Wholesale Electric Levelized Cost | Retail Electric Levelized Cost | Natural Gas Levelized Cost | Customer Levelized Cost | Total Levelized Cost | PV Regional Electric Energy | PV Regional Gas Energy | PV Regional Electric T&D Def. Cap. | PV Regional Gas T&D Def. Cap. | PV Regional Electric System CO2 | PV Regional Gas System CO2 | PV Regional Electric System Risk-Mitigation Benefit | PV Regional Gas System Risk-Mitigation Benefit | PV Regional Non-E Value | PV Regional Act Credit | PV Regional Capital Cost | PV Regional Admin Cost | PV Regional Annual O&M Cost | PV Regional Periodic Replacement Cost | PV Total Regional Benefit | PV Total Regional Cost | TRC B/C Ratio | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | Electric System CO2 Avoided (Lifetime Tons) | Gas System CO2 Avoided (Lifetime Tons) | Total System CO2 Avoided (Lifetime Tons) | Electric System CO2 Avoided (Annual Tons in 2018) | Gas System CO2 Avoided (Annual Tons in 2018) | Total System CO2 Avoided (Annual Tons in 2018) |  | Gas Site Savings (therms) | Load Shape (gas) | Diversitfied Load Factor (gas) | Wholesale Coincidence Factor (gas) | Total Gas Utility System Energy | Gas Utility System T&D Def. Cap. | Gas Utility System Risk Mitigation Benefit | Gas Utility System Total System Benefit | Gas Utility System Total Non-Consumer Cost | Gas Utility System Net Levelized Cost (Net of Gas T&D Capacity Benefits & Risk-Mitigation Benefits) in cents/therm | Gas Utility System System B/C Ratio
VRF-New-Large Off | VRF-New-Large Off-ElecHt | 20 | 5.2 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 5.5738 | 0.00027667 | 0.00027467 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.8382 | 0.097761 | 0.2936 | 0 | 3.2296 | 0.39883 | 8.0977 | 2.8382 | 0.11572 | 0.29539 | 0 | 3.2493 | 0.098746 | 32.906 | 2.8382 | 0.21348 | 0.30517 | 0 | 3.3569 | 0.49757 | -0.27824 | 6.7465 | 5.265 | 1.3036 | 10.8753 | 10.8037 | 28.2476 | 2.8382 | 0 | 0.21348 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30517 | 2.1398 |  | 0 | 0 | 3.3569 | 2.1398 | 1.5688 | 21.4008 | 0.052953 | 0 | 0.052953 | 0.0026476 | 0 | 0.0026476 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-Medium Off | VRF-New-Medium Off-ElecHt | 20 | 5.2 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 5.5738 | 0.00027667 | 0.00027467 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.8382 | 0.097761 | 0.2936 | 0 | 3.2296 | 0.39883 | 8.0977 | 2.8382 | 0.11572 | 0.29539 | 0 | 3.2493 | 0.098746 | 32.906 | 2.8382 | 0.21348 | 0.30517 | 0 | 3.3569 | 0.49757 | -0.27824 | 6.7465 | 5.265 | 1.3036 | 10.8753 | 10.8037 | 28.2476 | 2.8382 | 0 | 0.21348 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30517 | 2.1398 |  | 0 | 0 | 3.3569 | 2.1398 | 1.5688 | 21.4008 | 0.052953 | 0 | 0.052953 | 0.0026476 | 0 | 0.0026476 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-Small Off | VRF-New-Small Off-ElecHt | 20 | 5.41 | 0 | 3 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 5.7989 | 0.00028784 | 0.00028576 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | 3.2096 | 2.9528 | 0.10171 | 0.30545 | 0 | 3.36 | 0.59824 | 5.6165 | 2.9528 | 0.12039 | 0.30732 | 0 | 3.3806 | 0.14812 | 22.8232 | 2.9528 | 0.2221 | 0.31749 | 0 | 3.4924 | 0.74636 | 2.6236 | 4.6793 | 7.591 | 1.8795 | 15.6798 | 15.5765 | 40.7267 | 2.9528 | 0 | 0.2221 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31749 | 3.2096 |  | 0 | 0 | 3.4924 | 3.2096 | 1.0881 | 33.8798 | 0.055091 | 0 | 0.055091 | 0.0027545 | 0 | 0.0027545 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2357 | 9999 | 0
VRF-New-Xlarge Ret | VRF-New-Xlarge Ret-ElecHt | 20 | 5.2 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 5.5738 | 0.00027667 | 0.00027467 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.8382 | 0.097761 | 0.2936 | 0 | 3.2296 | 0.39883 | 8.0977 | 2.8382 | 0.11572 | 0.29539 | 0 | 3.2493 | 0.098746 | 32.906 | 2.8382 | 0.21348 | 0.30517 | 0 | 3.3569 | 0.49757 | -0.27824 | 6.7465 | 5.265 | 1.3036 | 10.8753 | 10.8037 | 28.2476 | 2.8382 | 0 | 0.21348 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30517 | 2.1398 |  | 0 | 0 | 3.3569 | 2.1398 | 1.5688 | 21.4008 | 0.052953 | 0 | 0.052953 | 0.0026476 | 0 | 0.0026476 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-Large Ret | VRF-New-Large Ret-ElecHt | 20 | 5.2 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 5.5738 | 0.00027667 | 0.00027467 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.8382 | 0.097761 | 0.2936 | 0 | 3.2296 | 0.39883 | 8.0977 | 2.8382 | 0.11572 | 0.29539 | 0 | 3.2493 | 0.098746 | 32.906 | 2.8382 | 0.21348 | 0.30517 | 0 | 3.3569 | 0.49757 | -0.27824 | 6.7465 | 5.265 | 1.3036 | 10.8753 | 10.8037 | 28.2476 | 2.8382 | 0 | 0.21348 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30517 | 2.1398 |  | 0 | 0 | 3.3569 | 2.1398 | 1.5688 | 21.4008 | 0.052953 | 0 | 0.052953 | 0.0026476 | 0 | 0.0026476 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-Medium Ret | VRF-New-Medium Ret-ElecHt | 20 | 5.2 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 5.5738 | 0.00027667 | 0.00027467 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.8382 | 0.097761 | 0.2936 | 0 | 3.2296 | 0.39883 | 8.0977 | 2.8382 | 0.11572 | 0.29539 | 0 | 3.2493 | 0.098746 | 32.906 | 2.8382 | 0.21348 | 0.30517 | 0 | 3.3569 | 0.49757 | -0.27824 | 6.7465 | 5.265 | 1.3036 | 10.8753 | 10.8037 | 28.2476 | 2.8382 | 0 | 0.21348 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30517 | 2.1398 |  | 0 | 0 | 3.3569 | 2.1398 | 1.5688 | 21.4008 | 0.052953 | 0 | 0.052953 | 0.0026476 | 0 | 0.0026476 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-Small Ret | VRF-New-Small Ret-ElecHt | 20 | 5.2 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 5.5738 | 0.00027667 | 0.00027467 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.8382 | 0.097761 | 0.2936 | 0 | 3.2296 | 0.39883 | 8.0977 | 2.8382 | 0.11572 | 0.29539 | 0 | 3.2493 | 0.098746 | 32.906 | 2.8382 | 0.21348 | 0.30517 | 0 | 3.3569 | 0.49757 | -0.27824 | 6.7465 | 5.265 | 1.3036 | 10.8753 | 10.8037 | 28.2476 | 2.8382 | 0 | 0.21348 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30517 | 2.1398 |  | 0 | 0 | 3.3569 | 2.1398 | 1.5688 | 21.4008 | 0.052953 | 0 | 0.052953 | 0.0026476 | 0 | 0.0026476 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-School K-12 | VRF-New-School K-12-ElecHt | 20 | 5.2 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 5.5738 | 0.00027667 | 0.00027467 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.8382 | 0.097761 | 0.2936 | 0 | 3.2296 | 0.39883 | 8.0977 | 2.8382 | 0.11572 | 0.29539 | 0 | 3.2493 | 0.098746 | 32.906 | 2.8382 | 0.21348 | 0.30517 | 0 | 3.3569 | 0.49757 | -0.27824 | 6.7465 | 5.265 | 1.3036 | 10.8753 | 10.8037 | 28.2476 | 2.8382 | 0 | 0.21348 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30517 | 2.1398 |  | 0 | 0 | 3.3569 | 2.1398 | 1.5688 | 21.4008 | 0.052953 | 0 | 0.052953 | 0.0026476 | 0 | 0.0026476 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-University | VRF-New-University-ElecHt | 20 | 5.41 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 5.7989 | 0.00028784 | 0.00028576 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.9528 | 0.10171 | 0.30545 | 0 | 3.36 | 0.39883 | 8.4247 | 2.9528 | 0.12039 | 0.30732 | 0 | 3.3806 | 0.098746 | 34.2349 | 2.9528 | 0.2221 | 0.31749 | 0 | 3.4924 | 0.49757 | -0.53321 | 7.0189 | 5.0606 | 1.253 | 10.4532 | 10.3843 | 27.1511 | 2.9528 | 0 | 0.2221 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31749 | 2.1398 |  | 0 | 0 | 3.4924 | 2.1398 | 1.6322 | 20.3043 | 0.055091 | 0 | 0.055091 | 0.0027545 | 0 | 0.0027545 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-Warehouse | VRF-New-Warehouse-ElecHt | 20 | 5.2 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 5.5738 | 0.00027667 | 0.00027467 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.8382 | 0.097761 | 0.2936 | 0 | 3.2296 | 0.39883 | 8.0977 | 2.8382 | 0.11572 | 0.29539 | 0 | 3.2493 | 0.098746 | 32.906 | 2.8382 | 0.21348 | 0.30517 | 0 | 3.3569 | 0.49757 | -0.27824 | 6.7465 | 5.265 | 1.3036 | 10.8753 | 10.8037 | 28.2476 | 2.8382 | 0 | 0.21348 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30517 | 2.1398 |  | 0 | 0 | 3.3569 | 2.1398 | 1.5688 | 21.4008 | 0.052953 | 0 | 0.052953 | 0.0026476 | 0 | 0.0026476 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-Supermarket | VRF-New-Supermarket-ElecHt | 20 | 5.41 | 0 | 3 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 5.7989 | 0.00028784 | 0.00028576 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | 3.2096 | 2.9528 | 0.10171 | 0.30545 | 0 | 3.36 | 0.59824 | 5.6165 | 2.9528 | 0.12039 | 0.30732 | 0 | 3.3806 | 0.14812 | 22.8232 | 2.9528 | 0.2221 | 0.31749 | 0 | 3.4924 | 0.74636 | 2.6236 | 4.6793 | 7.591 | 1.8795 | 15.6798 | 15.5765 | 40.7267 | 2.9528 | 0 | 0.2221 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31749 | 3.2096 |  | 0 | 0 | 3.4924 | 3.2096 | 1.0881 | 33.8798 | 0.055091 | 0 | 0.055091 | 0.0027545 | 0 | 0.0027545 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2357 | 9999 | 0
VRF-New-MiniMart | VRF-New-MiniMart-ElecHt | 20 | 5.41 | 0 | 3 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 5.7989 | 0.00028784 | 0.00028576 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | 3.2096 | 2.9528 | 0.10171 | 0.30545 | 0 | 3.36 | 0.59824 | 5.6165 | 2.9528 | 0.12039 | 0.30732 | 0 | 3.3806 | 0.14812 | 22.8232 | 2.9528 | 0.2221 | 0.31749 | 0 | 3.4924 | 0.74636 | 2.6236 | 4.6793 | 7.591 | 1.8795 | 15.6798 | 15.5765 | 40.7267 | 2.9528 | 0 | 0.2221 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31749 | 3.2096 |  | 0 | 0 | 3.4924 | 3.2096 | 1.0881 | 33.8798 | 0.055091 | 0 | 0.055091 | 0.0027545 | 0 | 0.0027545 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2357 | 9999 | 0
VRF-New-Restaurant | VRF-New-Restaurant-ElecHt | 20 | 5.41 | 0 | 3 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 5.7989 | 0.00028784 | 0.00028576 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | 3.2096 | 2.9528 | 0.10171 | 0.30545 | 0 | 3.36 | 0.59824 | 5.6165 | 2.9528 | 0.12039 | 0.30732 | 0 | 3.3806 | 0.14812 | 22.8232 | 2.9528 | 0.2221 | 0.31749 | 0 | 3.4924 | 0.74636 | 2.6236 | 4.6793 | 7.591 | 1.8795 | 15.6798 | 15.5765 | 40.7267 | 2.9528 | 0 | 0.2221 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31749 | 3.2096 |  | 0 | 0 | 3.4924 | 3.2096 | 1.0881 | 33.8798 | 0.055091 | 0 | 0.055091 | 0.0027545 | 0 | 0.0027545 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2357 | 9999 | 0
VRF-New-Lodging | VRF-New-Lodging-ElecHt | 20 | 5.2 | 0 | 4 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 5.5738 | 0.00027667 | 0.00027467 | 0 | 0 | 0 | 0.79765 | 0.19749 | 1.6476 | 1.6368 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79765 | 0.19749 | 1.6476 | 1.6368 | 4.2795 | 2.8382 | 0.097761 | 0.2936 | 0 | 3.2296 | 0.79765 | 4.0488 | 2.8382 | 0.11572 | 0.29539 | 0 | 3.2493 | 0.19749 | 16.453 | 2.8382 | 0.21348 | 0.30517 | 0 | 3.3569 | 0.99515 | 6.2903 | 3.3732 | 10.53 | 2.6071 | 21.7507 | 21.6073 | 56.4952 | 2.8382 | 0 | 0.21348 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30517 | 4.2795 |  | 0 | 0 | 3.3569 | 4.2795 | 0.7844 | 49.6484 | 0.052953 | 0 | 0.052953 | 0.0026476 | 0 | 0.0026476 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.6476 | 9999 | 0
VRF-New-Hospital | VRF-New-Hospital-ElecHt | 20 | 5.2 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 5.5738 | 0.00027667 | 0.00027467 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.8382 | 0.097761 | 0.2936 | 0 | 3.2296 | 0.39883 | 8.0977 | 2.8382 | 0.11572 | 0.29539 | 0 | 3.2493 | 0.098746 | 32.906 | 2.8382 | 0.21348 | 0.30517 | 0 | 3.3569 | 0.49757 | -0.27824 | 6.7465 | 5.265 | 1.3036 | 10.8753 | 10.8037 | 28.2476 | 2.8382 | 0 | 0.21348 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30517 | 2.1398 |  | 0 | 0 | 3.3569 | 2.1398 | 1.5688 | 21.4008 | 0.052953 | 0 | 0.052953 | 0.0026476 | 0 | 0.0026476 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-Residential Care | VRF-New-Residential Care-ElecHt | 20 | 5.41 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 5.7989 | 0.00028784 | 0.00028576 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.9528 | 0.10171 | 0.30545 | 0 | 3.36 | 0.39883 | 8.4247 | 2.9528 | 0.12039 | 0.30732 | 0 | 3.3806 | 0.098746 | 34.2349 | 2.9528 | 0.2221 | 0.31749 | 0 | 3.4924 | 0.49757 | -0.53321 | 7.0189 | 5.0606 | 1.253 | 10.4532 | 10.3843 | 27.1511 | 2.9528 | 0 | 0.2221 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31749 | 2.1398 |  | 0 | 0 | 3.4924 | 2.1398 | 1.6322 | 20.3043 | 0.055091 | 0 | 0.055091 | 0.0027545 | 0 | 0.0027545 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-Assembly | VRF-New-Assembly-ElecHt | 20 | 5.2 | 0 | 3 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 5.5738 | 0.00027667 | 0.00027467 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | 3.2096 | 2.8382 | 0.097761 | 0.2936 | 0 | 3.2296 | 0.59824 | 5.3985 | 2.8382 | 0.11572 | 0.29539 | 0 | 3.2493 | 0.14812 | 21.9373 | 2.8382 | 0.21348 | 0.30517 | 0 | 3.3569 | 0.74636 | 3.006 | 4.4977 | 7.8975 | 1.9554 | 16.313 | 16.2055 | 42.3714 | 2.8382 | 0 | 0.21348 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30517 | 3.2096 |  | 0 | 0 | 3.3569 | 3.2096 | 1.0459 | 35.5246 | 0.052953 | 0 | 0.052953 | 0.0026476 | 0 | 0.0026476 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2357 | 9999 | 0
VRF-New-Other | VRF-New-Other-ElecHt | 20 | 5.2 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 5.5738 | 0.00027667 | 0.00027467 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.8382 | 0.097761 | 0.2936 | 0 | 3.2296 | 0.39883 | 8.0977 | 2.8382 | 0.11572 | 0.29539 | 0 | 3.2493 | 0.098746 | 32.906 | 2.8382 | 0.21348 | 0.30517 | 0 | 3.3569 | 0.49757 | -0.27824 | 6.7465 | 5.265 | 1.3036 | 10.8753 | 10.8037 | 28.2476 | 2.8382 | 0 | 0.21348 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30517 | 2.1398 |  | 0 | 0 | 3.3569 | 2.1398 | 1.5688 | 21.4008 | 0.052953 | 0 | 0.052953 | 0.0026476 | 0 | 0.0026476 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-Large Off | VRF-New-Large Off-GasHt | 20 | 3.8217 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 4.0964 | 0.00020333 | 0.00020187 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.0859 | 0.071848 | 0.21577 | 0 | 2.3735 | 0.39883 | 5.9513 | 2.0859 | 0.085046 | 0.21709 | 0 | 2.388 | 0.098746 | 24.1837 | 2.0859 | 0.15689 | 0.22428 | 0 | 2.4671 | 0.49757 | 2.0908 | 4.9582 | 7.1639 | 1.7737 | 14.7977 | 14.7002 | 38.4356 | 2.0859 | 0 | 0.15689 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22428 | 2.1398 |  | 0 | 0 | 2.4671 | 2.1398 | 1.153 | 31.5887 | 0.038917 | 0 | 0.038917 | 0.0019458 | 0 | 0.0019458 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-Medium Off | VRF-New-Medium Off-GasHt | 20 | 3.8217 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 4.0964 | 0.00020333 | 0.00020187 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.0859 | 0.071848 | 0.21577 | 0 | 2.3735 | 0.39883 | 5.9513 | 2.0859 | 0.085046 | 0.21709 | 0 | 2.388 | 0.098746 | 24.1837 | 2.0859 | 0.15689 | 0.22428 | 0 | 2.4671 | 0.49757 | 2.0908 | 4.9582 | 7.1639 | 1.7737 | 14.7977 | 14.7002 | 38.4356 | 2.0859 | 0 | 0.15689 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22428 | 2.1398 |  | 0 | 0 | 2.4671 | 2.1398 | 1.153 | 31.5887 | 0.038917 | 0 | 0.038917 | 0.0019458 | 0 | 0.0019458 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-Small Off | VRF-New-Small Off-GasHt | 20 | 4.2 | 0 | 3 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 4.502 | 0.00022346 | 0.00022185 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | 3.2096 | 2.2924 | 0.07896 | 0.23714 | 0 | 2.6085 | 0.59824 | 4.3603 | 2.2924 | 0.093466 | 0.23859 | 0 | 2.6245 | 0.14812 | 17.7186 | 2.2924 | 0.17243 | 0.24648 | 0 | 2.7113 | 0.74636 | 5.352 | 3.6327 | 9.7779 | 2.4209 | 20.1971 | 20.064 | 52.4598 | 2.2924 | 0 | 0.17243 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24648 | 3.2096 |  | 0 | 0 | 2.7113 | 3.2096 | 0.84474 | 45.613 | 0.04277 | 0 | 0.04277 | 0.0021384 | 0 | 0.0021384 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2357 | 9999 | 0
VRF-New-Xlarge Ret | VRF-New-Xlarge Ret-GasHt | 20 | 3.8217 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 4.0964 | 0.00020333 | 0.00020187 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.0859 | 0.071848 | 0.21577 | 0 | 2.3735 | 0.39883 | 5.9513 | 2.0859 | 0.085046 | 0.21709 | 0 | 2.388 | 0.098746 | 24.1837 | 2.0859 | 0.15689 | 0.22428 | 0 | 2.4671 | 0.49757 | 2.0908 | 4.9582 | 7.1639 | 1.7737 | 14.7977 | 14.7002 | 38.4356 | 2.0859 | 0 | 0.15689 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22428 | 2.1398 |  | 0 | 0 | 2.4671 | 2.1398 | 1.153 | 31.5887 | 0.038917 | 0 | 0.038917 | 0.0019458 | 0 | 0.0019458 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-Large Ret | VRF-New-Large Ret-GasHt | 20 | 3.8217 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 4.0964 | 0.00020333 | 0.00020187 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.0859 | 0.071848 | 0.21577 | 0 | 2.3735 | 0.39883 | 5.9513 | 2.0859 | 0.085046 | 0.21709 | 0 | 2.388 | 0.098746 | 24.1837 | 2.0859 | 0.15689 | 0.22428 | 0 | 2.4671 | 0.49757 | 2.0908 | 4.9582 | 7.1639 | 1.7737 | 14.7977 | 14.7002 | 38.4356 | 2.0859 | 0 | 0.15689 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22428 | 2.1398 |  | 0 | 0 | 2.4671 | 2.1398 | 1.153 | 31.5887 | 0.038917 | 0 | 0.038917 | 0.0019458 | 0 | 0.0019458 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-Medium Ret | VRF-New-Medium Ret-GasHt | 20 | 3.8217 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 4.0964 | 0.00020333 | 0.00020187 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.0859 | 0.071848 | 0.21577 | 0 | 2.3735 | 0.39883 | 5.9513 | 2.0859 | 0.085046 | 0.21709 | 0 | 2.388 | 0.098746 | 24.1837 | 2.0859 | 0.15689 | 0.22428 | 0 | 2.4671 | 0.49757 | 2.0908 | 4.9582 | 7.1639 | 1.7737 | 14.7977 | 14.7002 | 38.4356 | 2.0859 | 0 | 0.15689 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22428 | 2.1398 |  | 0 | 0 | 2.4671 | 2.1398 | 1.153 | 31.5887 | 0.038917 | 0 | 0.038917 | 0.0019458 | 0 | 0.0019458 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-Small Ret | VRF-New-Small Ret-GasHt | 20 | 3.8217 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 4.0964 | 0.00020333 | 0.00020187 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.0859 | 0.071848 | 0.21577 | 0 | 2.3735 | 0.39883 | 5.9513 | 2.0859 | 0.085046 | 0.21709 | 0 | 2.388 | 0.098746 | 24.1837 | 2.0859 | 0.15689 | 0.22428 | 0 | 2.4671 | 0.49757 | 2.0908 | 4.9582 | 7.1639 | 1.7737 | 14.7977 | 14.7002 | 38.4356 | 2.0859 | 0 | 0.15689 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22428 | 2.1398 |  | 0 | 0 | 2.4671 | 2.1398 | 1.153 | 31.5887 | 0.038917 | 0 | 0.038917 | 0.0019458 | 0 | 0.0019458 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-School K-12 | VRF-New-School K-12-GasHt | 20 | 3.8217 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 4.0964 | 0.00020333 | 0.00020187 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.0859 | 0.071848 | 0.21577 | 0 | 2.3735 | 0.39883 | 5.9513 | 2.0859 | 0.085046 | 0.21709 | 0 | 2.388 | 0.098746 | 24.1837 | 2.0859 | 0.15689 | 0.22428 | 0 | 2.4671 | 0.49757 | 2.0908 | 4.9582 | 7.1639 | 1.7737 | 14.7977 | 14.7002 | 38.4356 | 2.0859 | 0 | 0.15689 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22428 | 2.1398 |  | 0 | 0 | 2.4671 | 2.1398 | 1.153 | 31.5887 | 0.038917 | 0 | 0.038917 | 0.0019458 | 0 | 0.0019458 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-University | VRF-New-University-GasHt | 20 | 4.2 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 4.502 | 0.00022346 | 0.00022185 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.2924 | 0.07896 | 0.23714 | 0 | 2.6085 | 0.39883 | 6.5404 | 2.2924 | 0.093466 | 0.23859 | 0 | 2.6245 | 0.098746 | 26.5779 | 2.2924 | 0.17243 | 0.24648 | 0 | 2.7113 | 0.49757 | 1.2857 | 5.4491 | 6.5186 | 1.6139 | 13.4647 | 13.376 | 34.9732 | 2.2924 | 0 | 0.17243 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24648 | 2.1398 |  | 0 | 0 | 2.7113 | 2.1398 | 1.2671 | 28.1264 | 0.04277 | 0 | 0.04277 | 0.0021384 | 0 | 0.0021384 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-Warehouse | VRF-New-Warehouse-GasHt | 20 | 3.8217 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 4.0964 | 0.00020333 | 0.00020187 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.0859 | 0.071848 | 0.21577 | 0 | 2.3735 | 0.39883 | 5.9513 | 2.0859 | 0.085046 | 0.21709 | 0 | 2.388 | 0.098746 | 24.1837 | 2.0859 | 0.15689 | 0.22428 | 0 | 2.4671 | 0.49757 | 2.0908 | 4.9582 | 7.1639 | 1.7737 | 14.7977 | 14.7002 | 38.4356 | 2.0859 | 0 | 0.15689 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22428 | 2.1398 |  | 0 | 0 | 2.4671 | 2.1398 | 1.153 | 31.5887 | 0.038917 | 0 | 0.038917 | 0.0019458 | 0 | 0.0019458 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-Supermarket | VRF-New-Supermarket-GasHt | 20 | 4.2 | 0 | 3 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 4.502 | 0.00022346 | 0.00022185 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | 3.2096 | 2.2924 | 0.07896 | 0.23714 | 0 | 2.6085 | 0.59824 | 4.3603 | 2.2924 | 0.093466 | 0.23859 | 0 | 2.6245 | 0.14812 | 17.7186 | 2.2924 | 0.17243 | 0.24648 | 0 | 2.7113 | 0.74636 | 5.352 | 3.6327 | 9.7779 | 2.4209 | 20.1971 | 20.064 | 52.4598 | 2.2924 | 0 | 0.17243 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24648 | 3.2096 |  | 0 | 0 | 2.7113 | 3.2096 | 0.84474 | 45.613 | 0.04277 | 0 | 0.04277 | 0.0021384 | 0 | 0.0021384 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2357 | 9999 | 0
VRF-New-MiniMart | VRF-New-MiniMart-GasHt | 20 | 4.2 | 0 | 3 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 4.502 | 0.00022346 | 0.00022185 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | 3.2096 | 2.2924 | 0.07896 | 0.23714 | 0 | 2.6085 | 0.59824 | 4.3603 | 2.2924 | 0.093466 | 0.23859 | 0 | 2.6245 | 0.14812 | 17.7186 | 2.2924 | 0.17243 | 0.24648 | 0 | 2.7113 | 0.74636 | 5.352 | 3.6327 | 9.7779 | 2.4209 | 20.1971 | 20.064 | 52.4598 | 2.2924 | 0 | 0.17243 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24648 | 3.2096 |  | 0 | 0 | 2.7113 | 3.2096 | 0.84474 | 45.613 | 0.04277 | 0 | 0.04277 | 0.0021384 | 0 | 0.0021384 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2357 | 9999 | 0
VRF-New-Restaurant | VRF-New-Restaurant-GasHt | 20 | 4.2 | 0 | 3 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 4.502 | 0.00022346 | 0.00022185 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | 3.2096 | 2.2924 | 0.07896 | 0.23714 | 0 | 2.6085 | 0.59824 | 4.3603 | 2.2924 | 0.093466 | 0.23859 | 0 | 2.6245 | 0.14812 | 17.7186 | 2.2924 | 0.17243 | 0.24648 | 0 | 2.7113 | 0.74636 | 5.352 | 3.6327 | 9.7779 | 2.4209 | 20.1971 | 20.064 | 52.4598 | 2.2924 | 0 | 0.17243 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24648 | 3.2096 |  | 0 | 0 | 2.7113 | 3.2096 | 0.84474 | 45.613 | 0.04277 | 0 | 0.04277 | 0.0021384 | 0 | 0.0021384 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2357 | 9999 | 0
VRF-New-Lodging | VRF-New-Lodging-GasHt | 20 | 3.8217 | 0 | 4 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 4.0964 | 0.00020333 | 0.00020187 | 0 | 0 | 0 | 0.79765 | 0.19749 | 1.6476 | 1.6368 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79765 | 0.19749 | 1.6476 | 1.6368 | 4.2795 | 2.0859 | 0.071848 | 0.21577 | 0 | 2.3735 | 0.79765 | 2.9756 | 2.0859 | 0.085046 | 0.21709 | 0 | 2.388 | 0.19749 | 12.0919 | 2.0859 | 0.15689 | 0.22428 | 0 | 2.4671 | 0.99515 | 11.0285 | 2.4791 | 14.3279 | 3.5474 | 29.5954 | 29.4004 | 76.8711 | 2.0859 | 0 | 0.15689 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22428 | 4.2795 |  | 0 | 0 | 2.4671 | 4.2795 | 0.57648 | 70.0243 | 0.038917 | 0 | 0.038917 | 0.0019458 | 0 | 0.0019458 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.6476 | 9999 | 0
VRF-New-Hospital | VRF-New-Hospital-GasHt | 20 | 3.8217 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 4.0964 | 0.00020333 | 0.00020187 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.0859 | 0.071848 | 0.21577 | 0 | 2.3735 | 0.39883 | 5.9513 | 2.0859 | 0.085046 | 0.21709 | 0 | 2.388 | 0.098746 | 24.1837 | 2.0859 | 0.15689 | 0.22428 | 0 | 2.4671 | 0.49757 | 2.0908 | 4.9582 | 7.1639 | 1.7737 | 14.7977 | 14.7002 | 38.4356 | 2.0859 | 0 | 0.15689 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22428 | 2.1398 |  | 0 | 0 | 2.4671 | 2.1398 | 1.153 | 31.5887 | 0.038917 | 0 | 0.038917 | 0.0019458 | 0 | 0.0019458 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-Residential Care | VRF-New-Residential Care-GasHt | 20 | 4.2 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 4.502 | 0.00022346 | 0.00022185 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.2924 | 0.07896 | 0.23714 | 0 | 2.6085 | 0.39883 | 6.5404 | 2.2924 | 0.093466 | 0.23859 | 0 | 2.6245 | 0.098746 | 26.5779 | 2.2924 | 0.17243 | 0.24648 | 0 | 2.7113 | 0.49757 | 1.2857 | 5.4491 | 6.5186 | 1.6139 | 13.4647 | 13.376 | 34.9732 | 2.2924 | 0 | 0.17243 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24648 | 2.1398 |  | 0 | 0 | 2.7113 | 2.1398 | 1.2671 | 28.1264 | 0.04277 | 0 | 0.04277 | 0.0021384 | 0 | 0.0021384 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
VRF-New-Assembly | VRF-New-Assembly-GasHt | 20 | 3.8217 | 0 | 3 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 4.0964 | 0.00020333 | 0.00020187 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59824 | 0.14812 | 1.2357 | 1.2276 | 3.2096 | 2.0859 | 0.071848 | 0.21577 | 0 | 2.3735 | 0.59824 | 3.9675 | 2.0859 | 0.085046 | 0.21709 | 0 | 2.388 | 0.14812 | 16.1225 | 2.0859 | 0.15689 | 0.22428 | 0 | 2.4671 | 0.74636 | 6.5597 | 3.3055 | 10.7459 | 2.6606 | 22.1966 | 22.0503 | 57.6533 | 2.0859 | 0 | 0.15689 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22428 | 3.2096 |  | 0 | 0 | 2.4671 | 3.2096 | 0.76864 | 50.8065 | 0.038917 | 0 | 0.038917 | 0.0019458 | 0 | 0.0019458 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2357 | 9999 | 0
VRF-New-Other | VRF-New-Other-GasHt | 20 | 3.8217 | 0 | 2 | 0 | 0 | C-All-HVAC-CAC-All-All-E |  |  | 4.0964 | 0.00020333 | 0.00020187 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | (na) | (na) | (na) | (na) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39883 | 0.098746 | 0.82381 | 0.81838 | 2.1398 | 2.0859 | 0.071848 | 0.21577 | 0 | 2.3735 | 0.39883 | 5.9513 | 2.0859 | 0.085046 | 0.21709 | 0 | 2.388 | 0.098746 | 24.1837 | 2.0859 | 0.15689 | 0.22428 | 0 | 2.4671 | 0.49757 | 2.0908 | 4.9582 | 7.1639 | 1.7737 | 14.7977 | 14.7002 | 38.4356 | 2.0859 | 0 | 0.15689 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22428 | 2.1398 |  | 0 | 0 | 2.4671 | 2.1398 | 1.153 | 31.5887 | 0.038917 | 0 | 0.038917 | 0.0019458 | 0 | 0.0019458 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.82381 | 9999 | 0
Category Results; Sorted by TRC Levelized Cost
Total Results |  | Measure Input Data | [8 empty] | Savings | [5 empty] | PV Capital |  |  |  | PV Admin |  |  |  | PV O&M |  |  |  | PV Periodic Repl. |  |  |  | Total PV Capital, O&M and Periodic Repl Costs |  |  |  |  | PV Wholesale Electric Utility Costs & Benefits | [6 empty] | PV Retail Electric Utility Costs & Benefits | [6 empty] | PV Electric Utility System Costs & Benefits | [5 empty] | Electric Utility System Economics |  | Sponsor Levelized Cost (mills/kwh) |  |  |  |  | PV Regional Costs & Benefits | [15 empty] | TRC Economics |  | Physical CO2 | [6 empty] | Gas Inputs |  |  |  | PV Gas Utility System Costs & Benefits |  |  |  |  | Gas Utility System Economics
Category | Measure | Measure Life | Site Savings (kWh) | Site Savings (therms) | Capital Cost ($/unit) | Annual O&M Cost ($/unit) | PV Per. Repl. Cost ($/unit) | Load Shape (electric) | Diversified Load Factor (electric) | Wholesale Power Coincidence Factor (electric) | Wholesale Electric Energy (kWh) | Wholesale Electric Demand (kw) | Retail Electric Demand (kW) | Wholesale Gas Energy (therms/yr) | Wholesale Gas Demand (therms/day) | Retail Gas Demand (therms/day) | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Total | Wholesale Utility System Energy | Wholesale Utility System T&D Def. Cap. | Wholesale Utility System Act C-E Credit | Wholesale Utility System Risk Mitigation Benefit | Wholesale Utility System Total System Benefit | Wholesale Utility System Total Non-Consumer Cost | Wholesale Utility System B/C Ratio | Retail Utility System Energy | Retail Utility System T&D Def. Cap. | Retail Utility System Act C-E Credit | Retail Utility System Risk Mitigation Benefit | Retail Utility System Total System Benefit | Retail Utility System Total Non-Consumer Cost | Retail Utility System System B/C Ratio | Utility System Energy | Utility System T&D Def. Cap. | Utility System Act C-E Credit | Utility System Total Risk Mitigation Benefit | Utility System Total System Benefit | Utility System Total Non-Consumer Cost | Utility System Net Levelized Cost (Net of Elec T&D Capacity Benefits, Act Credit & Risk-Mitigation Benefit) in mills/kwh | Utility System System B/C Ratio | Wholesale Electric Levelized Cost | Retail Electric Levelized Cost | Natural Gas Levelized Cost | Customer Levelized Cost | Total Levelized Cost | PV Regional Electric Energy | PV Regional Gas Energy | PV Regional Electric T&D Def. Cap. | PV Regional Gas T&D Def. Cap. | PV Regional Electric System CO2 | PV Regional Gas System CO2 | PV Regional Electric System Risk-Mitigation Benefit | PV Regional Gas System Risk-Mitigation Benefit | PV Regional Non-E Value | PV Regional Act Credit | PV Regional Capital Cost | PV Regional Admin Cost | PV Regional Annual O&M Cost | PV Regional Periodic Replacement Cost | PV Total Regional Benefit | PV Total Regional Cost | TRC B/C Ratio | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | Electric System CO2 Avoided (Lifetime Tons) | Gas System CO2 Avoided (Lifetime Tons) | Total System CO2 Avoided (Lifetime Tons) | Electric System CO2 Avoided (Annual Tons in 2018) | Gas System CO2 Avoided (Annual Tons in 2018) | Total System CO2 Avoided (Annual Tons in 2018) |  | Gas Site Savings (therms) | Load Shape (gas) | Diversitfied Load Factor (gas) | Wholesale Coincidence Factor (gas) | Total Gas Utility System Energy | Gas Utility System T&D Def. Cap. | Gas Utility System Risk Mitigation Benefit | Gas Utility System Total System Benefit | Gas Utility System Total Non-Consumer Cost | Gas Utility System Net Levelized Cost (Net of Gas T&D Capacity Benefits & Risk-Mitigation Benefits) in cents/therm | Gas Utility System System B/C Ratio
VRF-New-University |  | 20 | 9.61 | 0 | 4 | 0 | 0 |  |  |  | 10.3009 | 0.00051131 | 0.00050762 | 0 | 0 | 0 | 0.79765 | 0.19749 | 1.6476 | 1.6368 | 0.24 | 0.06 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0377 | 0.25749 | 2.1476 | 1.6368 | 5.0795 | 5.2452 | 0.18067 | 0.54259 | 0 | 5.9685 | 1.0377 | 5.7519 | 5.2452 | 0.21386 | 0.54591 | 0 | 6.005 | 0.25749 | 23.3212 | 5.2452 | 0.39453 | 0.56398 | 0 | 6.2037 | 1.2951 | 2.4047 | 4.79 | 7.4122 | 1.8393 | 15.341 | 11.6918 | 36.2843 | 5.2452 | 0 | 0.39453 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56398 | 4.2795 | 0.8 | 0 | 0 | 6.2037 | 5.0795 | 1.2213 | 29.4375 | 0.097861 | 0 | 0.097861 | 0.0048929 | 0 | 0.0048929 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1476 | 9999 | 0
VRF-New-Residential Care |  | 20 | 9.61 | 0 | 4 | 0 | 0 |  |  |  | 10.3009 | 0.00051131 | 0.00050762 | 0 | 0 | 0 | 0.79765 | 0.19749 | 1.6476 | 1.6368 | 0.24 | 0.06 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0377 | 0.25749 | 2.1476 | 1.6368 | 5.0795 | 5.2452 | 0.18067 | 0.54259 | 0 | 5.9685 | 1.0377 | 5.7519 | 5.2452 | 0.21386 | 0.54591 | 0 | 6.005 | 0.25749 | 23.3212 | 5.2452 | 0.39453 | 0.56398 | 0 | 6.2037 | 1.2951 | 2.4047 | 4.79 | 7.4122 | 1.8393 | 15.341 | 11.6918 | 36.2843 | 5.2452 | 0 | 0.39453 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56398 | 4.2795 | 0.8 | 0 | 0 | 6.2037 | 5.0795 | 1.2213 | 29.4375 | 0.097861 | 0 | 0.097861 | 0.0048929 | 0 | 0.0048929 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1476 | 9999 | 0
VRF-New-Large Off |  | 20 | 9.0217 | 0 | 4 | 0 | 0 |  |  |  | 9.6703 | 0.00048 | 0.00047654 | 0 | 0 | 0 | 0.79765 | 0.19749 | 1.6476 | 1.6368 | 0.24 | 0.06 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0377 | 0.25749 | 2.1476 | 1.6368 | 5.0795 | 4.9241 | 0.16961 | 0.50937 | 0 | 5.6031 | 1.0377 | 5.3998 | 4.9241 | 0.20077 | 0.51249 | 0 | 5.6374 | 0.25749 | 21.8934 | 4.9241 | 0.37037 | 0.52945 | 0 | 5.8239 | 1.2951 | 3.008 | 4.4967 | 7.8956 | 1.9593 | 16.3414 | 12.4543 | 38.6506 | 4.9241 | 0 | 0.37037 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52945 | 4.2795 | 0.8 | 0 | 0 | 5.8239 | 5.0795 | 1.1465 | 31.8038 | 0.09187 | 0 | 0.09187 | 0.0045934 | 0 | 0.0045934 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1476 | 9999 | 0
VRF-New-Medium Off |  | 20 | 9.0217 | 0 | 4 | 0 | 0 |  |  |  | 9.6703 | 0.00048 | 0.00047654 | 0 | 0 | 0 | 0.79765 | 0.19749 | 1.6476 | 1.6368 | 0.24 | 0.06 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0377 | 0.25749 | 2.1476 | 1.6368 | 5.0795 | 4.9241 | 0.16961 | 0.50937 | 0 | 5.6031 | 1.0377 | 5.3998 | 4.9241 | 0.20077 | 0.51249 | 0 | 5.6374 | 0.25749 | 21.8934 | 4.9241 | 0.37037 | 0.52945 | 0 | 5.8239 | 1.2951 | 3.008 | 4.4967 | 7.8956 | 1.9593 | 16.3414 | 12.4543 | 38.6506 | 4.9241 | 0 | 0.37037 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52945 | 4.2795 | 0.8 | 0 | 0 | 5.8239 | 5.0795 | 1.1465 | 31.8038 | 0.09187 | 0 | 0.09187 | 0.0045934 | 0 | 0.0045934 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1476 | 9999 | 0
VRF-New-Xlarge Ret |  | 20 | 9.0217 | 0 | 4 | 0 | 0 |  |  |  | 9.6703 | 0.00048 | 0.00047654 | 0 | 0 | 0 | 0.79765 | 0.19749 | 1.6476 | 1.6368 | 0.24 | 0.06 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0377 | 0.25749 | 2.1476 | 1.6368 | 5.0795 | 4.9241 | 0.16961 | 0.50937 | 0 | 5.6031 | 1.0377 | 5.3998 | 4.9241 | 0.20077 | 0.51249 | 0 | 5.6374 | 0.25749 | 21.8934 | 4.9241 | 0.37037 | 0.52945 | 0 | 5.8239 | 1.2951 | 3.008 | 4.4967 | 7.8956 | 1.9593 | 16.3414 | 12.4543 | 38.6506 | 4.9241 | 0 | 0.37037 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52945 | 4.2795 | 0.8 | 0 | 0 | 5.8239 | 5.0795 | 1.1465 | 31.8038 | 0.09187 | 0 | 0.09187 | 0.0045934 | 0 | 0.0045934 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1476 | 9999 | 0
VRF-New-Large Ret |  | 20 | 9.0217 | 0 | 4 | 0 | 0 |  |  |  | 9.6703 | 0.00048 | 0.00047654 | 0 | 0 | 0 | 0.79765 | 0.19749 | 1.6476 | 1.6368 | 0.24 | 0.06 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0377 | 0.25749 | 2.1476 | 1.6368 | 5.0795 | 4.9241 | 0.16961 | 0.50937 | 0 | 5.6031 | 1.0377 | 5.3998 | 4.9241 | 0.20077 | 0.51249 | 0 | 5.6374 | 0.25749 | 21.8934 | 4.9241 | 0.37037 | 0.52945 | 0 | 5.8239 | 1.2951 | 3.008 | 4.4967 | 7.8956 | 1.9593 | 16.3414 | 12.4543 | 38.6506 | 4.9241 | 0 | 0.37037 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52945 | 4.2795 | 0.8 | 0 | 0 | 5.8239 | 5.0795 | 1.1465 | 31.8038 | 0.09187 | 0 | 0.09187 | 0.0045934 | 0 | 0.0045934 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1476 | 9999 | 0
VRF-New-Medium Ret |  | 20 | 9.0217 | 0 | 4 | 0 | 0 |  |  |  | 9.6703 | 0.00048 | 0.00047654 | 0 | 0 | 0 | 0.79765 | 0.19749 | 1.6476 | 1.6368 | 0.24 | 0.06 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0377 | 0.25749 | 2.1476 | 1.6368 | 5.0795 | 4.9241 | 0.16961 | 0.50937 | 0 | 5.6031 | 1.0377 | 5.3998 | 4.9241 | 0.20077 | 0.51249 | 0 | 5.6374 | 0.25749 | 21.8934 | 4.9241 | 0.37037 | 0.52945 | 0 | 5.8239 | 1.2951 | 3.008 | 4.4967 | 7.8956 | 1.9593 | 16.3414 | 12.4543 | 38.6506 | 4.9241 | 0 | 0.37037 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52945 | 4.2795 | 0.8 | 0 | 0 | 5.8239 | 5.0795 | 1.1465 | 31.8038 | 0.09187 | 0 | 0.09187 | 0.0045934 | 0 | 0.0045934 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1476 | 9999 | 0
VRF-New-Small Ret |  | 20 | 9.0217 | 0 | 4 | 0 | 0 |  |  |  | 9.6703 | 0.00048 | 0.00047654 | 0 | 0 | 0 | 0.79765 | 0.19749 | 1.6476 | 1.6368 | 0.24 | 0.06 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0377 | 0.25749 | 2.1476 | 1.6368 | 5.0795 | 4.9241 | 0.16961 | 0.50937 | 0 | 5.6031 | 1.0377 | 5.3998 | 4.9241 | 0.20077 | 0.51249 | 0 | 5.6374 | 0.25749 | 21.8934 | 4.9241 | 0.37037 | 0.52945 | 0 | 5.8239 | 1.2951 | 3.008 | 4.4967 | 7.8956 | 1.9593 | 16.3414 | 12.4543 | 38.6506 | 4.9241 | 0 | 0.37037 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52945 | 4.2795 | 0.8 | 0 | 0 | 5.8239 | 5.0795 | 1.1465 | 31.8038 | 0.09187 | 0 | 0.09187 | 0.0045934 | 0 | 0.0045934 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1476 | 9999 | 0
VRF-New-School K-12 |  | 20 | 9.0217 | 0 | 4 | 0 | 0 |  |  |  | 9.6703 | 0.00048 | 0.00047654 | 0 | 0 | 0 | 0.79765 | 0.19749 | 1.6476 | 1.6368 | 0.24 | 0.06 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0377 | 0.25749 | 2.1476 | 1.6368 | 5.0795 | 4.9241 | 0.16961 | 0.50937 | 0 | 5.6031 | 1.0377 | 5.3998 | 4.9241 | 0.20077 | 0.51249 | 0 | 5.6374 | 0.25749 | 21.8934 | 4.9241 | 0.37037 | 0.52945 | 0 | 5.8239 | 1.2951 | 3.008 | 4.4967 | 7.8956 | 1.9593 | 16.3414 | 12.4543 | 38.6506 | 4.9241 | 0 | 0.37037 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52945 | 4.2795 | 0.8 | 0 | 0 | 5.8239 | 5.0795 | 1.1465 | 31.8038 | 0.09187 | 0 | 0.09187 | 0.0045934 | 0 | 0.0045934 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1476 | 9999 | 0
VRF-New-Warehouse |  | 20 | 9.0217 | 0 | 4 | 0 | 0 |  |  |  | 9.6703 | 0.00048 | 0.00047654 | 0 | 0 | 0 | 0.79765 | 0.19749 | 1.6476 | 1.6368 | 0.24 | 0.06 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0377 | 0.25749 | 2.1476 | 1.6368 | 5.0795 | 4.9241 | 0.16961 | 0.50937 | 0 | 5.6031 | 1.0377 | 5.3998 | 4.9241 | 0.20077 | 0.51249 | 0 | 5.6374 | 0.25749 | 21.8934 | 4.9241 | 0.37037 | 0.52945 | 0 | 5.8239 | 1.2951 | 3.008 | 4.4967 | 7.8956 | 1.9593 | 16.3414 | 12.4543 | 38.6506 | 4.9241 | 0 | 0.37037 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52945 | 4.2795 | 0.8 | 0 | 0 | 5.8239 | 5.0795 | 1.1465 | 31.8038 | 0.09187 | 0 | 0.09187 | 0.0045934 | 0 | 0.0045934 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1476 | 9999 | 0
VRF-New-Hospital |  | 20 | 9.0217 | 0 | 4 | 0 | 0 |  |  |  | 9.6703 | 0.00048 | 0.00047654 | 0 | 0 | 0 | 0.79765 | 0.19749 | 1.6476 | 1.6368 | 0.24 | 0.06 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0377 | 0.25749 | 2.1476 | 1.6368 | 5.0795 | 4.9241 | 0.16961 | 0.50937 | 0 | 5.6031 | 1.0377 | 5.3998 | 4.9241 | 0.20077 | 0.51249 | 0 | 5.6374 | 0.25749 | 21.8934 | 4.9241 | 0.37037 | 0.52945 | 0 | 5.8239 | 1.2951 | 3.008 | 4.4967 | 7.8956 | 1.9593 | 16.3414 | 12.4543 | 38.6506 | 4.9241 | 0 | 0.37037 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52945 | 4.2795 | 0.8 | 0 | 0 | 5.8239 | 5.0795 | 1.1465 | 31.8038 | 0.09187 | 0 | 0.09187 | 0.0045934 | 0 | 0.0045934 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1476 | 9999 | 0
VRF-New-Other |  | 20 | 9.0217 | 0 | 4 | 0 | 0 |  |  |  | 9.6703 | 0.00048 | 0.00047654 | 0 | 0 | 0 | 0.79765 | 0.19749 | 1.6476 | 1.6368 | 0.24 | 0.06 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0377 | 0.25749 | 2.1476 | 1.6368 | 5.0795 | 4.9241 | 0.16961 | 0.50937 | 0 | 5.6031 | 1.0377 | 5.3998 | 4.9241 | 0.20077 | 0.51249 | 0 | 5.6374 | 0.25749 | 21.8934 | 4.9241 | 0.37037 | 0.52945 | 0 | 5.8239 | 1.2951 | 3.008 | 4.4967 | 7.8956 | 1.9593 | 16.3414 | 12.4543 | 38.6506 | 4.9241 | 0 | 0.37037 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52945 | 4.2795 | 0.8 | 0 | 0 | 5.8239 | 5.0795 | 1.1465 | 31.8038 | 0.09187 | 0 | 0.09187 | 0.0045934 | 0 | 0.0045934 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1476 | 9999 | 0
VRF-New-Small Off |  | 20 | 9.61 | 0 | 6 | 0 | 0 |  |  |  | 10.3009 | 0.00051131 | 0.00050762 | 0 | 0 | 0 | 1.1965 | 0.29624 | 2.4714 | 2.4551 | 0.36 | 0.09 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5565 | 0.38624 | 3.2214 | 2.4551 | 7.6193 | 5.2452 | 0.18067 | 0.54259 | 0 | 5.9685 | 1.5565 | 3.8346 | 5.2452 | 0.21386 | 0.54591 | 0 | 6.005 | 0.38624 | 15.5474 | 5.2452 | 0.39453 | 0.56398 | 0 | 6.2037 | 1.9427 | 7.0305 | 3.1933 | 11.1183 | 2.759 | 23.0115 | 17.5377 | 54.4265 | 5.2452 | 0 | 0.39453 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56398 | 6.4193 | 1.2 | 0 | 0 | 6.2037 | 7.6193 | 0.81421 | 47.5796 | 0.097861 | 0 | 0.097861 | 0.0048929 | 0 | 0.0048929 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 3.2214 | 9999 | 0
VRF-New-Supermarket |  | 20 | 9.61 | 0 | 6 | 0 | 0 |  |  |  | 10.3009 | 0.00051131 | 0.00050762 | 0 | 0 | 0 | 1.1965 | 0.29624 | 2.4714 | 2.4551 | 0.36 | 0.09 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5565 | 0.38624 | 3.2214 | 2.4551 | 7.6193 | 5.2452 | 0.18067 | 0.54259 | 0 | 5.9685 | 1.5565 | 3.8346 | 5.2452 | 0.21386 | 0.54591 | 0 | 6.005 | 0.38624 | 15.5474 | 5.2452 | 0.39453 | 0.56398 | 0 | 6.2037 | 1.9427 | 7.0305 | 3.1933 | 11.1183 | 2.759 | 23.0115 | 17.5377 | 54.4265 | 5.2452 | 0 | 0.39453 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56398 | 6.4193 | 1.2 | 0 | 0 | 6.2037 | 7.6193 | 0.81421 | 47.5796 | 0.097861 | 0 | 0.097861 | 0.0048929 | 0 | 0.0048929 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 3.2214 | 9999 | 0
VRF-New-MiniMart |  | 20 | 9.61 | 0 | 6 | 0 | 0 |  |  |  | 10.3009 | 0.00051131 | 0.00050762 | 0 | 0 | 0 | 1.1965 | 0.29624 | 2.4714 | 2.4551 | 0.36 | 0.09 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5565 | 0.38624 | 3.2214 | 2.4551 | 7.6193 | 5.2452 | 0.18067 | 0.54259 | 0 | 5.9685 | 1.5565 | 3.8346 | 5.2452 | 0.21386 | 0.54591 | 0 | 6.005 | 0.38624 | 15.5474 | 5.2452 | 0.39453 | 0.56398 | 0 | 6.2037 | 1.9427 | 7.0305 | 3.1933 | 11.1183 | 2.759 | 23.0115 | 17.5377 | 54.4265 | 5.2452 | 0 | 0.39453 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56398 | 6.4193 | 1.2 | 0 | 0 | 6.2037 | 7.6193 | 0.81421 | 47.5796 | 0.097861 | 0 | 0.097861 | 0.0048929 | 0 | 0.0048929 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 3.2214 | 9999 | 0
VRF-New-Restaurant |  | 20 | 9.61 | 0 | 6 | 0 | 0 |  |  |  | 10.3009 | 0.00051131 | 0.00050762 | 0 | 0 | 0 | 1.1965 | 0.29624 | 2.4714 | 2.4551 | 0.36 | 0.09 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5565 | 0.38624 | 3.2214 | 2.4551 | 7.6193 | 5.2452 | 0.18067 | 0.54259 | 0 | 5.9685 | 1.5565 | 3.8346 | 5.2452 | 0.21386 | 0.54591 | 0 | 6.005 | 0.38624 | 15.5474 | 5.2452 | 0.39453 | 0.56398 | 0 | 6.2037 | 1.9427 | 7.0305 | 3.1933 | 11.1183 | 2.759 | 23.0115 | 17.5377 | 54.4265 | 5.2452 | 0 | 0.39453 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56398 | 6.4193 | 1.2 | 0 | 0 | 6.2037 | 7.6193 | 0.81421 | 47.5796 | 0.097861 | 0 | 0.097861 | 0.0048929 | 0 | 0.0048929 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 3.2214 | 9999 | 0
VRF-New-Assembly |  | 20 | 9.0217 | 0 | 6 | 0 | 0 |  |  |  | 9.6703 | 0.00048 | 0.00047654 | 0 | 0 | 0 | 1.1965 | 0.29624 | 2.4714 | 2.4551 | 0.36 | 0.09 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5565 | 0.38624 | 3.2214 | 2.4551 | 7.6193 | 4.9241 | 0.16961 | 0.50937 | 0 | 5.6031 | 1.5565 | 3.5999 | 4.9241 | 0.20077 | 0.51249 | 0 | 5.6374 | 0.38624 | 14.5956 | 4.9241 | 0.37037 | 0.52945 | 0 | 5.8239 | 1.9427 | 7.9355 | 2.9978 | 11.8434 | 2.9389 | 24.5122 | 18.6814 | 57.9759 | 4.9241 | 0 | 0.37037 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52945 | 6.4193 | 1.2 | 0 | 0 | 5.8239 | 7.6193 | 0.76437 | 51.129 | 0.09187 | 0 | 0.09187 | 0.0045934 | 0 | 0.0045934 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 3.2214 | 9999 | 0
VRF-New-Lodging |  | 20 | 9.0217 | 0 | 8 | 0 | 0 |  |  |  | 9.6703 | 0.00048 | 0.00047654 | 0 | 0 | 0 | 1.5953 | 0.39498 | 3.2952 | 3.2735 | 0.48 | 0.12 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0753 | 0.51498 | 4.2952 | 3.2735 | 10.1591 | 4.9241 | 0.16961 | 0.50937 | 0 | 5.6031 | 2.0753 | 2.6999 | 4.9241 | 0.20077 | 0.51249 | 0 | 5.6374 | 0.51498 | 10.9467 | 4.9241 | 0.37037 | 0.52945 | 0 | 5.8239 | 2.5903 | 12.8629 | 2.2484 | 15.7912 | 3.9186 | 32.6829 | 24.9085 | 77.3012 | 4.9241 | 0 | 0.37037 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52945 | 8.5591 | 1.6 | 0 | 0 | 5.8239 | 10.1591 | 0.57327 | 70.4543 | 0.09187 | 0 | 0.09187 | 0.0045934 | 0 | 0.0045934 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 4.2952 | 9999 | 0
Supply Curve Results; Categories sorted by TRC Net Levelized Cost
Totals for Categories with Benefits Exceeding Costs. Levelized cost is TRC Net Levelized Cost (Net of Benefits) | [12 empty] | Savings Allocation by Cost Bin and Month for Segments 1 | [12 empty] | Savings Allocation by Cost Bin and Month for Segments 2
| Totals Basis | Busbar Electric Savings in kWh | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Measures with B/C > 1.00 | 146.074 | 63 | 0 | 63 | 67.4026 | 87.9735 | 3778.086 | 1.0484 | 27.1059 | 1.3423 | 1.3877 | 2.4284 | 1.7806 | 3.2294 | 3.1313 | 7.2344 | 12.5142 | 22.8527 | 24.9555 | 11.7373 | 5.3744 | 2.4101 | 2.0244 |  | 2.4036 | 1.7825 | 2.4637 | 2.4644 | 4.3282 | 4.7337 | 8.3131 | 6.5479 | 5.6176 | 3.1663 | 2.4043 | 2.176
| Categories with B/C > 1.00 | 117.3043 | 48 | 9.6 | 57.6 | 60.9544 | 70.6469 | 4301.4265 | 2.9021 | 31.3882 | 1.1597 | 1.1144 | 0.32153 | 0.23576 | 0.42758 | 0.41459 | 0.95785 | 1.6569 | 3.0257 | 3.3042 | 1.554 | 0.71159 | 0.3191 | 0.26803 |  | 0.31824 | 0.23601 | 0.32619 | 0.32629 | 0.57307 | 0.62675 | 1.1007 | 0.86696 | 0.74378 | 0.41923 | 0.31834 | 0.2881
Supply Curve Results: By TRC Net Levelized Cost - Net of Benefits
| Block 1: <= 0 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 2: <= 10 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 3: 10-20 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 4: 20-30 mills/kWh | 20.6018 | 8 | 1.6 | 9.6 | 10.1591 | 12.4075 | 4081.9747 | 2.4047 | 29.4375 | 1.2213 | 0.19572 | 0.3425 | 0.25113 | 0.45546 | 0.44163 | 1.0203 | 1.765 | 3.2231 | 3.5196 | 1.6554 | 0.75799 | 0.33991 | 0.28551 |  | 0.339 | 0.2514 | 0.34747 | 0.34757 | 0.61044 | 0.66763 | 1.1725 | 0.92349 | 0.79229 | 0.44657 | 0.3391 | 0.30689
| Block 5: 30-40 mills/kWh | 96.7025 | 40 | 8 | 48 | 50.7953 | 58.2394 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.9187 | 1.6077 | 1.1788 | 2.1379 | 2.073 | 4.7892 | 8.2845 | 15.1287 | 16.5208 | 7.7702 | 3.5579 | 1.5955 | 1.3402 |  | 1.5912 | 1.1801 | 1.631 | 1.6314 | 2.8653 | 3.1338 | 5.5034 | 4.3348 | 3.7189 | 2.0961 | 1.5917 | 1.4405
| Block 6: 40-50 mills/kWh | 41.2036 | 24 | 4.8 | 28.8 | 30.4772 | 24.815 | 6122.962 | 7.0305 | 47.5796 | 0.81421 | 0.39144 | 0.685 | 0.50227 | 0.91092 | 0.88326 | 2.0406 | 3.5299 | 6.4461 | 7.0393 | 3.3108 | 1.516 | 0.67982 | 0.57102 |  | 0.67799 | 0.5028 | 0.69493 | 0.69513 | 1.2209 | 1.3353 | 2.3449 | 1.847 | 1.5846 | 0.89314 | 0.67819 | 0.61379
| Block 7: 50-60 mills/kWh | 9.6703 | 6 | 1.2 | 7.2 | 7.6193 | 5.8239 | 6522.2687 | 7.9355 | 51.129 | 0.76437 | 0.09187 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 |  | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
| Block 8: 60-70 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 9: 70-80 mills/kWh | 9.6703 | 8 | 1.6 | 9.6 | 10.1591 | 5.8239 | 8696.3583 | 12.8629 | 70.4543 | 0.57327 | 0.09187 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 |  | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
| Block 10: 80-90 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 11: 90-100 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 12: 100-110 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 13: 110-120 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 14: 120-130 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 15: 130-140 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 16: 140-150 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 17: 150-160 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 18: 160-170 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 19: 170-180 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 20: 180-190 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 21: 190-200 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 22: > 200 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Shaped Savings Results; By Category and sorted by TRC BC ratio
[13 empty] | Savings Allocation by Cost Bin and Month for Segments 1 Feb: Savings Allocation by Category and Month for Segments 1 |  |  | Savings Allocation by Category and Month for Segments 2
Category | Measure | Busbar Savings | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Wholesale KW | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
VRF-New-University |  | 10.3009 | 4 | 0.8 | 4.8 | 5.0795 | 6.2037 | 4081.9747 | 2.4047 | 29.4375 | 1.2213 | 0.097861 | 0.00051131 | 0.17125 | 0.12557 | 0.22773 | 0.22081 | 0.51016 | 0.88248 | 1.6115 | 1.7598 | 0.8277 | 0.379 | 0.16996 | 0.14276 |  | 0.1695 | 0.1257 | 0.17373 | 0.17378 | 0.30522 | 0.33381 | 0.58623 | 0.46175 | 0.39614 | 0.22328 | 0.16955 | 0.15345
VRF-New-Residential Care |  | 10.3009 | 4 | 0.8 | 4.8 | 5.0795 | 6.2037 | 4081.9747 | 2.4047 | 29.4375 | 1.2213 | 0.097861 | 0.00051131 | 0.17125 | 0.12557 | 0.22773 | 0.22081 | 0.51016 | 0.88248 | 1.6115 | 1.7598 | 0.8277 | 0.379 | 0.16996 | 0.14276 |  | 0.1695 | 0.1257 | 0.17373 | 0.17378 | 0.30522 | 0.33381 | 0.58623 | 0.46175 | 0.39614 | 0.22328 | 0.16955 | 0.15345
VRF-New-Large Off |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 |  | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Medium Off |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 |  | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Xlarge Ret |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 |  | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Large Ret |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 |  | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Medium Ret |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 |  | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Small Ret |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 |  | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-School K-12 |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 |  | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Warehouse |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 |  | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Hospital |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 |  | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Other |  | 9.6703 | 4 | 0.8 | 4.8 | 5.0795 | 5.8239 | 4348.1792 | 3.008 | 31.8038 | 1.1465 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 |  | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Small Off |  | 10.3009 | 6 | 1.2 | 7.2 | 7.6193 | 6.2037 | 6122.962 | 7.0305 | 47.5796 | 0.81421 | 0.097861 | 0.00051131 | 0.17125 | 0.12557 | 0.22773 | 0.22081 | 0.51016 | 0.88248 | 1.6115 | 1.7598 | 0.8277 | 0.379 | 0.16996 | 0.14276 |  | 0.1695 | 0.1257 | 0.17373 | 0.17378 | 0.30522 | 0.33381 | 0.58623 | 0.46175 | 0.39614 | 0.22328 | 0.16955 | 0.15345
VRF-New-Supermarket |  | 10.3009 | 6 | 1.2 | 7.2 | 7.6193 | 6.2037 | 6122.962 | 7.0305 | 47.5796 | 0.81421 | 0.097861 | 0.00051131 | 0.17125 | 0.12557 | 0.22773 | 0.22081 | 0.51016 | 0.88248 | 1.6115 | 1.7598 | 0.8277 | 0.379 | 0.16996 | 0.14276 |  | 0.1695 | 0.1257 | 0.17373 | 0.17378 | 0.30522 | 0.33381 | 0.58623 | 0.46175 | 0.39614 | 0.22328 | 0.16955 | 0.15345
VRF-New-MiniMart |  | 10.3009 | 6 | 1.2 | 7.2 | 7.6193 | 6.2037 | 6122.962 | 7.0305 | 47.5796 | 0.81421 | 0.097861 | 0.00051131 | 0.17125 | 0.12557 | 0.22773 | 0.22081 | 0.51016 | 0.88248 | 1.6115 | 1.7598 | 0.8277 | 0.379 | 0.16996 | 0.14276 |  | 0.1695 | 0.1257 | 0.17373 | 0.17378 | 0.30522 | 0.33381 | 0.58623 | 0.46175 | 0.39614 | 0.22328 | 0.16955 | 0.15345
VRF-New-Restaurant |  | 10.3009 | 6 | 1.2 | 7.2 | 7.6193 | 6.2037 | 6122.962 | 7.0305 | 47.5796 | 0.81421 | 0.097861 | 0.00051131 | 0.17125 | 0.12557 | 0.22773 | 0.22081 | 0.51016 | 0.88248 | 1.6115 | 1.7598 | 0.8277 | 0.379 | 0.16996 | 0.14276 |  | 0.1695 | 0.1257 | 0.17373 | 0.17378 | 0.30522 | 0.33381 | 0.58623 | 0.46175 | 0.39614 | 0.22328 | 0.16955 | 0.15345
VRF-New-Assembly |  | 9.6703 | 6 | 1.2 | 7.2 | 7.6193 | 5.8239 | 6522.2687 | 7.9355 | 51.129 | 0.76437 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 |  | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
VRF-New-Lodging |  | 9.6703 | 8 | 1.6 | 9.6 | 10.1591 | 5.8239 | 8696.3583 | 12.8629 | 70.4543 | 0.57327 | 0.09187 | 0.00048 | 0.16077 | 0.11788 | 0.21379 | 0.2073 | 0.47892 | 0.82845 | 1.5129 | 1.6521 | 0.77702 | 0.35579 | 0.15955 | 0.13402 |  | 0.15912 | 0.11801 | 0.1631 | 0.16314 | 0.28653 | 0.31338 | 0.55034 | 0.43348 | 0.37189 | 0.20961 | 0.15917 | 0.14405
Note on I6: :ProCost Perioodic replacement costs and savinsg of the measure. These are costs and savings that occur periodicially, but at different periods than annually. Can be positive or negative. Periodic replacement costs for both the measure and the baseline measure should be included if applicable. ProCost can analysze these costs in two ways dependent on the 'Repeat Periodic Replacemetn' switch in the ProData page. When set to 'On', ProCost repeats replacement costs for multiple times over the life of a measure depending on the input period and measure life. For example fluorescent lamps may have a 4-year replacement cycle that repeats 3 times in a 15-year measure life. When set to 'Off', ProCost reads the period as the year after installation that the replacement cost occurs and does not subsequently reinstall or repeat the replacement costs. For example a compressor may be replaced only once in the life of a heat-pump system. Example: A new fluorescent lighting systems may have a measure life of 15 years, and a lamp life of five years. Two lamps lamps per fixture must be replaced at years 6 and 11. Lamp and labor costs, expressed as positive costs, are entered as a cost and the period would be enetered as 5. The baseline measure may have a four year lamp life and would have required a three-lamp replacement at years 5, 9 and 13. Lamp and labor replacement costs would be entered as annual savings in dollars with a 4-year period. ProCost determines the net present value of the two cost streams.
Note on O6: :ProCost If the measure has gas savings for incfreases, enter the annual savings and shape of the savings here. Example: Clothes washer saves electric motor and dryer energy and gas water heat.
Note on A7: :Procost Category for the measure. Individual measures can be grouped into categories. Procost output is reported by measure and by category. All measures must belong to at least one category. Category name can be the same as measure name. Example: Measures can be combined into one category if they have components with different load shapes or measure lives. On wash machines there may be one load shape for the electric motor savings component, a second load shape for the electric water heat savings component and a third shape for electric dryer savings component.
Note on B7: :ProCost Name of Measure. User-defined. For PTR measures, defined naming conventions apply.
Note on C7: :ProCost Annual electric savings for the measure in kWh at the site. May be positive, negative or zero. Savings are incremental to the baseline alternative.
Note on D7: :ProCost Physical life of the measure in years. Must be >=1.
Note on E7: :ProCost Initial cost to install the measure in dollars. Costs are incremental to the baseline alternative. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on F7: :ProCost Annaul opperations and maintenace cost for the measure in dollars. Must be incremental cost over the baseline alternative. May be positive, negative or zero. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page. O&M costs are enetered as positive values. Negative values represent O&M savings compared to the baseline alternative. Example: Annualized maintenace cost for a heat pump heating system compared to a baseline electric resistance heating system.
Note on G7: :ProCost Name of the pointer to the shape of the savings. The shapes represent the daily and monthly shape of the savings in four time segments for each month of the year. Shape of the savings is relative to the baseline alternative. These shaps are in the MC_AND_Loadshape file.
Note on H7: :ProCost Annual value of any non-energy benefits of the measure, relative to the baseline alternative. Expressed in dollars per year and denominated in dollars of the 'Cost Reference Year'. Positive value represents dollar savings. Negative value represents dollar cost. Example: Water, detergent and sewer savings from efficient clothes washer.
Note on I7: : Cost in dollars that is incurred for Period 1. Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on J7: :ProCost Duration of Period1. The time at which Period 1 costs, or savings, occur. In years.
Note on K7: : Cost in dollars that is incurred for Period 2 Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on L7: :ProCost Duration of Period 2. The time at which Period 2 costs, or savings, occur. In years.
Note on M7: : Cost in dollars that is incurred for Period 3. Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on N7: :ProCost Duration of Period 3. The time at which Period 3 costs, or savings, occur. In years.
Note on O7: : Annual gas savings, or increases, in therms.
Note on P7: :ProCost Name of the pointer to the shape of the savings. The shapes represent the daily and monthly shape of the savings in four time segments for each month of the year. Shape of the savings is relative to the baseline alternative. These shaps are in the MC_AND_Loadshape file.
Note on BH70: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BM70: Direct and program administrative costs of the measure to sponsor. Separate costs for each sponsor. Depends on share of costs incurred by sponsor, sponsor cost of capital, and financing term which are user-defined inputs. Includes applicable Capital, O&M, Periodic Replacement and Program Administrative costs. Sponsor costs are levelized over program life. Does not include any adjustments for benefit. NOTE: Units are per kWh for 'Electric' runs and per therm for 'Gas' runs for all sponsors.
Note on CE70: All costs minus all benefits regardless of which sponsor incurs the cost or accrues the benefits. TRC Net Levelized Cost includes all applicable costs and all benefits. In addition to energy system costs and benefits, TRC Net Levelized Cost includes non-energy, other-fuel, O&M, periodic-replacement and risk-mitigation benefits and costs. TRC Net Levelized Cost corresponds to TRC B/C ratios with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure. The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the TRC B/C ratio and the TRC Net Levelized Cost. If Risk-Mitigation credit is non-zero, TRC Levelized Cost will be reduced by the risk-mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on CW70: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BH111: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on BM111: Direct and program administrative costs of the measure to sponsor. Separate costs for each sponsor. Depends on share of costs incurred by sponsor, sponsor cost of capital, and financing term which are user-defined inputs. Includes applicable Capital, O&M, Periodic Replacement and Program Administrative costs. Sponsor costs are levelized over program life. Does not include any adjustments for benefit. NOTE: Units are per kWh for 'Electric' runs and per therm for 'Gas' runs for all sponsors.
Note on CE111: All costs minus all benefits regardless of which sponsor incurs the cost or accrues the benefits. TRC Net Levelized Cost includes all applicable costs and all benefits. In addition to energy system costs and benefits, TRC Net Levelized Cost includes non-energy, other-fuel, O&M, periodic-replacement and risk-mitigation benefits and costs. TRC Net Levelized Cost corresponds to TRC B/C ratios with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure. The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the TRC B/C ratio and the TRC Net Levelized Cost. If Risk-Mitigation credit is non-zero, TRC Levelized Cost will be reduced by the risk-mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on CW111: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.

## MMap
Measure Map
therm = 100,000 Btu
therm = 100 kbtu
| VRF | [8 empty] | 20
[11 empty] | GasHt%TYP | ElecHt%TYP | HtPmpHt%TYP | raw | raw | 0.15501 | CoolSat%TYP
Measure Name | Base Measure Name | Measure Index Name | Category1 | BType | MOPP | End Use | Heat Fuel | Cooling System Type | Shape Pointer | Life | Gas Heat Shares | Electric Heat Shares | HtPmpHt | RAW Savings (kWh/yr.) | RAW Capital Cost ($) | Cost Premium for Retrofit | COOLING SATURATION | Btype IDX | WT Savings by Fuel Type | WT Cost by Fuel Type | Wt Gas Savings (Therms) | Retrofit Adjustment | SAVELOOKUP
VRF-New-Large Off | VRF | VRF-New | VRF-New-Large Off-ElecHt | Large Off | New | HVAC | ElecHt |  |  | 20 | 54.04% | 20.94% | 25.02% | 5.2 | 3.68 | 1 | 76.89% | 2 | 1.0891 | 0.77071 | 0 | 1 | Large Off - New | Costs
VRF-New-Medium Off | VRF | VRF-New | VRF-New-Medium Off-ElecHt | Medium Off | New | HVAC | ElecHt |  |  | 20 | 51.43% | 22.13% | 26.44% | 2.83 | 2.29 | 1 | 91.57% | 3 | 0.62631 | 0.5068 | 0 | 1 | Medium Off - New
VRF-New-Small Off | VRF | VRF-New | VRF-New-Small Off-ElecHt | Small Off | New | HVAC | ElecHt |  |  | 20 | 32.75% | 30.64% | 36.6% | 5.2 | 2.29 | 1 | 85.58% | 4 | 1.5933 | 0.70168 | 0 | 1 | Small Off - New
VRF-New-Xlarge Ret | VRF | VRF-New | VRF-New-Xlarge Ret-ElecHt | Xlarge Ret | New | HVAC | ElecHt |  |  | 20 | 91.61% | 5.3% | 3.094% | 2.94 | 2.6667 | 1 | 95.16% | 5 | 0.15581 | 0.14132 | 0 | 1 | Xlarge Ret - New
VRF-New-Large Ret | VRF | VRF-New | VRF-New-Large Ret-ElecHt | Large Ret | New | HVAC | ElecHt |  |  | 20 | 98.32% | 1.059% | 0.6184% | 2.94 | 2.6667 | 1 | 98.53% | 6 | 0.031144 | 0.028248 | 0 | 1 | Large Ret - New
VRF-New-Medium Ret | VRF | VRF-New | VRF-New-Medium Ret-ElecHt | Medium Ret | New | HVAC | ElecHt |  |  | 20 | 80.99% | 12.01% | 7.009% | 2.94 | 2.6667 | 1 | 65.23% | 7 | 0.35298 | 0.32017 | 0 | 1 | Medium Ret - New
VRF-New-Small Ret | VRF | VRF-New | VRF-New-Small Ret-ElecHt | Small Ret | New | HVAC | ElecHt |  |  | 20 | 56.72% | 27.33% | 15.95% | 2.94 | 2.6667 | 1 | 66.01% | 8 | 0.80348 | 0.72878 | 0 | 1 | Small Ret - New
VRF-New-School K-12 | VRF | VRF-New | VRF-New-School K-12-ElecHt | School K-12 | New | HVAC | ElecHt |  |  | 20 | 84.78% | 5.837% | 9.385% | 2.94 | 2.6667 | 1 | 69.62% | 9 | 0.17161 | 0.15565 | 0 | 1 | School K-12 - New
VRF-New-University | VRF | VRF-New | VRF-New-University-ElecHt | University | New | HVAC | ElecHt |  |  | 20 | 80% | 10% | 10% | 2.94 | 2.6667 | 1 | 75% | 10 | 0.294 | 0.26667 | 0 | 1 | University - New
VRF-New-Warehouse | VRF | VRF-New | VRF-New-Warehouse-ElecHt | Warehouse | New | HVAC | ElecHt |  |  | 20 | 98.7% | 0.6393% | 0.6603% | 2.94 | 2.6667 | 1 | 23% | 11 | 0.018795 | 0.017048 | 0 | 1 | Warehouse - New
VRF-New-Supermarket | VRF | VRF-New | VRF-New-Supermarket-ElecHt | Supermarket | New | HVAC | ElecHt |  |  | 20 | 46.96% | 3.918% | 6.235% | 7.3248 | 4.95 | 1 | 89.44% | 12 | 0.28701 | 0.19395 | 0 | 1 | Supermarket - New
VRF-New-MiniMart | VRF | VRF-New | VRF-New-MiniMart-ElecHt | MiniMart | New | HVAC | ElecHt |  |  | 20 | 86.61% | 0.9894% | 1.574% | 7.3248 | 4.95 | 1 | 91.39% | 13 | 0.072472 | 0.048976 | 0 | 1 | MiniMart - New
VRF-New-Restaurant | VRF | VRF-New | VRF-New-Restaurant-ElecHt | Restaurant | New | HVAC | ElecHt |  |  | 20 | 79.37% | 3.005% | 17.63% | 7.3248 | 4.95 | 1 | 95.81% | 14 | 0.22012 | 0.14875 | 0 | 1 | Restaurant - New
VRF-New-Lodging | VRF | VRF-New | VRF-New-Lodging-ElecHt | Lodging | New | HVAC | ElecHt |  |  | 20 | 24.94% | 44.68% | 30.38% | 5.2 | 3.68 | 1 | 82.64% | 15 | 2.3233 | 1.6442 | 0 | 1 | Lodging - New
VRF-New-Hospital | VRF | VRF-New | VRF-New-Hospital-ElecHt | Hospital | New | HVAC | ElecHt |  |  | 20 | 91% | 8% | 1% | 5.3185 | 4.13 | 1 | 95% | 16 | 0.42548 | 0.3304 | 0 | 1 | Hospital - New
VRF-New-Residential Care | VRF | VRF-New | VRF-New-Residential Care-ElecHt | Residential Care | New | HVAC | ElecHt |  |  | 20 | 40.56% | 33.99% | 25.46% | 5.3185 | 4.13 | 1 | 82.65% | 17 | 1.8075 | 1.4036 | 0 | 1 | Residential Care - New
VRF-New-Assembly | VRF | VRF-New | VRF-New-Assembly-ElecHt | Assembly | New | HVAC | ElecHt |  |  | 20 | 77.82% | 10.64% | 11.54% | 5.3185 | 2.6667 | 1 | 77.18% | 18 | 0.5659 | 0.28374 | 0 | 1 | Assembly - New
VRF-New-Other | VRF | VRF-New | VRF-New-Other-ElecHt | Other | New | HVAC | ElecHt |  |  | 20 | 72.57% | 16.94% | 10.49% | 5.3185 | 2.6667 | 1 | 71.31% | 19 | 0.90092 | 0.45172 | 0 | 1 | Other - New
VRF-New-Large Off | VRF | VRF-New | VRF-New-Large Off-GasHt | Large Off | New | HVAC | GasHt |  |  | 20 | 54.04% | 20.94% | 9.748% | 4 | 4.0889 | 1 | 95.13% | 2 | 2.1615 | 2.2095 | 0.048365 | 1 | Large Off - New
VRF-New-Medium Off | VRF | VRF-New | VRF-New-Medium Off-GasHt | Medium Off | New | HVAC | GasHt |  |  | 20 | 51.43% | 22.13% | 1.177% | 2.6 | 2.5444 | 1 | 97.67% | 3 | 1.3372 | 1.3086 | 0.048365 | 1 | Medium Off - New
VRF-New-Small Off | VRF | VRF-New | VRF-New-Small Off-GasHt | Small Off | New | HVAC | GasHt |  |  | 20 | 32.75% | 30.64% | 27.77% | 4 | 2.5444 | 1 | 91.12% | 4 | 1.3102 | 0.83341 | 0.048365 | 1 | Small Off - New
VRF-New-Xlarge Ret | VRF | VRF-New | VRF-New-Xlarge Ret-GasHt | Xlarge Ret | New | HVAC | GasHt |  |  | 20 | 91.61% | 5.3% | 17.52% | 2.04 | 2.963 | 1 | 98.61% | 5 | 1.8688 | 2.7143 | 0.048365 | 1 | Xlarge Ret - New
VRF-New-Large Ret | VRF | VRF-New | VRF-New-Large Ret-GasHt | Large Ret | New | HVAC | GasHt |  |  | 20 | 98.32% | 1.059% | 14.93% | 2.04 | 2.963 | 1 | 77.18% | 6 | 2.0058 | 2.9133 | 0.048365 | 1 | Large Ret - New
VRF-New-Medium Ret | VRF | VRF-New | VRF-New-Medium Ret-GasHt | Medium Ret | New | HVAC | GasHt |  |  | 20 | 80.99% | 12.01% | 1.418% | 2.04 | 2.963 | 1 | 90.53% | 7 | 1.6521 | 2.3996 | 0.048365 | 1 | Medium Ret - New
VRF-New-Small Ret | VRF | VRF-New | VRF-New-Small Ret-GasHt | Small Ret | New | HVAC | GasHt |  |  | 20 | 56.72% | 27.33% | 35.3% | 2.04 | 2.963 | 1 | 53.67% | 8 | 1.157 | 1.6805 | 0.048365 | 1 | Small Ret - New
VRF-New-School K-12 | VRF | VRF-New | VRF-New-School K-12-GasHt | School K-12 | New | HVAC | GasHt |  |  | 20 | 84.78% | 5.837% | 24.62% | 2.04 | 2.963 | 1 | 96.13% | 9 | 1.7295 | 2.5119 | 0.048365 | 1 | School K-12 - New
VRF-New-University | VRF | VRF-New | VRF-New-University-GasHt | University | New | HVAC | GasHt |  |  | 20 | 80% | 10% | 11.08% | 2.04 | 2.963 | 1 | 75% | 10 | 1.632 | 2.3704 | 0.048365 | 1 | University - New
VRF-New-Warehouse | VRF | VRF-New | VRF-New-Warehouse-GasHt | Warehouse | New | HVAC | GasHt |  |  | 20 | 98.7% | 0.6393% | 17.52% | 2.04 | 2.963 | 1 | 18.16% | 11 | 2.0135 | 2.9245 | 0.048365 | 1 | Warehouse - New
VRF-New-Supermarket | VRF | VRF-New | VRF-New-Supermarket-GasHt | Supermarket | New | HVAC | GasHt |  |  | 20 | 46.96% | 3.918% | 10.01% | 5.9073 | 5.5 | 1 | 92.15% | 12 | 2.7739 | 2.5826 | 0.048365 | 1 | Supermarket - New
VRF-New-MiniMart | VRF | VRF-New | VRF-New-MiniMart-GasHt | MiniMart | New | HVAC | GasHt |  |  | 20 | 86.61% | 0.9894% | 0.3792% | 5.9073 | 5.5 | 1 | 83.87% | 13 | 5.1161 | 4.7633 | 0.048365 | 1 | MiniMart - New
VRF-New-Restaurant | VRF | VRF-New | VRF-New-Restaurant-GasHt | Restaurant | New | HVAC | GasHt |  |  | 20 | 79.37% | 3.005% | 6.112% | 5.9073 | 5.5 | 1 | 100% | 14 | 4.6884 | 4.3651 | 0.048365 | 1 | Restaurant - New
VRF-New-Lodging | VRF | VRF-New | VRF-New-Lodging-GasHt | Lodging | New | HVAC | GasHt |  |  | 20 | 24.94% | 44.68% | 12.04% | 4 | 4.0889 | 1 | 94.44% | 15 | 0.99767 | 1.0198 | 0.048365 | 1 | Lodging - New
VRF-New-Hospital | VRF | VRF-New | VRF-New-Hospital-GasHt | Hospital | New | HVAC | GasHt |  |  | 20 | 91% | 8% | 15.5% | 3.901 | 4.5889 | 1 | 95% | 16 | 3.5499 | 4.1759 | 0.048365 | 1 | Hospital - New
VRF-New-Residential Care | VRF | VRF-New | VRF-New-Residential Care-GasHt | Residential Care | New | HVAC | GasHt |  |  | 20 | 40.56% | 33.99% | 0.8634% | 3.901 | 4.5889 | 1 | 84.23% | 17 | 1.5821 | 1.8611 | 0.048365 | 1 | Residential Care - New
VRF-New-Assembly | VRF | VRF-New | VRF-New-Assembly-GasHt | Assembly | New | HVAC | GasHt |  |  | 20 | 77.82% | 10.64% | 0.8634% | 3.901 | 2.963 | 1 | 91.18% | 18 | 3.0356 | 2.3056 | 0.048365 | 1 | Assembly - New
VRF-New-Other | VRF | VRF-New | VRF-New-Other-GasHt | Other | New | HVAC | GasHt |  |  | 20 | 72.57% | 16.94% | 8.133% | 3.901 | 2.963 | 1 | 87.72% | 19 | 2.831 | 2.1503 | 0.048365 | 1 | Other - New
VRF-Retro-Large Off | VRF | VRF-Retro | VRF-Retro-Large Off-ElecHt | Large Off | Retro | HVAC | ElecHt |  |  | 20 | 54.04% | 20.94% | 9.748% | 5.2 | 3.68 | 1.155 | 95.13% | 2 | 1.2424 | 0.89018 | 0 | 1.1408 | Large Off - Retro
VRF-Retro-Medium Off | VRF | VRF-Retro | VRF-Retro-Medium Off-ElecHt | Medium Off | Retro | HVAC | ElecHt |  |  | 20 | 51.43% | 22.13% | 1.177% | 2.83 | 2.29 | 1.155 | 97.67% | 3 | 0.71452 | 0.58536 | 0 | 1.1408 | Medium Off - Retro
VRF-Retro-Small Off | VRF | VRF-Retro | VRF-Retro-Small Off-ElecHt | Small Off | Retro | HVAC | ElecHt |  |  | 20 | 32.75% | 30.64% | 27.77% | 5.2 | 2.29 | 1.155 | 91.12% | 4 | 1.8177 | 0.81044 | 0 | 1.1408 | Small Off - Retro
VRF-Retro-Xlarge Ret | VRF | VRF-Retro | VRF-Retro-Xlarge Ret-ElecHt | Xlarge Ret | Retro | HVAC | ElecHt |  |  | 20 | 91.61% | 5.3% | 17.52% | 2.94 | 2.6667 | 1.155 | 98.61% | 5 | 0.15413 | 0.16323 | 0 | 0.98924 | Xlarge Ret - Retro
VRF-Retro-Large Ret | VRF | VRF-Retro | VRF-Retro-Large Ret-ElecHt | Large Ret | Retro | HVAC | ElecHt |  |  | 20 | 98.32% | 1.059% | 14.93% | 2.94 | 2.6667 | 1.155 | 77.18% | 6 | 0.030809 | 0.032627 | 0 | 0.98924 | Large Ret - Retro
VRF-Retro-Medium Ret | VRF | VRF-Retro | VRF-Retro-Medium Ret-ElecHt | Medium Ret | Retro | HVAC | ElecHt |  |  | 20 | 80.99% | 12.01% | 1.418% | 2.94 | 2.6667 | 1.155 | 90.53% | 7 | 0.34919 | 0.36979 | 0 | 0.98924 | Medium Ret - Retro
VRF-Retro-Small Ret | VRF | VRF-Retro | VRF-Retro-Small Ret-ElecHt | Small Ret | Retro | HVAC | ElecHt |  |  | 20 | 56.72% | 27.33% | 35.3% | 2.94 | 2.6667 | 1.155 | 53.67% | 8 | 0.79484 | 0.84174 | 0 | 0.98924 | Small Ret - Retro
VRF-Retro-School K-12 | VRF | VRF-Retro | VRF-Retro-School K-12-ElecHt | School K-12 | Retro | HVAC | ElecHt |  |  | 20 | 84.78% | 5.837% | 24.62% | 2.94 | 2.6667 | 1.155 | 96.13% | 9 | 0.16666 | 0.17978 | 0 | 0.97119 | School K-12 - Retro
VRF-Retro-University | VRF | VRF-Retro | VRF-Retro-University-ElecHt | University | Retro | HVAC | ElecHt |  |  | 20 | 80% | 10% | 11.08% | 2.94 | 2.6667 | 1.155 | 75% | 10 | 0.294 | 0.308 | 0 | 1 | University - Retro
VRF-Retro-Warehouse | VRF | VRF-Retro | VRF-Retro-Warehouse-ElecHt | Warehouse | Retro | HVAC | ElecHt |  |  | 20 | 98.7% | 0.6393% | 17.52% | 2.94 | 2.6667 | 1.155 | 18.16% | 11 | 0.025667 | 0.01969 | 0 | 1.3656 | Warehouse - Retro
VRF-Retro-Supermarket | VRF | VRF-Retro | VRF-Retro-Supermarket-ElecHt | Supermarket | Retro | HVAC | ElecHt |  |  | 20 | 46.96% | 3.918% | 10.01% | 7.3248 | 4.95 | 1.155 | 92.15% | 12 | 0.28967 | 0.22402 | 0 | 1.0093 | Supermarket - Retro
VRF-Retro-MiniMart | VRF | VRF-Retro | VRF-Retro-MiniMart-ElecHt | MiniMart | Retro | HVAC | ElecHt |  |  | 20 | 86.61% | 0.9894% | 0.3792% | 7.3248 | 4.95 | 1.155 | 83.87% | 13 | 0.073145 | 0.056567 | 0 | 1.0093 | MiniMart - Retro
VRF-Retro-Restaurant | VRF | VRF-Retro | VRF-Retro-Restaurant-ElecHt | Restaurant | Retro | HVAC | ElecHt |  |  | 20 | 79.37% | 3.005% | 6.112% | 7.3248 | 4.95 | 1.155 | 100% | 14 | 0.24362 | 0.17181 | 0 | 1.1068 | Restaurant - Retro
VRF-Retro-Lodging | VRF | VRF-Retro | VRF-Retro-Lodging-ElecHt | Lodging | Retro | HVAC | ElecHt |  |  | 20 | 24.94% | 44.68% | 12.04% | 5.2 | 3.68 | 1.155 | 94.44% | 15 | 2.4593 | 1.8991 | 0 | 1.0585 | Lodging - Retro
VRF-Retro-Hospital | VRF | VRF-Retro | VRF-Retro-Hospital-ElecHt | Hospital | Retro | HVAC | ElecHt |  |  | 20 | 91% | 8% | 15.5% | 5.3185 | 4.13 | 1.155 | 95% | 16 | 0.42548 | 0.38161 | 0 | 1 | Hospital - Retro
VRF-Retro-Residential Care | VRF | VRF-Retro | VRF-Retro-Residential Care-ElecHt | Residential Care | Retro | HVAC | ElecHt |  |  | 20 | 40.56% | 33.99% | 0.8634% | 5.3185 | 4.13 | 1.155 | 84.23% | 17 | 1.9806 | 1.6212 | 0 | 1.0958 | Residential Care - Retro
VRF-Retro-Assembly | VRF | VRF-Retro | VRF-Retro-Assembly-ElecHt | Assembly | Retro | HVAC | ElecHt |  |  | 20 | 77.82% | 10.64% | 0.8634% | 5.3185 | 2.6667 | 1.155 | 91.18% | 18 | 0.46873 | 0.32772 | 0 | 0.8283 | Assembly - Retro
VRF-Retro-Other | VRF | VRF-Retro | VRF-Retro-Other-ElecHt | Other | Retro | HVAC | ElecHt |  |  | 20 | 72.57% | 16.94% | 8.133% | 5.3185 | 2.6667 | 1.155 | 87.72% | 19 | 0.9684 | 0.52174 | 0 | 1.0749 | Other - Retro
VRF-Retro-Large Off | VRF | VRF-Retro | VRF-Retro-Large Off-GasHt | Large Off | Retro | HVAC | GasHt |  |  | 20 | 54.04% | 20.94% | 9.748% | 4 | 4.0889 | 1.155 | 95.13% | 2 | 2.4659 | 2.552 | 0.048365 | 1.1408 | Large Off - Retro
VRF-Retro-Medium Off | VRF | VRF-Retro | VRF-Retro-Medium Off-GasHt | Medium Off | Retro | HVAC | GasHt |  |  | 20 | 51.43% | 22.13% | 1.177% | 2.6 | 2.5444 | 1.155 | 97.67% | 3 | 1.5255 | 1.5115 | 0.048365 | 1.1408 | Medium Off - Retro
VRF-Retro-Small Off | VRF | VRF-Retro | VRF-Retro-Small Off-GasHt | Small Off | Retro | HVAC | GasHt |  |  | 20 | 32.75% | 30.64% | 27.77% | 4 | 2.5444 | 1.155 | 91.12% | 4 | 1.4947 | 0.9626 | 0.048365 | 1.1408 | Small Off - Retro
VRF-Retro-Xlarge Ret | VRF | VRF-Retro | VRF-Retro-Xlarge Ret-GasHt | Xlarge Ret | Retro | HVAC | GasHt |  |  | 20 | 91.61% | 5.3% | 17.52% | 2.04 | 2.963 | 1.155 | 98.61% | 5 | 1.8487 | 3.135 | 0.048365 | 0.98924 | Xlarge Ret - Retro
VRF-Retro-Large Ret | VRF | VRF-Retro | VRF-Retro-Large Ret-GasHt | Large Ret | Retro | HVAC | GasHt |  |  | 20 | 98.32% | 1.059% | 14.93% | 2.04 | 2.963 | 1.155 | 77.18% | 6 | 1.9842 | 3.3648 | 0.048365 | 0.98924 | Large Ret - Retro
VRF-Retro-Medium Ret | VRF | VRF-Retro | VRF-Retro-Medium Ret-GasHt | Medium Ret | Retro | HVAC | GasHt |  |  | 20 | 80.99% | 12.01% | 1.418% | 2.04 | 2.963 | 1.155 | 90.53% | 7 | 1.6343 | 2.7715 | 0.048365 | 0.98924 | Medium Ret - Retro
VRF-Retro-Small Ret | VRF | VRF-Retro | VRF-Retro-Small Ret-GasHt | Small Ret | Retro | HVAC | GasHt |  |  | 20 | 56.72% | 27.33% | 35.3% | 2.04 | 2.963 | 1.155 | 53.67% | 8 | 1.1446 | 1.941 | 0.048365 | 0.98924 | Small Ret - Retro
VRF-Retro-School K-12 | VRF | VRF-Retro | VRF-Retro-School K-12-GasHt | School K-12 | Retro | HVAC | GasHt |  |  | 20 | 84.78% | 5.837% | 24.62% | 2.04 | 2.963 | 1.155 | 96.13% | 9 | 1.6796 | 2.9013 | 0.048365 | 0.97119 | School K-12 - Retro
VRF-Retro-University | VRF | VRF-Retro | VRF-Retro-University-GasHt | University | Retro | HVAC | GasHt |  |  | 20 | 80% | 10% | 11.08% | 2.04 | 2.963 | 1.155 | 75% | 10 | 1.632 | 2.7378 | 0.048365 | 1 | University - Retro
VRF-Retro-Warehouse | VRF | VRF-Retro | VRF-Retro-Warehouse-GasHt | Warehouse | Retro | HVAC | GasHt |  |  | 20 | 98.7% | 0.6393% | 17.52% | 2.04 | 2.963 | 1.155 | 18.16% | 11 | 2.7496 | 3.3778 | 0.048365 | 1.3656 | Warehouse - Retro
VRF-Retro-Supermarket | VRF | VRF-Retro | VRF-Retro-Supermarket-GasHt | Supermarket | Retro | HVAC | GasHt |  |  | 20 | 46.96% | 3.918% | 10.01% | 5.9073 | 5.5 | 1.155 | 92.15% | 12 | 2.7997 | 2.983 | 0.048365 | 1.0093 | Supermarket - Retro
VRF-Retro-MiniMart | VRF | VRF-Retro | VRF-Retro-MiniMart-GasHt | MiniMart | Retro | HVAC | GasHt |  |  | 20 | 86.61% | 0.9894% | 0.3792% | 5.9073 | 5.5 | 1.155 | 83.87% | 13 | 5.1636 | 5.5017 | 0.048365 | 1.0093 | MiniMart - Retro
VRF-Retro-Restaurant | VRF | VRF-Retro | VRF-Retro-Restaurant-GasHt | Restaurant | Retro | HVAC | GasHt |  |  | 20 | 79.37% | 3.005% | 6.112% | 5.9073 | 5.5 | 1.155 | 100% | 14 | 5.189 | 5.0417 | 0.048365 | 1.1068 | Restaurant - Retro
VRF-Retro-Lodging | VRF | VRF-Retro | VRF-Retro-Lodging-GasHt | Lodging | Retro | HVAC | GasHt |  |  | 20 | 24.94% | 44.68% | 12.04% | 4 | 4.0889 | 1.155 | 94.44% | 15 | 1.0561 | 1.1779 | 0.048365 | 1.0585 | Lodging - Retro
VRF-Retro-Hospital | VRF | VRF-Retro | VRF-Retro-Hospital-GasHt | Hospital | Retro | HVAC | GasHt |  |  | 20 | 91% | 8% | 15.5% | 3.901 | 4.5889 | 1.155 | 95% | 16 | 3.5499 | 4.8232 | 0.048365 | 1 | Hospital - Retro
VRF-Retro-Residential Care | VRF | VRF-Retro | VRF-Retro-Residential Care-GasHt | Residential Care | Retro | HVAC | GasHt |  |  | 20 | 40.56% | 33.99% | 0.8634% | 3.901 | 4.5889 | 1.155 | 84.23% | 17 | 1.7336 | 2.1496 | 0.048365 | 1.0958 | Residential Care - Retro
VRF-Retro-Assembly | VRF | VRF-Retro | VRF-Retro-Assembly-GasHt | Assembly | Retro | HVAC | GasHt |  |  | 20 | 77.82% | 10.64% | 0.8634% | 3.901 | 2.963 | 1.155 | 91.18% | 18 | 2.5144 | 2.663 | 0.048365 | 0.8283 | Assembly - Retro
VRF-Retro-Other | VRF | VRF-Retro | VRF-Retro-Other-GasHt | Other | Retro | HVAC | GasHt |  |  | 20 | 72.57% | 16.94% | 8.133% | 3.901 | 2.963 | 1.155 | 87.72% | 19 | 3.043 | 2.4836 | 0.048365 | 1.0749 | Other - Retro
Note on W10: Kevin Smit: Based on ratio of existing to new building EUI. Adjust retrofit savings based on this ratio

## Savings & Cost
Savings
Savings Matrix - Built up from specific studies. Proxy values used for building types not covered in studies. Low applicability handled in supply curve applicability
|  | Savings - Gas Ht (kWh/SF) | Savings - Elect Ht (kWh/SF) |  |  |  | Notes:
Very Low | Medium Off | 2.6 | 2.83 |  | Medium Office |  | The BPA 1.20 kWh/sf is way below all other data points, so not used here. Even the 2.83 seems low; only use for Med. Office. The 2.60 from ETO is a proxy
Low | Medium Ret | 2.04 | 2.94 |  | Retail, School
Med | Small Off | 4 | 5.2 |  | Small office,
Med-High | Medical | 3.901 | 5.3185 |  | Hospital, residential casre |  | Gas heat baseline is developed from the Electric baseline minus the average difference from the BPA study
High | Supermarket | 5.9073 | 7.3248 |  | Supermarket, Minimart, restaurant |  | Gas heat baseline is developed from the Electric baseline minus the average difference from the BPA study
[7 empty] | BPA Data | [8 empty] | Ecotope 2014 |  |  |  | Savings
[9 empty] | Savings - Gas Ht (kWh/SF) | Savings - Elect Ht (kWh/SF) | [5 empty] | Case Study | As Designed System EUI (kBtu/sf/yr) | Code System 1 EUI (kBtu/sf/yr) | Code System 2 EUI (kBtu/sf/yr) | Kbtu/sf |  | Energy Usage | Cost | Minimum1 | Average1 | Maximum1 | Standard 90.1-2010
[7 empty] | Medium Office | No HR | 1.06 | 2.69 | 1.63 |  |  |  |  | King County Housing Authority | 30 | 66 | 70 | 36 | 40 | Total Energy Usage, kBtu/ft2 | – | 48.1 | 60.7 | 79 | 55
[8 empty] | With HR | 1.2 | 2.83 | 1.63 |  |  |  |  | Fire Station 72 | 33 | 56 | 67 | 23 | 34 | Heating | – | 10.4 | 13.1 | 17 | 9
[7 empty] | Small Office | No HR | 4.2 | 5.41 | 1.21 |  |  |  |  | Westside School | 16 | 33 | 28 | 17 | 12 | Cooling | – | 5.8 | 7.3 | 9.5 | 6.9
[8 empty] | With HR | 4 | 5.2 | 1.2 | [8 empty] | kwh/sf |  | Fans | – | 4.3 | 5.5 | 7.1 | 5.2
[11 empty] | 1.4175 |  |  |  |  | kWh/sf | 9.5541 | 21.0191 | 22.293 | 11.465 | 12.7389 | HVAC, kWh/ft2 | – | 4 | 5.1 | 6.6 | 3.8
[17 empty] | 10.5096 | 17.8344 | 21.3376 | 7.3248 | 10.828
[17 empty] | 5.0955 | 10.5096 | 8.9172 | 5.414 | 3.8217 |  |  |  | Elect Ht | Gas Ht | Gas
[5 empty] | Gas Savings | [17 empty] | Savings | Savings
Savings Matrix | kWh/sf | kWh/sf | kBtu/sf | kBtu/sf | kBtu/sf | [17 empty] | kWh/Sf | kBtu/Sf | kWh/sf Eq | kWh/sf | kBtu/sf
| GasHt | ElecHt | [5 empty] | BPA Corrected Data | [13 empty] | BPA Small office | 3.81 |  | 3.81 | 2.3925 | 4.8365
Large Off | 4 | 5.2 | 13.648 | 17.7424 | 4.8365 | Med |  |  | kbtu/sf | kWh/sf | [6 empty] | Energy Trust Modeling Data |  |  |  |  | BPA Medium office | 3.22 |  | 3.22 | 1.8025 | 4.8365
Medium Off | 2.6 | 2.83 | 8.8712 | 9.656 | 4.8365 | Very Low |  | Small Office | 13 | 3.8101 | [6 empty] | Baseline System |  |  |  |  | Ecotope - Office |  | 12.74 | 3.7339 | 2.3164 | 4.8365
Small Off | 4 | 5.2 | 13.648 | 17.7424 | 4.8365 | Med |  | Medium Office | 11 | 3.2239 | [5 empty] | Office |  | Incremental Cost ($/sf) | Savings |  |  | Ecotope - Fire Station |  | 10.83 | 3.1741 | 1.7566 | 4.8365
Xlarge Ret | 2.04 | 2.94 | 6.9605 | 10.0313 | 4.8365 | Low | BPA Modeling | [9 empty] | VAV | 2.29 | 3.16 |  |  | Ecotope - School |  | 5.414 | 1.5868 | 0.16926 | 4.8365
Large Ret | 2.04 | 2.94 | 6.9605 | 10.0313 | 4.8365 | Low | [10 empty] | PSZ | 3.68 | 2.6 |  |  | PECI Medical Clinic-Seattle |  | 13.6 | 3.9859 | 2.5684 | 4.8365
Medium Ret | 2.04 | 2.94 | 6.9605 | 10.0313 | 4.8365 | Low | Medium Office |  |  | VAV w/ gas boiler | VAV w/elect ht | [5 empty] | Split | 4.33 | 2.6 |  |  | PECI Medical Clinic-Spokane |  | 16.7 | 4.8945 | 3.477 | 4.8365
Small Ret | 2.04 | 2.94 | 6.9605 | 10.0313 | 4.8365 | Low |  | No Heat Recovery |  | Savings | Savings |  |  |  |  | Retail | [5 empty] | LBL-Minimum | 4 |  | 4 | 2.5825 | 4.8365
School K-12 | 2.04 | 2.94 | 6.9605 | 10.0313 | 4.8365 | Low |  |  |  | kWh/sf | kWh/sf | [5 empty] | PSZ | 4.13 | 2.04 |  |  | LBL-Average | 5.1 |  | 5.1 | 3.6825 | 4.8365
University | 2.04 | 2.94 | 6.9605 | 10.0313 | 4.8365 | Low |  |  | Seattle | 1.2 | 2.53 | [5 empty] | Split | 4.95 | 2.04 |  |  | LBL-Maximum | 6.6 |  | 6.6 | 5.1825 | 4.8365
Warehouse | 2.04 | 2.94 | 6.9605 | 10.0313 | 4.8365 | Low |  |  | Spokane | 0.92 | 2.85 |  |  |  |  | School | [5 empty] | ETO-Office (VAV) | 3.16
Supermarket | 5.9073 | 7.3248 | 20.1558 | 24.9924 | 4.8365 | High |  |  | Average | 1.06 | 2.69 | [5 empty] | PSZ | 5.13 | 2.17 |  |  | ETO-Office (PSZ) | 2.6
MiniMart | 5.9073 | 7.3248 | 20.1558 | 24.9924 | 4.8365 | High | [9 empty] | Multi-Family | [5 empty] | ETO-Retail | 2.04
Restaurant | 5.9073 | 7.3248 | 20.1558 | 24.9924 | 4.8365 | High |  | With Heat Recovery | [8 empty] | PTHP | 2.04 | 2.2 |  |  | ETO-School | 2.17
Lodging | 4 | 5.2 | 13.648 | 17.7424 | 4.8365 | Med |  |  | Average | 1.2 | 2.83 | [10 empty] | ETO-Multifamily | 2.2
Hospital | 3.901 | 5.3185 | 13.3101 | 18.1466 | 4.8365 | Med-High | [9 empty] | All | Ave (all) | 3.65 | 2.94
Residential Care | 3.901 | 5.3185 | 13.3101 | 18.1466 | 4.8365 | Med-High | Small office |  | No HR | 4.2 | 5.41
Assembly | 3.901 | 5.3185 | 13.3101 | 18.1466 | 4.8365 | Med-High |  |  | With HR | 4 | 5.2
Other | 3.901 | 5.3185 | 13.3101 | 18.1466 | 4.8365 | Med-High |  |  |  | Btu/sf | kWh/sf
[10 empty] | 3412.1415 | 1
[7 empty] | PECI Modeling |  |  | Total | kWh/sf
PECI Savings | 22% |  |  | Presentation July 23, 2013 to RTF subcommittee |  |  | Two small offices |  |  | HVAC
PECI Savings | 4.5 | kBTU per SF | Office server room | [6 empty] | RTU Base | VRF | Savings | %
EESConsulting | 20% | of HVAC savings | Literature survey | [5 empty] | Seattle | 12.2 | 8 | 4.2 | 34.43%
[9 empty] | Boise/Spokane | 16.8 | 9.2 | 7.6 | 45.24%
[7 empty] | Medical Clinic |  | Seattle | 19.6 | 6 | 13.6 | 69.39%
[9 empty] | Boise/Spokane | 24.6 | 7.9 | 16.7 | 67.89%
4.3312
5.3185
Cost
Baseline 1 - Primarily Rooftop systems
Cost Matrix | [9 empty] | VRF System Cost Comparison | [5 empty] | Baseline 2 - Primarily VAV systems
[9 empty] | Ecotope 2014 |  |  | VRF System | Baseline 1 | Baseline 2
|  | Savings - Gas Ht (kWh/SF) | Savings - Elect Ht (kWh/SF) | [6 empty] | Case Study | Building Type | Code Proposal (as designed $/sq.ft.) | Code System 1 ($/sq.ft.) | Code System 2 ($/sq.ft.) |  |  |  | Incremental Over Baseline 1 ($/sf) | Incremental Over Baseline 2 ($/sf) | $/sf
Very Low | Medium Off | 2.5444 | 2.29 |  | Medium Office |  |  |  |  | King County Housing Authority | Office | 16 | 9.1 | 14.8 | 1.7582 | 1.0811 |  | 6.9 | 1.2 | 4.05
Low | Medium Ret | 2.963 | 2.6667 |  | Retail, School |  |  |  |  | Fire Station 72 | Institution | 24.8 | 30.5 | 17.7 | 0.81311 | 1.4011 |  | -5.7 | 7.1 | 0.7
Med | Small Off | 4.0889 | 3.68 |  | Small office, |  |  |  |  | Westside School | School | 10.8 | 8.8 | 6.3 | 1.2273 | 1.7143 |  | 2 | 4.5 | 3.25
Med-High | Medical | 4.5889 | 4.13 |  | Hospital, residential casre | [13 empty] | 2.6667 | Average Incremental Cost
High | Supermarket | 5.5 | 4.95 |  | Supermarket, Minimart, restaurant (low applicability) | [13 empty] | 0.97402 | Adjust to 2012$
2.5974
[12 empty] | Other Sources: | EES Consulting | 20% higher than baseline |  | Source: 2011 literature surveys
PNNL |  | VAV With electric heat | 20 | $/sf
|  | CAV with gas heat | 18 | $/Sf
|  | VRF | 24 | $/Sf
|  | Incremental Cost for VRF-Gas Base | 6 | $/sf | 1.3333
|  | Incremental Cost for VRF-Electric Base | 4 | $/sf | 1.2
|  |  | 20% |  | 1.1111 | Use this as a proxy for gas baseline over electric baseline
Per comment from Mira Vowels, BPA "I would expect Higher gas-baseline incremental costs that electric baseline
PNNL Reference:
[5 empty] | PNNL 2012 |  |  |  | 2012-12-01
Cost Matrix |  |  |  |  | Cost Data |  | $/sf |  | Variable Refrigerant Flow Systems
| GasHt | ElecHt |  |  |  | Medium office | 2 |  | Brian Thornton
Large Off | 4.0889 | 3.68 | Med |  |  | Small office | 3 |  | Anne Wagner
Medium Off | 2.5444 | 2.29 | Very Low |  |  | Lodging | 4
Small Off | 2.5444 | 2.29 | Very Low
Xlarge Ret | 2.963 | 2.6667 | Low |  |  |  | 1.155 | Use this as a proxy for cost incement for retro vs. new
Large Ret | 2.963 | 2.6667 | Low
Medium Ret | 2.963 | 2.6667 | Low |  | Professional judgement regarding costs by building type
Small Ret | 2.963 | 2.6667 | Low
School K-12 | 2.963 | 2.6667 | Low
University | 2.963 | 2.6667 | Low |  |  | Energy Trust Modeling Data
Warehouse | 2.963 | 2.6667 | Low |  |  | Baseline System
Supermarket | 5.5 | 4.95 | High |  | Office |  | Incremental Cost ($/sf) | Savings
MiniMart | 5.5 | 4.95 | High |  |  | VAV | 2.29 | 3.16
Restaurant | 5.5 | 4.95 | High |  |  | PSZ | 3.68 | 2.6
Lodging | 4.0889 | 3.68 | Med |  |  | Split | 4.33 | 2.6
Hospital | 4.5889 | 4.13 | Med-High |  | Retail
Residential Care | 4.5889 | 4.13 | Med-High |  |  | PSZ | 4.13 | 2.04
Assembly | 2.963 | 2.6667 | Low |  |  | Split | 4.95 | 2.04
Other | 2.963 | 2.6667 | Low |  | School
[6 empty] | PSZ | 5.13 | 2.17
Multi-Family
[6 empty] | PTHP | 2.04 | 2.2
[5 empty] | All | Ave (all) | 3.65 | 2.94

## Notes & ETO Data
Notes:
[9 empty] | VRF Pilot – Task 1 | [5 empty] | These data were received after the initial workbook was released for review
[9 empty] | Energy Trust of Oregon New Buildings | [5 empty] | These data are modeled results and the reslts of literature surveys
Below are data from Energy Trust of Oregon, 2014 | [8 empty] | DRAFT¦ September 30, 2014 | [5 empty] | The savings values and the costs are lower than the ones being used in the workbook
These are all for new construction only.
Building Type / Baseline System | Ave Energy Savings |  |  |  | % Whole Building Energy Savings | % HVAC Energy Savings |  |  |  | Incremental Cost
| (kWh/sf/yr) | [8 empty] | ($/sf)
| Ave | Min |  | Max | Ave | Ave | Min |  | Max | Ave | Min |  | Max
Office
VAV | 3.16 | 1.73 | 4.82 |  | 19.7% | 35.3% |  | 23.3% | 63.4% | 2.29 |  | 0.23 |  | 4.83
PSZ | 2.6 | 1.97 | 3.31 |  | 14.3% | 32% |  | 13.1% | 47.7% | 3.68 |  | 0.23 |  | 8.69
Split | 2.6 | 1.97 | 3.31 |  | 14.3% | 32% |  | 13.1% | 47.7% | 4.33 |  | 0.23 |  | 11.97
Retail
PSZ | 2.04 | 1.73 | 2.23 |  | 14.9% | 36.8% |  | 30.1% | 47.7% | 4.13 |  | 0.41 |  | 8.69
Split | 2.04 | 1.73 | 2.23 |  | 14.9% | 36.8% |  | 30.1% | 47.7% | 4.95 |  | 0.41 |  | 11.97
School
PSZ | 2.17 | 1.73 | 2.62 |  | 17% | 36.3% |  | 30.1% | 47.7% | 5.13 |  | 0.32 |  | 11.97
Multi-Family
PTHP | 2.2 | 1.64 | 3.24 |  | 31% | 29.3% |  | 25% | 46.8% | 2.04 |  | 0.33 |  | 3.8
All Projects + All Baselines
Average | 2.94 |  |  |  | 21% | 38% |  |  |  | 3.65
Energy Savings for VRF in Multifamily and Schools, ETO, January 2015
PNNL 2012
This study concludes that HVAC energy cost savings of 34% is achievable for VRF relative to VAV with hot water reheat, and CAV with gas heat, and 45% HVAC energy cost savings relative to VAV with electric reheat compared to a variety of conventional existing, or code minimum efficiency, new HVAC systems across a range of building types and climate settings. The average HVAC energy cost savings of VRF is estimated at 34% compared to VAV with chilled water and electric reheat, and 26% compared to VAV with chilled water and hot water reheat, but this a broad estimate and the data doesn’t distinguish between air-cooled and water-cooled chillers, or VRF systems. These savings percentages are based on the information found for this report and should be reviewed at the time VRF systems are being considered as there is a lack of field verified energy savings information.
RTF Discussion
Experts indicate that VRF systems can be installed for now or very low cost compared to standard equipment.

## Applicability Matrix
New Construction | Assumption: Either VRF + Lighting is applied to new buildings, OR the Ultra Low Energy Building Measure is applies. Use these to eliminate overlap
Applicability Matrix |  | VRF | Lighting | ULEB
| Large Off | 5% | 5% | 95% | PUT THESE VALUES IN COM_MASTER_7P!
| Medium Off | 70% | 70% | 30%
| Small Off | 70% | 70% | 30%
| Xlarge Ret | 25% | 25% | 75%
| Large Ret | 25% | 25% | 75%
| Medium Ret | 25% | 25% | 75%
| Small Ret | 25% | 25% | 75%
| School K-12 | 70% | 70% | 30%
| University | 70% | 70% | 30%
| Warehouse | 1% | 1% | 99%
| Supermarket | 5% | 5% | 95%
| MiniMart | 5% | 5% | 95%
| Restaurant | 25% | 25% | 75%
| Lodging | 70% | 70% | 30%
| Hospital | 5% | 5% | 95%
| Residential Care | 70% | 70% | 30%
| Assembly | 25% | 25% | 75%
| Other | 70% | 70% | 30%
Retrofit Applicability
30% of buildings in CBSA have undergone HVAC retrofit. Assume 1/3 of this is major enough to warrant VRF:
Presented to CRAC |  |  | Commets from CRAC |  |  | 9.9%
| Large Off | NO |  |  | Large Off | 0.495%
| Medium Off | YES |  |  | Medium Off | 6.93%
| Small Off | YES |  |  | Small Off | 6.93%
| Xlarge Ret | NO |  |  | Xlarge Ret | 2.475%
| Large Ret | NO |  |  | Large Ret | 2.475%
| Medium Ret | NO |  |  | Medium Ret | 2.475%
| Small Ret | NO |  |  | Small Ret | 2.475%
| School K-12 | YES |  |  | School K-12 | 6.93%
| University | YES |  |  | University | 6.93%
| Warehouse | NO |  |  | Warehouse | 0.099%
| Supermarket | NO |  |  | Supermarket | 0.495%
| MiniMart | NO |  |  | MiniMart | 0.495%
| Restaurant | NO | Yes |  | Restaurant | 2.475%
| Lodging | YES |  |  | Lodging | 6.93%
| Hospital | YES |  |  | Hospital | 0.495%
| Residential Care | YES |  |  | Residential Care | 6.93%
| Assembly | NO |  |  | Assembly | 2.475%
| Other | YES |  |  | Other | 6.93%

## HVAC Retrofit Data
Share of buildings that have undergone HVAC rennovation |  |  |  | Include_Total_EUI | TRUE
Values
Row Labels | Sum of Sf_PNW | Sum of Wt_PNW |  |  | Column Labels
No | 1986091349.2749 | 129428.0819 | 63.63% |  | Sum of _Sf_PNW |  |  | Count of _Sf_PNW2 |  |  | Average of Total_EUI_Norm_kBtu
Unknown | 205716789.9366 | 17272.3471 | 6.59% | Row Labels | Pre-1980 | 1981-2003 | 2004-2013 | Pre-1980 | 1981-2003 | 2004-2013 | Pre-1980 | 1981-2003 | 2004-2013
Yes | 929722347.7885 | 56504.8959 | 29.78% | Assembly | 121252835.2292 | 67010842.4436 | 154297762.3776 | 41 | 21 | 35 | 66.0842 | 56.8948 | 86.1002
Grand Total | 3121530487 | 203205.3249 | 100% | Grocery | 25857894.8687 | 24517146.8004 | 25836108.0035 | 30 | 21 | 20 | 252.643 | 341.0372 | 285.3554
|  |  |  | Lodging | 33203141.2813 | 65528615.3504 | 71484168 | 20 | 26 | 25 | 88.0387 | 96.0211 | 84.8815
|  |  |  | Office | 172821476.6924 | 228728277.5093 | 297625499.4827 | 37 | 30 | 46 | 78.1874 | 89.869 | 67.4065
|  |  |  | Other | 83830286.5371 | 86711674.6969 | 157213912 | 27 | 25 | 28 | 76.4543 | 83.8707 | 71.7518
| Values |  |  | Residential Care | 24779967.1805 | 46413928.8195 | 53966740 | 16 | 30 | 24 | 121.1504 | 93.7675 | 90.1551
Row Labels | Sum of Sf_PNW | Sum of Wt_PNW |  | Restaurant | 19737566.1966 | 17219241.8034 | 16079931 | 14 | 10 | 19 | 476.8645 | 328.6967 | 348.4665
Assembly | 368872052 | 21261.8903 |  | Retail/Service | 171434849.9778 | 164535491.7801 | 205249496.0139 | 42 | 34 | 49 | 67.597 | 80.9485 | 74.895
No | 234868147.9966 | 12465.7724 | 63.67% | School K-12 | 86598684.3048 | 34483926.8948 | 113565709 | 31 | 17 | 23 | 67.3027 | 59.6532 | 67.4687
Unknown | 16697870.8775 | 1026.9163 | 4.527% | Warehouse | 212412102.806 | 106473964.194 | 123337987 | 14 | 9 | 20 | 47.1406 | 55.6752 | 29.9848
Yes | 117306033.1259 | 7769.2016 | 31.8% | Grand Total | 951928805.0745 | 841623110.2923 | 1218657312.8777 | 272 | 223 | 289 | 114.7303 | 116.6519 | 105.7381
Grocery | 77120838 | 6846.5638
No | 59404807.8723 | 5180.9883 | 77.03% | Include_Total_EUI | TRUE
Unknown | 1252607.3313 | 385.2834 | 1.624%
Yes | 16463422.7965 | 1280.2921 | 21.35% |  | Values
Lodging | 171040928 | 3557.2085 |  | Row Labels | Sum of _Sf_PNW | Count of _Sf_PNW2 | Average of Total_EUI_Norm_kBtu |  |  |  | Ratio of Existing to new |  |  | Ratio
No | 113372386.3725 | 2380.4666 | 66.28% | Assembly | 342561440.0504 | 97 | 71.317 |  | 1.3029 | 1.5133 | 0.8283 |  | Large Off | 1.1408
Unknown | 1251647.9673 | 58.9288 | 0.7318% | Grocery | 76211149.6726 | 71 | 288.0025 |  | 1.1295 | 0.83673 | 1.0093 |  | Medium Off | 1.1408
Yes | 56416893.6602 | 1117.8131 | 32.98% | Lodging | 170215924.6317 | 71 | 89.8502 |  | 0.96414 | 0.88399 | 1.0585 |  | Small Off | 1.1408
Office | 734358126 | 61592.8877 |  | Office | 699175253.6844 | 113 | 76.9 |  | 0.86211 | 0.75005 | 1.1408 |  | Xlarge Ret | 0.98924
No | 486716102.3267 | 37699.7133 | 66.28% | Other | 327755873.234 | 80 | 77.126 |  | 0.93849 | 0.8555 | 1.0749 |  | Large Ret | 0.98924
Unknown | 33914892.2062 | 7314.7629 | 4.618% | Residential Care | 125160636 | 70 | 98.7879 |  | 0.74416 | 0.96147 | 1.0958 |  | Medium Ret | 0.98924
Yes | 213727131.4672 | 16578.4116 | 29.1% | Restaurant | 53036739 | 43 | 385.6729 |  | 0.73075 | 1.0601 | 1.1068 |  | Small Ret | 0.98924
Other | 333434465 | 16636.0142 |  | Retail/Service | 541219837.7718 | 125 | 74.0894 |  | 1.108 | 0.92522 | 0.98924 |  | School K-12 | 0.97119
No | 206197720.2223 | 12371.268 | 61.84% | School K-12 | 234648320.1996 | 71 | 65.5249 |  | 1.0025 | 1.131 | 0.97119 |  | University | 1
Unknown | 18675875.4696 | 793.6899 | 5.601% | Warehouse | 442224054 | 43 | 40.9475 |  | 0.63607 | 0.53857 | 1.3656 |  | Warehouse | 1.3656
Yes | 108560869.3082 | 3471.0562 | 32.56% | Grand Total | 3012209228.2445 | 784 | 111.9622 |  | 0.92162 | 0.90644 | 1.0589 |  | Supermarket | 1.0093
Residential Care | 125160636 | 4242.1114 | [8 empty] | 1.0636 | Average | MiniMart | 1.0093
No | 87348144.6876 | 2600.7218 | 69.79% | [9 empty] | Restaurant | 1.1068
Unknown | 10502868.6935 | 490.093 | 8.392% | [9 empty] | Lodging | 1.0585
Yes | 27309622.6188 | 1151.2966 | 21.82% | [9 empty] | Hospital | 1
Restaurant | 53036739 | 12537.9956 | [10 empty] | Residential Care | 1.0958
No | 31191359.5081 | 6790.3161 | 58.81% | [9 empty] | Assembly | 0.8283
Unknown | 5171639.3977 | 1472.3583 | 9.751% | [9 empty] | Other | 1.0749
Yes | 16673740.0942 | 4275.3213 | 31.44%
Retail/Service | 570929488 | 48814.4933
No | 385271593.6082 | 31161.6797 | 67.48%
Unknown | 52988406.2091 | 3895.0295 | 9.281%
Yes | 132669488.1827 | 13757.7841 | 23.24%
School K-12 | 245353161 | 5777.1979
No | 140816869.3244 | 3655.0891 | #DIV/0!
Unknown | 12744911.98 | 196.2902 | #DIV/0!
Yes | 91791379.6955 | 1925.8187 | #DIV/0!
Warehouse | 442224054 | 21938.962
No | 240904217.3564 | 15122.0666 | 54.48%
Unknown | 52516069.8043 | 1638.9949 | 11.88%
Yes | 148803766.8393 | 5177.9005 | 33.65%
Grand Total | 3121530487 | 203205.3249

## Ecotope Data
Ecotope Data
| Case Study | Real World System | Code System 1 | Code System 2
| King County Housing Authority | VRF Heat Pumps w/ DOAS (ERV) | Packaged Roof Top Heat Pump Units, modeled w/ System 9 (PSZHP) inputs from WSEC performance path | Packaged VAV RTU w/ Parallel Fan Powered Terminal Units and Electric Re-heat. Modeled w/ System 3 inputs from 2015 IECC.
| Fire Station 72 | Ground Loop HX serving Water to Water Heat Pumps, radiant distribution with DOAS (ERV) | Ground Loop HX serving constant volume water to air heat pumps. | Water Source Heat Pumps w/ Fluid Cooler and Electric Boiler. Modeled with System 6 inputs from 2015 IECC
| Westside School | VRF Heat Pumps w/ DOAS (ERV) | Packaged Roof Top Heat Pump Units, modeled w/ System 9 (PSZHP) inputs from WSEC performance path | Single Zone Gas Unit Ventilators
| Case Study | As Designed System EUI (kBtu/sf/yr) | Code System 1 EUI (kBtu/sf/yr) | Code System 2 EUI (kBtu/sf/yr)
| King County Housing Authority | 30 | 66 | 70
| Fire Station 72 | 33 | 56 | 67
| Westside School | 16 | 33 | 28
| Case Study |  | Building Type |  | Code Proposal (as designed $/sq.ft.) | Code System 1 ($/sq.ft.) | Code System 2 ($/sq.ft.)
| King County Housing Authority | Office |  | 16 |  | 9.1 | 14.8
| Fire Station 72 | Institution |  | 24.8 |  | 30.5 | 17.7
| Westside School | School |  | 10.8 |  | 8.8 | 6.3
Envelope
Envelope U-factors were held constant at code levels across all three HVAC systems in each case study to isolate the effects of the HVAC systems on the energy use. 2012 WSEC U-factors were used, because they were more stringent than the 2015 IECC values. The only variation in the U-factors between the different buildings was in the slab insulation. Fire Station 72 included radiant (heated & cooled) floors, which requires continuous insulation below the slab. The F-factor actually increases from 0.54 for un-heated to 0.65 for heated due to increased heat transfer through the slab even though the insulation levels increase.
Lights
The building area method was used in all the models, which means that all spaces are modeled with a single lighting power density (LPD), rather than modeling each space with a unique value. LPDs were taken from the 2015 IECC Table 405.5.2(1), as they were more stringent than the 2012 WSEC values.
Plugs
Plug loads were based on values taken from building audits during the design process for each of the buildings.
Schedules
Schedules for the King County Housing are based on the standard National Renewable Energy Lab (NREL) prototype schedules for office buildings, but edited to calibrate the modeling output with billing data. Schedules for Fire Station 72 are based on several fire station audits performed for the City of Seattle and then tweaked to calibrate the model outputs with billing data. Schedules for the Westside School are from the 2012 Seattle Energy Code RS-29 code compliance path.
Sizing
The two code models in each building were sized at 1 CFM/SF, a rule of thumb commonly used by HVAC system designers and installers. This is roughly equivalent to 400 SF/ton. The DOAS models followed the 115% of peak cooling or 125% of peak heating load called out in the proposed code path.
Ventilation
The outdoor air flow rates for models with packaged equipment were set at 18%, which is the average value found by Ecotope in large scale PRTU studies. The DOAS models were set at 130% of the ASHRAE 62 minimum requirements.