## Interactions
Lighting Interaction Factors |  |  |  | Version 12-16-2003 |  | Original data of 09-11-2003 from Ecotope with 10/21/2003 addemdum from Kennedy on schools and 12-16-2003 hours addendum from Grist
INTERACTION factor is in the releative change in heating or cooling from one kWh of lighting savings. Gas interaction is in therms per kWh of lighting savings.
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
Buildng Activity Tyape Category |  |  |  | 2: Heating Only; 6: Cooling; 7: Net Heating and Cooling; 11: Hours
Building Category | Building Sub-Category | RTF Deemed Savings Lookup Category (2001) | RTF Deemed Savings Lookup Category (2004) | 7P Supply Curve Category | INTERACTION factor with ElecHt | INTERACTION factor with HtPmpHt | INTERACTION factor with GasHt (Watts Equivalent) | INTERACTION factor with GasHt (therms per lighting kWh saved) | Cooling Only | INTERACTION factor with ElecHt and Cooling | INTERACTION factor with HtPmpHt | INTERACTION factor with GasHt (Watts Equivalent) | Gas Interaction (therms per lighting kWh saved) | Default Annual Hours of Lighting Operation (2004) | Default Full Load Equivalent Factor | Hour Adjsut from LMC 2002 | Effective Lighting Hours for Supply Curve | 7P Hours (from CBSA 2014)
Assembly | Assembly |  | Other | Other | -0.18 | -0.09 | -0.24 | -0.0081888 | 0.11 | -0.07 | 0.02 | -0.13 | -0.0081888 | 4000 | 0.9 | 90% | 3600
Assembly | Church, Religious, Civic |  |  |  | -0.18 | -0.09 | -0.24 | -0.0081888 | 0.11 | -0.07 | 0.02 | -0.13 | -0.0081888 | 1800 | 0.9
Assembly | Casino |  |  |  | -0.42 | -0.21 | -0.56 | -0.019107 | 0.19 | -0.23 | -0.02 | -0.37 | -0.019107 | 8760 | 0.9
Assembly | Expo Hall |  |  | Assembly | -0.18 | -0.09 | -0.24 | -0.0081888 | 0.11 | -0.07 | 0.02 | -0.13 | -0.0081888 | 3000 | 0.9 | 93.33% | 2800
Assembly | Fair Arena |  |  |  | -0.42 | -0.21 | -0.56 | -0.019107 | 0.19 | -0.23 | -0.02 | -0.37 | -0.019107 | 3000 | 0.9
Education | College or University |  | University | University | -0.47 | -0.235 | -0.62667 | -0.021382 | 0.19 | -0.28 | -0.045 | -0.43667 | -0.021382 | 3000 | 0.9 | 100% | 3000
Education | Daycare / Preschool |  |  |  | -0.73 | -0.365 | -0.97333 | -0.03321 | 0.05 | -0.68 | -0.315 | -0.92333 | -0.03321 | 2800 | 0.9
Education | Elementary School | School |  | School K-12 | -0.48 | -0.24 | -0.64 | -0.021837 | 0.1 | -0.38 | -0.14 | -0.54 | -0.021837 | 2400 | 0.9 | 120.8% | 2900
Education | Middle School |  | K-12 |  | -0.48 | -0.24 | -0.64 | -0.021837 | 0.1 | -0.38 | -0.14 | -0.54 | -0.021837 | 2400 | 0.9
Education | High School |  |  |  | -0.48 | -0.24 | -0.64 | -0.021837 | 0.12 | -0.36 | -0.12 | -0.52 | -0.021837 | 2400 | 0.9
Education | University Dormitory |  |  |  | -0.4 | -0.2 | -0.53333 | -0.018197 | 0.1 | -0.3 | -0.1 | -0.43333 | -0.018197 | 3600 | 0.9
Education | Laboratory, Research |  |  |  | -0.72 | -0.36 | -0.96 | -0.032755 | 0.01 | -0.71 | -0.35 | -0.95 | -0.032755 | 5800 | 0.9
Grocery | Grocery or Food Retail | Grocery | Supermarket | Supermarket | -0.22 | -0.11 | -0.29333 | -0.010009 | 0.08 | -0.14 | -0.03 | -0.21333 | -0.010009 | 6500 | 0.9 | 89.23% | 5800
Grocery | Convenience Retail Sales |  | MIniMart | MiniMart | -0.39 | -0.195 | -0.52 | -0.017742 | 0.14 | -0.25 | -0.055 | -0.38 | -0.017742 | 6500 | 0.9 | 89.23% | 5800
Health | Birthing Center |  |  |  | -0.72 | -0.36 | -0.96 | -0.032755 | 0.01 | -0.71 | -0.35 | -0.95 | -0.032755 | 5800 | 0.9
Health | Hospital | Health | Hospital | Hospital | -0.72 | -0.36 | -0.96 | -0.032755 | 0.01 | -0.71 | -0.35 | -0.95 | -0.032755 | 5900 | 0.9 | 108.5% | 6400
Health | Nursing Home |  |  | Residential Care | -0.4 | -0.2 | -0.53333 | -0.018197 | 0.1 | -0.3 | -0.1 | -0.43333 | -0.018197 | 4400 | 0.9
Health | Medical Office |  |  | Medium Off | -0.18 | -0.09 | -0.24 | -0.0081888 | 0.11 | -0.07 | 0.02 | -0.13 | -0.0081888 | 3600 | 0.9 | 105.6% | 3800
Health | Other Medical |  | Other Health | OtherHealth | -0.18 | -0.09 | -0.24 | -0.0081888 | 0.11 | -0.07 | 0.02 | -0.13 | -0.0081888 | 3600 | 0.9 | 100% | 3600
Health | Outpatient Care |  |  |  | -0.18 | -0.09 | -0.24 | -0.0081888 | 0.11 | -0.07 | 0.02 | -0.13 | -0.0081888 | 3400 | 0.9
Health | Medical Laboratory |  |  |  | -0.72 | -0.36 | -0.96 | -0.032755 | 0.01 | -0.71 | -0.35 | -0.95 | -0.032755 | 5800 | 0.9
Health | Retirement Center |  |  |  | -0.4 | -0.2 | -0.53333 | -0.018197 | 0.1 | -0.3 | -0.1 | -0.43333 | -0.018197 | 3600 | 0.9
Institution | Jail Facility |  |  |  | -0.4 | -0.2 | -0.53333 | -0.018197 | 0.1 | -0.3 | -0.1 | -0.43333 | -0.018197 | 5800 | 0.9
Institution | Police Station |  |  |  | -0.39 | -0.195 | -0.52 | -0.017742 | 0.14 | -0.25 | -0.055 | -0.38 | -0.017742 | 5800 | 0.9
Institution | Juvenile Corrections |  |  |  | -0.4 | -0.2 | -0.53333 | -0.018197 | 0.1 | -0.3 | -0.1 | -0.43333 | -0.018197 | 5800 | 0.9
Institution | Fire Station |  |  |  | -0.4 | -0.2 | -0.53333 | -0.018197 | 0.1 | -0.3 | -0.1 | -0.43333 | -0.018197 | 5800 | 0.9
Lodging | Hotel |  |  |  | -0.4 | -0.2 | -0.53333 | -0.018197 | 0.1 | -0.3 | -0.1 | -0.43333 | -0.018197 | 3600 | 0.9
Lodging | Retirement/Assisted |  |  |  | -0.4 | -0.2 | -0.53333 | -0.018197 | 0.1 | -0.3 | -0.1 | -0.43333 | -0.018197 | 3600 | 0.9
Lodging | Motel | Hospitality | Lodging | Lodging | -0.4 | -0.2 | -0.53333 | -0.018197 | 0.1 | -0.3 | -0.1 | -0.43333 | -0.018197 | 3600 | 0.9 | 116.7% | 4200
Lodging | Lodge |  |  |  | -0.4 | -0.2 | -0.53333 | -0.018197 | 0.1 | -0.3 | -0.1 | -0.43333 | -0.018197 | 3600 | 0.9
Office | Large Office - VAV | Large (>20,000 ft2) Office | Large Office | Large Off | -0.18 | -0.09 | -0.24 | -0.0081888 | 0.11 | -0.07 | 0.02 | -0.13 | -0.0081888 | 4200 | 0.9 | 102.4% | 4300
Office | Large Office - Water Loop |  |  |  | -0.13 | -0.065 | -0.17333 | -0.0059141 | 0.3 | 0.17 | 0.235 | 0.12667 | -0.0059141 | 3900 | 0.9
Office | Small Office - RTU | Small (<=20,000 ft2) Office | Small Office | Small Off | -0.47 | -0.235 | -0.62667 | -0.021382 | 0.19 | -0.28 | -0.045 | -0.43667 | -0.021382 | 3000 | 0.9 | 126.7% | 3800
Other | Railroad Terminal |  |  |  | -0.13 | -0.065 | -0.17333 | -0.0059141 | 0.14 | 0.01 | 0.075 | -0.033333 | -0.0059141 | 8760 | 0.7
Other | Bus Terminal |  |  |  | -0.13 | -0.065 | -0.17333 | -0.0059141 | 0.14 | 0.01 | 0.075 | -0.033333 | -0.0059141 | 8760 | 0.7
Other | Airport Terminal |  |  |  | -0.13 | -0.065 | -0.17333 | -0.0059141 | 0.14 | 0.01 | 0.075 | -0.033333 | -0.0059141 | 8760 | 0.7
Other | Auto Repair Only |  |  |  | -0.39 | -0.195 | -0.52 | -0.017742 | 0 | -0.39 | -0.195 | -0.52 | -0.017742 | 3900 | 0.9
Other | Bakery |  |  |  | 0 | 0 | 0 | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 3500 | 0.9
Other | Community Pool |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 0.9
Other | Green House |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3500 | 0.9
Other | Laundry |  |  |  | 0 | 0 | 0 | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 3500 | 0.9
Other | Newspaper Office/Press |  |  |  | -0.4 | -0.2 | -0.53333 | -0.018197 | 0.12 | -0.28 | -0.08 | -0.41333 | -0.018197 | 3500 | 0.9
Other | Parking Garage |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 0.7
Other | Shop |  |  |  | -0.39 | -0.195 | -0.52 | -0.017742 | 0 | -0.39 | -0.195 | -0.52 | -0.017742 | 3000 | 0.9
Other | Miscellaneous |  |  |  | -0.39 | -0.195 | -0.52 | -0.017742 | 0 | -0.39 | -0.195 | -0.52 | -0.017742 | 3500 | 0.9
Other | Exterior |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4500 | 1
Restaurant | Fast Food | Restaurant | Restaurant | Restaurant | -0.59 | -0.295 | -0.78667 | -0.026841 | 0.02 | -0.57 | -0.275 | -0.76667 | -0.026841 | 5000 | 0.9 | 102% | 5100
Restaurant | Full Restaurant |  |  |  | -0.59 | -0.295 | -0.78667 | -0.026841 | 0.02 | -0.57 | -0.275 | -0.76667 | -0.026841 | 5200 | 0.9
Retail | Auto Sales |  |  |  | -0.39 | -0.195 | -0.52 | -0.017742 | 0.12 | -0.27 | -0.075 | -0.4 | -0.017742 | 3900 | 0.9
Retail | Bank |  |  |  | -0.39 | -0.195 | -0.52 | -0.017742 | 0.12 | -0.27 | -0.075 | -0.4 | -0.017742 | 3900 | 0.9
Retail | Anchor Retail |  | Large Multi-Story Retail | Large Ret | -0.43 | -0.215 | -0.57333 | -0.019562 | 0.18 | -0.25 | -0.035 | -0.39333 | -0.019562 | 4000 | 0.9 | 100% | 4000
Retail | Big Box Retail | Large (>20,000 ft2) Retail | Big Box Retail | Xlarge Ret | -0.33 | -0.165 | -0.44 | -0.015013 | 0.19 | -0.14 | 0.025 | -0.25 | -0.015013 | 4800 | 0.9 | 100% | 4800
Retail | Small Retail | Small (<=20,000 ft2) Retail | Small Retail | Medium Ret | -0.39 | -0.195 | -0.52 | -0.017742 | 0.12 | -0.27 | -0.075 | -0.4 | -0.017742 | 3900 | 0.9 | 100% | 3900
Retail | Boutique Retail |  | Boutique Retail | Small Ret | -0.31 | -0.155 | -0.41333 | -0.014103 | 0.13 | -0.18 | -0.025 | -0.28333 | -0.014103 | 3400 | 0.9 | 100% | 3400
Retail | Post Office |  |  |  | -0.39 | -0.195 | -0.52 | -0.017742 | 0.12 | -0.27 | -0.075 | -0.4 | -0.017742 | 3900 | 0.9
Warehouse | Warehouse | Warehouse | Warehouse | Warehouse | -0.39 | -0.195 | -0.52 | -0.017742 | 0 | -0.39 | -0.195 | -0.52 | -0.017742 | 3500 | 0.9 | 108.6% | 3800
Warehouse | Wholesale |  |  |  | -0.4 | -0.2 | -0.53333 | -0.018197 | 0.12 | -0.28 | -0.08 | -0.41333 | -0.018197 | 3500 | 0.9
Warehouse | Refrigerated Warehouse |  |  |  | 0 | 0 | 0 | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 3500 | 0.9
Warehouse | Shop/Storage |  |  |  | -0.39 | -0.195 | -0.52 | -0.017742 | 0.08 | -0.31 | -0.115 | -0.44 | -0.017742 | 2000 | 0.9
Warehouse | Warehouse/Distribution |  |  |  | -0.39 | -0.195 | -0.52 | -0.017742 | 0.08 | -0.31 | -0.115 | -0.44 | -0.017742 | 5800 | 0.9
Manufacturing | Mfg - 1 Shift - No heating load |  | Mfg - 1 Shift - No HVAC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2400 | 0.9
Manufacturing | Mfg - 2 Shift - No heating load |  | Mfg - 2 Shift - No HVAC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4600 | 0.9
Manufacturing | Mfg - 3 Shift - No heating load |  | Mfg - 3 Shift - No HVAC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 0.9 |  |  |  | Xlarge Ret | Large Ret | Medium Ret | Small Ret
Note on A1: Charlie Grist: INTERACTION factor is in the releative change in heating or cooling from one kWh of lighting savings. Gas interaction is in therms per kWh of lighting savings.
Note on K6: David Baylon: All in teractions combined in watts equivlent
Note on M7: Charlie Grist: Caution. This is a net energy value and should not be used to calculate BC ratios.
Note on N7: Charlie Grist: These values are the same as for heating only. There is no net change in the gas impact because of cooling.
Note on P7: Charlie Grist: Factor to represent not all watage on for the operating period.
Note on Q8: Charlie Grist: Updated 2008 with data from national Lighting Market Characterization from 2002 by Navigant"
Note on Q11: Charlie Grist: Updated 2008 with data from national Lighting Market Characterization from 2002 by Navigant"
Note on Q13: Charlie Grist: Updated 2008 with data from national Lighting Market Characterization from 2002 by Navigant"
Note on Q15: Charlie Grist: Updated 2008 with data from national Lighting Market Characterization from 2002 by Navigant"
Note on Q20: Charlie Grist: Updated 2008 with data from national Lighting Market Characterization from 2002 by Navigant"
Note on Q21: Charlie Grist: Updated 2008 with data from national Lighting Market Characterization from 2002 by Navigant"
Note on Q23: Charlie Grist: Updated 2008 with data from national Lighting Market Characterization from 2002 by Navigant"
Note on Q25: Charlie Grist: Updated 2008 with data from national Lighting Market Characterization from 2002 by Navigant"
Note on Q26: Charlie Grist: Updated 2008 with data from national Lighting Market Characterization from 2002 by Navigant"
Note on Q36: Charlie Grist: Updated 2008 with data from national Lighting Market Characterization from 2002 by Navigant"
Note on Q38: Charlie Grist: Updated 2008 with data from national Lighting Market Characterization from 2002 by Navigant"
Note on Q40: Charlie Grist: Updated 2008 with data from national Lighting Market Characterization from 2002 by Navigant"
Note on Q54: Charlie Grist: Updated 2008 with data from national Lighting Market Characterization from 2002 by Navigant"
Note on Q58: Charlie Grist: Updated 2008 with data from national Lighting Market Characterization from 2002 by Navigant"
Note on Q59: Charlie Grist: Updated 2008 with data from national Lighting Market Characterization from 2002 by Navigant"
Note on Q60: Charlie Grist: Updated 2008 with data from national Lighting Market Characterization from 2002 by Navigant"
Note on Q61: Charlie Grist: Updated 2008 with data from national Lighting Market Characterization from 2002 by Navigant"
Note on Q63: Charlie Grist: Updated 2008 with data from national Lighting Market Characterization from 2002 by Navigant"

## Yeild
Lighting Savings Electric YIELD Factors |  |  |  | Version 12-16-2003
YIELD is the net electric savings from a lighting conservation measure due to electric HVAC interactions. Multiply lighting savings by YIELD to get net savings. Does not include gas interactions.
Version of 09-11-2003 from Ecotope with 10/21/2003 addemdum from Kennedy on schools and 12-16-2003 hours addendum from Grist
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Buildng Activity Tyape Category |  |  |  | 2: Heating Only; 6: Cooling; 7: Net Heating and Cooling; 11: Hours
Building Category | Building Sub-Category | RTF Deemed Savings Lookup Category (2001) | RTF Deemed Savings Lookup Category (2004) | 7P Supply Curve Category | YIELD with ElecHt | YIELD with HtPmpHt | YIELD with GasHt | Gas Interaction (therms per lighting kWh saved) | Cooling Only | YIELD with ElecHt and Cooling | YIELD with HtPmpHt and Cooling | YIELD with GasHt and Cooling | Gas Interaction (therms per lighting kWh saved) | Default Annual Hours of Lighting Operation (2004) | Default Full Load Equivalent Factor | 7P Hours (from CBSA 2014)
Assembly | Assembly |  | Other | Other | 0.82 | 0.91 | 0.9832 | -0.0081888 | 1.11 | 0.93 | 1.02 | 1.0932 | -0.0081888 | 4000 | 0.9
Assembly | Church, Religious, Civic |  |  |  | 0.82 | 0.91 | 0.9832 | -0.0081888 | 1.11 | 0.93 | 1.02 | 1.0932 | -0.0081888 | 1800 | 0.9
Assembly | Casino |  |  |  | 0.58 | 0.79 | 0.9608 | -0.019107 | 1.19 | 0.77 | 0.98 | 1.1508 | -0.019107 | 8760 | 0.9
Assembly | Expo Hall |  |  | Assembly | 0.82 | 0.91 | 0.9832 | -0.0081888 | 1.11 | 0.93 | 1.02 | 1.0932 | -0.0081888 | 3000 | 0.9
Assembly | Fair Arena |  |  |  | 0.58 | 0.79 | 0.9608 | -0.019107 | 1.19 | 0.77 | 0.98 | 1.1508 | -0.019107 | 3000 | 0.9
Education | College or University |  | University | University | 0.53 | 0.765 | 0.95613 | -0.021382 | 1.19 | 0.72 | 0.955 | 1.1461 | -0.021382 | 3000 | 0.9
Education | Daycare / Preschool |  |  |  | 0.27 | 0.635 | 0.93187 | -0.03321 | 1.05 | 0.32 | 0.685 | 0.98187 | -0.03321 | 2800 | 0.9
Education | Elementary School | School |  | School K-12 | 0.52 | 0.76 | 0.9552 | -0.021837 | 1.1 | 0.62 | 0.86 | 1.0552 | -0.021837 | 2400 | 0.9
Education | Middle School |  | K-12 |  | 0.52 | 0.76 | 0.9552 | -0.021837 | 1.1 | 0.62 | 0.86 | 1.0552 | -0.021837 | 2400 | 0.9
Education | High School |  |  |  | 0.52 | 0.76 | 0.9552 | -0.021837 | 1.12 | 0.64 | 0.88 | 1.0752 | -0.021837 | 2400 | 0.9
Education | University Dormitory |  |  |  | 0.6 | 0.8 | 0.96267 | -0.018197 | 1.1 | 0.7 | 0.9 | 1.0627 | -0.018197 | 3600 | 0.9
Education | Laboratory, Research |  |  |  | 0.28 | 0.64 | 0.9328 | -0.032755 | 1.01 | 0.29 | 0.65 | 0.9428 | -0.032755 | 5800 | 0.9
Grocery | Grocery or Food Retail | Grocery | Supermarket | Supermarket | 0.78 | 0.89 | 0.97947 | -0.010009 | 1.08 | 0.86 | 0.97 | 1.0595 | -0.010009 | 6500 | 0.9
Grocery | Convenience Retail Sales |  | MIniMart | MiniMart | 0.61 | 0.805 | 0.9636 | -0.017742 | 1.14 | 0.75 | 0.945 | 1.1036 | -0.017742 | 6500 | 0.9
Health | Birthing Center |  |  |  | 0.28 | 0.64 | 0.9328 | -0.032755 | 1.01 | 0.29 | 0.65 | 0.9428 | -0.032755 | 5800 | 0.9
Health | Hospital | Health | Hospital | Hospital | 0.28 | 0.64 | 0.9328 | -0.032755 | 1.01 | 0.29 | 0.65 | 0.9428 | -0.032755 | 5900 | 0.9
Health | Nursing Home |  |  | Residential Care | 0.6 | 0.8 | 0.96267 | -0.018197 | 1.1 | 0.7 | 0.9 | 1.0627 | -0.018197 | 4400 | 0.9
Health | Medical Office |  |  | Medium Off | 0.82 | 0.91 | 0.9832 | -0.0081888 | 1.11 | 0.93 | 1.02 | 1.0932 | -0.0081888 | 3600 | 0.9
Health | Other Medical |  | Other Health | OtherHealth | 0.82 | 0.91 | 0.9832 | -0.0081888 | 1.11 | 0.93 | 1.02 | 1.0932 | -0.0081888 | 3600 | 0.9
Health | Outpatient Care |  |  |  | 0.82 | 0.91 | 0.9832 | -0.0081888 | 1.11 | 0.93 | 1.02 | 1.0932 | -0.0081888 | 3400 | 0.9
Health | Medical Laboratory |  |  |  | 0.28 | 0.64 | 0.9328 | -0.032755 | 1.01 | 0.29 | 0.65 | 0.9428 | -0.032755 | 5800 | 0.9
Health | Retirement Center |  |  |  | 0.6 | 0.8 | 0.96267 | -0.018197 | 1.1 | 0.7 | 0.9 | 1.0627 | -0.018197 | 3600 | 0.9
Institution | Jail Facility |  |  |  | 0.6 | 0.8 | 0.96267 | -0.018197 | 1.1 | 0.7 | 0.9 | 1.0627 | -0.018197 | 5800 | 0.9
Institution | Police Station |  |  |  | 0.61 | 0.805 | 0.9636 | -0.017742 | 1.14 | 0.75 | 0.945 | 1.1036 | -0.017742 | 5800 | 0.9
Institution | Juvenile Corrections |  |  |  | 0.6 | 0.8 | 0.96267 | -0.018197 | 1.1 | 0.7 | 0.9 | 1.0627 | -0.018197 | 5800 | 0.9
Institution | Fire Station |  |  |  | 0.6 | 0.8 | 0.96267 | -0.018197 | 1.1 | 0.7 | 0.9 | 1.0627 | -0.018197 | 5800 | 0.9
Lodging | Hotel |  |  |  | 0.6 | 0.8 | 0.96267 | -0.018197 | 1.1 | 0.7 | 0.9 | 1.0627 | -0.018197 | 3600 | 0.9
Lodging | Retirement/Assisted |  |  |  | 0.6 | 0.8 | 0.96267 | -0.018197 | 1.1 | 0.7 | 0.9 | 1.0627 | -0.018197 | 3600 | 0.9
Lodging | Motel | Hospitality | Lodging | Lodging | 0.6 | 0.8 | 0.96267 | -0.018197 | 1.1 | 0.7 | 0.9 | 1.0627 | -0.018197 | 3600 | 0.9
Lodging | Lodge |  |  |  | 0.6 | 0.8 | 0.96267 | -0.018197 | 1.1 | 0.7 | 0.9 | 1.0627 | -0.018197 | 3600 | 0.9
Office | Large Office - VAV | Large (>20,000 ft2) Office | Large Office | Large Off | 0.82 | 0.91 | 0.9832 | -0.0081888 | 1.11 | 0.93 | 1.02 | 1.0932 | -0.0081888 | 4200 | 0.9
Office | Large Office - Water Loop |  |  |  | 0.87 | 0.935 | 0.98787 | -0.0059141 | 1.3 | 1.17 | 1.235 | 1.2879 | -0.0059141 | 3900 | 0.9
Office | Small Office - RTU | Small (<=20,000 ft2) Office | Small Office | Small Off | 0.53 | 0.765 | 0.95613 | -0.021382 | 1.19 | 0.72 | 0.955 | 1.1461 | -0.021382 | 3000 | 0.9
Other | Railroad Terminal |  |  |  | 0.87 | 0.935 | 0.98787 | -0.0059141 | 1.14 | 1.01 | 1.075 | 1.1279 | -0.0059141 | 8760 | 0.7
Other | Bus Terminal |  |  |  | 0.87 | 0.935 | 0.98787 | -0.0059141 | 1.14 | 1.01 | 1.075 | 1.1279 | -0.0059141 | 8760 | 0.7
Other | Airport Terminal |  |  |  | 0.87 | 0.935 | 0.98787 | -0.0059141 | 1.14 | 1.01 | 1.075 | 1.1279 | -0.0059141 | 8760 | 0.7
Other | Auto Repair Only |  |  |  | 0.61 | 0.805 | 0.9636 | -0.017742 | 1 | 0.61 | 0.805 | 0.9636 | -0.017742 | 3900 | 0.9
Other | Bakery |  |  |  | 1 | 1 | 1 | 0 | 1.12 | 1.12 | 1.12 | 1.12 | 0 | 3500 | 0.9
Other | Community Pool |  |  |  | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 3000 | 0.9
Other | Green House |  |  |  | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 3500 | 0.9
Other | Laundry |  |  |  | 1 | 1 | 1 | 0 | 1.12 | 1.12 | 1.12 | 1.12 | 0 | 3500 | 0.9
Other | Newspaper Office/Press |  |  |  | 0.6 | 0.8 | 0.96267 | -0.018197 | 1.12 | 0.72 | 0.92 | 1.0827 | -0.018197 | 3500 | 0.9
Other | Parking Garage |  |  |  | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 8760 | 0.7
Other | Shop |  |  |  | 0.61 | 0.805 | 0.9636 | -0.017742 | 1 | 0.61 | 0.805 | 0.9636 | -0.017742 | 3000 | 0.9
Other | Miscellaneous |  |  |  | 0.61 | 0.805 | 0.9636 | -0.017742 | 1 | 0.61 | 0.805 | 0.9636 | -0.017742 | 3500 | 0.9
Other | Exterior |  | Exterior |  | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 4500 | 1
Restaurant | Fast Food | Restaurant | Restaurant | Restaurant | 0.41 | 0.705 | 0.94493 | -0.026841 | 1.02 | 0.43 | 0.725 | 0.96493 | -0.026841 | 5000 | 0.9
Restaurant | Full Restaurant |  |  |  | 0.41 | 0.705 | 0.94493 | -0.026841 | 1.02 | 0.43 | 0.725 | 0.96493 | -0.026841 | 5200 | 0.9
Retail | Auto Sales |  |  |  | 0.61 | 0.805 | 0.9636 | -0.017742 | 1.12 | 0.73 | 0.925 | 1.0836 | -0.017742 | 3900 | 0.9
Retail | Bank |  |  |  | 0.61 | 0.805 | 0.9636 | -0.017742 | 1.12 | 0.73 | 0.925 | 1.0836 | -0.017742 | 3900 | 0.9
Retail | Anchor Retail |  | Large Multi-Story Retail | Large Ret | 0.57 | 0.785 | 0.95987 | -0.019562 | 1.18 | 0.75 | 0.965 | 1.1399 | -0.019562 | 4000 | 0.9
Retail | Big Box Retail | Large (>20,000 ft2) Retail | Big Box Retail | Xlarge Ret | 0.67 | 0.835 | 0.9692 | -0.015013 | 1.19 | 0.86 | 1.025 | 1.1592 | -0.015013 | 4800 | 0.9
Retail | Small Retail | Small (<=20,000 ft2) Retail | Small Retail | Medium Ret | 0.61 | 0.805 | 0.9636 | -0.017742 | 1.12 | 0.73 | 0.925 | 1.0836 | -0.017742 | 3900 | 0.9
Retail | Boutique Retail |  | Boutique Retail | Small Ret | 0.69 | 0.845 | 0.97107 | -0.014103 | 1.13 | 0.82 | 0.975 | 1.1011 | -0.014103 | 3400 | 0.9
Retail | Post Office |  |  |  | 0.61 | 0.805 | 0.9636 | -0.017742 | 1.12 | 0.73 | 0.925 | 1.0836 | -0.017742 | 3900 | 0.9
Warehouse | Warehouse | Warehouse | Warehouse | Warehouse | 0.61 | 0.805 | 0.9636 | -0.017742 | 1 | 0.61 | 0.805 | 0.9636 | -0.017742 | 3500 | 0.9
Warehouse | Wholesale |  |  |  | 0.6 | 0.8 | 0.96267 | -0.018197 | 1.12 | 0.72 | 0.92 | 1.0827 | -0.018197 | 3500 | 0.9
Warehouse | Refrigerated Warehouse |  |  |  | 1 | 1 | 1 | 0 | 1.12 | 1.12 | 1.12 | 1.12 | 0 | 3500 | 0.9
Warehouse | Shop/Storage |  |  |  | 0.61 | 0.805 | 0.9636 | -0.017742 | 1.08 | 0.69 | 0.885 | 1.0436 | -0.017742 | 2000 | 0.9
Warehouse | Warehouse/Distribution |  |  |  | 0.61 | 0.805 | 0.9636 | -0.017742 | 1.08 | 0.69 | 0.885 | 1.0436 | -0.017742 | 5800 | 0.9
Manufacturing | Mfg - 1 Shift - No heating load |  | Mfg - 1 Shift - No HVAC |  | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2400 | 0.9
Manufacturing | Mfg - 2 Shift - No heating load |  | Mfg - 2 Shift - No HVAC |  | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 4600 | 0.9
Manufacturing | Mfg - 3 Shift - No heating load |  | Mfg - 3 Shift - No HVAC |  | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 7000 | 0.9
Note on K6: David Baylon: All in teractions combined in watts equivlent
Note on H7: Charlie Grist: Includes fan impacts from change in heating loads.
Note on K7: Charlie Grist: Assume 100% cooled area with electric cooling
Note on L7: Charlie Grist: Assume 100% cooled area with electric cooling
Note on M7: Charlie Grist: Assume 100% cooled area with electric cooling

## Notes
Notes
1 | Values are from a series of several hundred DOE 2 runs performed by Mike Kennedy in 2003 on several prototypes in several configurations of shell, lpd, ventilation rates, HVAC system configuration and climate
2 | Values are default estimates for common cases of building and system configuration and operating conditions thought to represent the population. Over 600 results were synthesized into the categories represented in the tables as a simplification for regional conservation analysis and for default values for the RTF calculators and deemed savings calculations. As a result the default values may not represent specific cases. Specific cases which are thought to have significantly different interactions than the defaults should be modeled under RTF protocols.
3 | Values represent whole-buildings
4 | Values for New and Existing Buildings were combined since differences were slight due to compensating shell and lpd characteristics.
5 | New building types were added to guide users to representative whole-building activity types
6 | YIELD is the net savings from a lighting conservation measure due to HVAC interactions. Multiply lighting savings by YIELD to get net savings.
7 | INTERACTION is in the change in savings from a lighting conservation measure due to HVAC interactions
8 | For thermal space heat systems INTERACTION is in therms per kWh of lighting savings.
9 | DEFAULT ANNUAL HOURS OF LIGHTING OPERATION are estimated from twelve sources.
10 | DEFAULT FULL LOAD EQUIVALENT HOURS FACTOR is used to estimate full load equivalent hours of shole building lighting operation in the deemed savings calculator.
Links | ..\..\Plan 5\Commercial\Data Sources\Kennedy\SchoolLightingInteractions.doc
..\..\Plan 5\Commercial\Data Sources\Kennedy\Lighting Savings Interactions.doc